## DiscreteSignals
SINAL | DESCRIÇÃO NOVA | SIGNAL TYPE | TYPE SEVERIDADE | DIRECTION | MM | FUNÇÃO | VALOR | CONTROL CODE | SEVERIDADE | Funcionamento | LINHA | BARRA | TRANSFORMADOR | ALIMENTADOR | TRANSFERÊNCIA
CMDE | PROPRIEDADE DO COMANDO | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | CMD_CEEE@CMD_RGE___CEEE@RGE___Custom___INV___admsINV_S_TC_SA
CCIC | CHAVE DE COMANDO ICCP | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | CMD_RGE@null___RGE@CPFLT___Custom_S_TC_SS_CPFLT |  |  |  |  | Chave Virtual para seleção de quem está com o controle dos equipamentos (intertrava comandos no SAGE)
20A | 20 - PROTECAO DIFERENCIAL DE CORRENTE (FASE A) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA |  |  |  |  | PROTECAO DIFERENCIAL QUE MONITORA A DIFERENCA ENTRE CORRENTES DE ENTRADA E SAIDA EM TRANSFORMADORES E GERADORES. DETECTA FALHAS INTERNAS COMPARANDO CORRENTES NOS TERMINAIS DE UM EQUIPAMENTO.
20CA | 20 - PROTECAO DIFERENCIAL DE CORRENTE (CORRENTE AUXILIAR) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
20TA | 20 - PROTECAO DIFERENCIAL DE CORRENTE (TEMPO A) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
20T | 20 - PROTECAO DIFERENCIAL DE CORRENTE (TEMPO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
20C | 20 - PROTECAO DIFERENCIAL DE CORRENTE (FASE C) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
20D | 20 - PROTECAO DIFERENCIAL DE CORRENTE (DIRECIONAL) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
20CD | 20 - PROTECAO DIFERENCIAL DE CORRENTE (CORRENTE DIFERENCIAL) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
20TD | 20 - PROTECAO DIFERENCIAL DE CORRENTE (TEMPO DIFERENCIAL) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
20T1 | 20 - PROTECAO DIFERENCIAL DE CORRENTE (TEMPO 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
20T2 | 20 - PROTECAO DIFERENCIAL DE CORRENTE (TEMPO 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
20TC | 20 - PROTECAO DIFERENCIAL DE CORRENTE (TEMPO C) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
INTR | 20 63 87 - PROTECOES INTRINSECAS | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
2087T | 20 - PROTECAO DIFERENCIAL DE CORRENTE (87T) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
263A | 26 - PROTECAO TERMICA DE EQUIPAMENTO (3A) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  |  |  | MONITORA TEMPERATURA DE EQUIPAMENTOS COMO TRANSFORMADORES E GERADORES. DETECTA CONDICOES DE SOBRETEMPERATURA USANDO SENSORES TERMICOS OU MODELOS DE ELEVACAO DE TEMPERATURA.
2063 | 20 - PROTECAO DIFERENCIAL DE CORRENTE (63) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
206T | 20 - PROTECAO DIFERENCIAL DE CORRENTE (6T) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21D | 21 - RELE DE DISTANCIA (IMPEDANCIA) (DIRECIONAL) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA |  |  |  |  | PROTECAO DE LINHAS DE TRANSMISSAO BASEADA EM MEDICAO DE IMPEDANCIA/DISTANCIA. OPERA POR ZONAS DE PROTECAO E OFERECE PROTECAO ESCALONADA. SENSIVEL A VARIACOES DE IMPEDANCIA DA LINHA.
21 | 21 - RELE DE DISTANCIA (IMPEDANCIA) | Enabled | FUNCÕES/43/PARALELISMO | Read | null@null___INCLUIDO@EXCLUIDO___Enabled_S_TS_SS
21 | 21 - RELE DE DISTANCIA (IMPEDANCIA) | Enabled | FUNCÕES/43/PARALELISMO | ReadWrite | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS
21_T | 21 - RELE DE DISTANCIA (IMPEDANCIA) (_T) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21EF | 21 - RELE DE DISTANCIA (IMPEDANCIA) (ENTRADA FALHA) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21EM | 21 - RELE DE DISTANCIA (IMPEDANCIA) (ENTRADA MULTIPLA) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21FA | 21 - RELE DE DISTANCIA (IMPEDANCIA) (FASE A) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21FB | 21 - RELE DE DISTANCIA (IMPEDANCIA) (FASE B) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21FC | 21 - RELE DE DISTANCIA (IMPEDANCIA) (FASE C) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21MO | 21 - RELE DE DISTANCIA (IMPEDANCIA) (MO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21MF | 21 - RELE DE DISTANCIA (IMPEDANCIA) (MF) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21N | 21 - RELE DE DISTANCIA (IMPEDANCIA) (NEUTRO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21F1 | 21 - RELE DE DISTANCIA (IMPEDANCIA) (FASE 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21F2 | 21 - RELE DE DISTANCIA (IMPEDANCIA) (FASE 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21F3 | 21 - RELE DE DISTANCIA (IMPEDANCIA) (FASE 3) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21F4 | 21 - RELE DE DISTANCIA (IMPEDANCIA) (FASE 4) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21N1 | 21 - RELE DE DISTANCIA (IMPEDANCIA) (NEUTRO ZONA 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21N2 | 21 - RELE DE DISTANCIA (IMPEDANCIA) (NEUTRO ZONA 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21N3 | 21 - RELE DE DISTANCIA (IMPEDANCIA) (NEUTRO ZONA 3) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21N4 | 21 - RELE DE DISTANCIA (IMPEDANCIA) (NEUTRO ZONA 4) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21Z1 | 21 - RELE DE DISTANCIA (IMPEDANCIA) (ZONA 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21Z2 | 21 - RELE DE DISTANCIA (IMPEDANCIA) (ZONA 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21Z3 | 21 - RELE DE DISTANCIA (IMPEDANCIA) (ZONA 3) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21Z4 | 21 - RELE DE DISTANCIA (IMPEDANCIA) (ZONA 4) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
21Z5 | 21 - RELE DE DISTANCIA (IMPEDANCIA) (ZONA 5) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
24I | 24 - RELE DE SOBRECORRENTE COM RESET DE SOBRECARGA (INTENSIDADE) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  |  |  | PROTECAO DE SOBRECORRENTE COM CAPACIDADE DE RESET (RESETABLE). MONITORA CORRENTE CONTINUA E OFERECE PROTECAO CONTRA SOBRECARGAS COM MECANISMO DE REINICIALIZACAO AUTOMATICA.
24I1 | 24 - RELE DE SOBRECORRENTE COM RESET DE SOBRECARGA (INTENSIDADE 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
24I2 | 24 - RELE DE SOBRECORRENTE COM RESET DE SOBRECARGA (INTENSIDADE 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
24T | 24 - RELE DE SOBRECORRENTE COM RESET DE SOBRECARGA (TEMPO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
24T1 | 24 - RELE DE SOBRECORRENTE COM RESET DE SOBRECARGA (TEMPO 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
24T2 | 24 - RELE DE SOBRECORRENTE COM RESET DE SOBRECARGA (TEMPO 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
24 | 24 - RELE DE SOBRECORRENTE COM RESET DE SOBRECARGA | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
25ER | 25 - RELE DE SINCRONISMO OU VERIFICACAO DE SINCRONISMO (EFEITO REVERSO) | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB |  |  |  |  | SUPERVISIONA SINCRONISMO ENTRE SISTEMA E MAQUINA SINCRONA. CONTROLA CONDICOES DE ACOPLAMENTO PARA EVITAR CONEXAO FORA DE FASE. MONITORA ANGULO, MAGNITUDE E FREQUENCIA.
25CA | 25 - RELE DE SINCRONISMO OU VERIFICACAO DE SINCRONISMO (CORRENTE AUXILIAR) | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
25IE | 25 - RELE DE SINCRONISMO OU VERIFICACAO DE SINCRONISMO (IMPEDANCIA ENTRADA) | Enabled | FUNCÕES/43/PARALELISMO | ReadWrite | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS
25IE | 25 - RELE DE SINCRONISMO OU VERIFICACAO DE SINCRONISMO (IMPEDANCIA ENTRADA) | Enabled | FUNCÕES/43/PARALELISMO | Read | null@null___INCLUIDO@EXCLUIDO___Enabled_S_TS_SS
25AM | 25 - RELE DE SINCRONISMO OU VERIFICACAO DE SINCRONISMO (ALIMENTACAO MULTIPLA) | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___MANUAL@AUTOMATICO___Custom_S_TS_SS
25LR | 25 - RELE DE SINCRONISMO OU VERIFICACAO DE SINCRONISMO (LIMITE REVERSO) | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___REMOTO@LOCAL___Custom_S_TS_SS
25OK | 25 - RELE DE SINCRONISMO OU VERIFICACAO DE SINCRONISMO (CONFIRMACAO) | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
25AT | 25 - RELE DE SINCRONISMO OU VERIFICACAO DE SINCRONISMO (ALIMENTACAO TESTE) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
25FT | 25 - RELE DE SINCRONISMO OU VERIFICACAO DE SINCRONISMO (FALHA TESTE) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
25VT | 25 - RELE DE SINCRONISMO OU VERIFICACAO DE SINCRONISMO (VERIFICACAO TENSAO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
25_T | 25 - RELE DE SINCRONISMO OU VERIFICACAO DE SINCRONISMO (_T) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
TOA | 26 - ALARME TEMPERATURA OLEO | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
TOC | 26 - ALARME TEMPERATURA OLEO CDC | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
TOD | 26 - TRIP TEMPERATURA OLEO | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
TOEA | 26 49 - ALARME TEMPERATURA | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
2649 | 26 - PROTECAO TERMICA DE EQUIPAMENTO (49) | Enabled | FUNCÕES/43/PARALELISMO | ReadWrite | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS |  |  |  |  | Usado para indicar que houve o trip do disjuntor do alimentador, devido atuação da proteção por temperatura dos transformadores. Para verificar quais alimentadores possuem a função ativada, deve-se verificar a folha de ajustes da proteção.
2649 | 26 - PROTECAO TERMICA DE EQUIPAMENTO (49) | Enabled | FUNCÕES/43/PARALELISMO | Read | null@null___INCLUIDO@EXCLUIDO___Enabled_S_TS_SS |  |  |  |  | Usado nos transformadores, pra indicar o trip por temperatura (óleo ou enrolamento).
TOED | 26 49 - TRIP TEMPERATURA | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
27BL | 27 - RELE DE SUBTENSAO (BLOQUEIO) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA |  |  |  |  | MONITORA TENSAO DA REDE E OPERA QUANDO ESSA CAI ABAIXO DE VALOR PRE-AJUSTADO. PROTECAO CONTRA PERDA DE TENSAO E DESCONEXAO DE CIRCUITOS EM CONDICOES ANORMAIS.
27 | 27 - RELE DE SUBTENSAO | Enabled | FUNCÕES/43/PARALELISMO | ReadWrite | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS
27 | 27 - RELE DE SUBTENSAO | Enabled | FUNCÕES/43/PARALELISMO | Read | null@null___INCLUIDO@EXCLUIDO___Enabled_S_TS_SS
27BR | 27 - RELE DE SUBTENSAO (BLOQUEIO REVERSO) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
27CD | 27 - RELE DE SUBTENSAO (CORRENTE DIFERENCIAL) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
27E1 | 27 - RELE DE SUBTENSAO (ESTAGIO 1) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
27E2 | 27 - RELE DE SUBTENSAO (ESTAGIO 2) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
27AB | 27 - RELE DE SUBTENSAO (ABERTURA) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
27AC | 27 - RELE DE SUBTENSAO (FECHAMENTO) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
27BC | 27 - RELE DE SUBTENSAO (BLOQUEIO CHAVEAMENTO) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
27LT | 27 - RELE DE SUBTENSAO (LIMITE TEMPO) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
27TP | 27 - RELE DE SUBTENSAO (TIPO) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
27CA | 27 - RELE DE SUBTENSAO (CORRENTE AUXILIAR) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
27CC | 27 - RELE DE SUBTENSAO (COMANDO CHAVEAMENTO) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
27_T | 27 - RELE DE SUBTENSAO (_T) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
2759 | 27 - RELE DE SUBTENSAO (59) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
32 | 32 - RELE DE POTENCIA DIRECIONAL | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  |  |  | MONITORA FLUXO DE POTENCIA ATIVA EM UMA DIRECAO ESPECIFICA. PROTECAO CONTRA FLUXO REVERSO EM GERADORES E ALIMENTADORES. SENSIVEL A MAGNITUDE E DIRECAO DA POTENCIA.
43AM | 43 - RELE DE TRANSFERENCIA MANUAL OU SELETOR (ALIMENTACAO MULTIPLA) | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___MANUAL@AUTOMATICO___Custom_S_TS_SS |  |  |  |  | CONTROLA TRANSFERENCIA MANUAL ENTRE FONTES DE ALIMENTACAO. UTILIZADO EM OPERACOES DE CHAVEAMENTO E SELECAO DE CIRCUITOS POR COMANDO DO OPERADOR.
43LR | 43 - RELE DE TRANSFERENCIA MANUAL OU SELETOR (LIMITE REVERSO) | Local | FUNCÕES/43/PARALELISMO | Read | null@null___REMOTO@LOCAL__Local_S_TS_SS
RLCD | 43 - CHAVE LOCAL REMOTO COMUTADOR | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___REMOTO@LOCAL___Custom_S_TS_SS
90LR | 90 - DISPOSITIVO REGULADOR (LIMITE REVERSO) | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___REMOTO@LOCAL___Custom_S_TS_SS |  |  |  |  | CONTROLA E REGULA PARAMETROS DE SISTEMA COMO TENSAO, POTENCIA OU FREQUENCIA. MANTEM VALORES DENTRO DE FAIXA PRE-AJUSTADA ATRAVES DE ATUACAO CONTINUA.
PLLR | 43 - CHAVE LOCAL REMOTO RELE PARALELISMO | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___REMOTO@LOCAL___Custom_S_TS_SS
43TR | 43 - RELE DE TRANSFERENCIA MANUAL OU SELETOR (TRANSFERENCIA) | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___REMOTO@LOCAL___Custom_S_TS_SS
43VF | 43 - RELE DE TRANSFERENCIA MANUAL OU SELETOR (VERIFICACAO FALHA) | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___REMOTO@LOCAL___Custom_S_TS_SS
43EP | 43 - RELE DE TRANSFERENCIA MANUAL OU SELETOR (ENTRADA PRIMARIA) | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___REMOTO@LOCAL___Custom_S_TS_SS
43RT | 43 - RELE DE TRANSFERENCIA MANUAL OU SELETOR (RETORNO) | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___REMOTO@LOCAL___Custom_S_TS_SS
43TC | 43 - RELE DE TRANSFERENCIA MANUAL OU SELETOR (TEMPO C) | Local | FUNCÕES/43/PARALELISMO | Read | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS
43TP | 43 - RELE DE TRANSFERENCIA MANUAL OU SELETOR (TIPO) | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___INCLUIDO@EXCLUIDO___Custom_S_TS_SS
46 | 46 - RELE DE SEQUENCIA REVERSA OU DESBALANCO DE FASE | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  |  |  | DETECTA SEQUENCIA REVERSA DE FASES (RST EM VEZ DE STR) OU DESBALANCO ENTRE FASES. PROTECAO PARA MOTORES E EQUIPAMENTOS SENSIVEIS A SEQUENCIA DE FASES.
46E1 | 46 - RELE DE SEQUENCIA REVERSA OU DESBALANCO DE FASE (ESTAGIO 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
TEA | 49 - ALARME TEMPERATURA ENROLAMENTO | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
TED | 49 - TRIP TEMPERATURA ENROLAMENTO | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
50CD | 50 - RELE DE SOBRECORRENTE INSTANTANEA (CORRENTE DIFERENCIAL) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  |  |  | DETECTA SOBRECORRENTE COM OPERACAO IMEDIATA (SEM ATRASO DE TEMPO). PROTECAO DE ALTA VELOCIDADE CONTRA CURTOS-CIRCUITOS. USADO PARA PROTECAO PRIMARIA RAPIDA DE CIRCUITOS.
50_1 | 50 - RELE DE SOBRECORRENTE INSTANTANEA (_1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
50_2 | 50 - RELE DE SOBRECORRENTE INSTANTANEA (_2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
50BF | 50 - RELE DE SOBRECORRENTE INSTANTANEA (BLOQUEIO FALHA DISJUNTOR) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
50F | 50 - RELE DE SOBRECORRENTE INSTANTANEA (FASE) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
50FA | 50 - RELE DE SOBRECORRENTE INSTANTANEA (FASE A) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
50FB | 50 - RELE DE SOBRECORRENTE INSTANTANEA (FASE B) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
50FC | 50 - RELE DE SOBRECORRENTE INSTANTANEA (FASE C) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
50CA | 50 - RELE DE SOBRECORRENTE INSTANTANEA (CORRENTE AUXILIAR) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
50F1 | 50 - RELE DE SOBRECORRENTE INSTANTANEA (FASE 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
50F2 | 50 - RELE DE SOBRECORRENTE INSTANTANEA (FASE 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
50F3 | 50 - RELE DE SOBRECORRENTE INSTANTANEA (FASE 3) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
50FN | 50 - RELE DE SOBRECORRENTE INSTANTANEA (FASE-NEUTRO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
50N | 50 - RELE DE SOBRECORRENTE INSTANTANEA (NEUTRO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
50N1 | 50 - RELE DE SOBRECORRENTE INSTANTANEA (NEUTRO ZONA 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
50N2 | 50 - RELE DE SOBRECORRENTE INSTANTANEA (NEUTRO ZONA 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
50N3 | 50 - RELE DE SOBRECORRENTE INSTANTANEA (NEUTRO ZONA 3) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
5BKP | 50 51 - SOBRECORRENTE BACKUP | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
5F | 50 51 - SOBRECORRENTE FASE | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
5FA | 50 51 - SOBRECORRENTE FASE A | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
5FB | 50 51 - SOBRECORRENTE FASE B | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
5FC | 50 51 - SOBRECORRENTE FASE C | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
5FN | 50 51 - SOBRECORRENTE FASE NEUTRO | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
5FN1 | 50 51 - SOBRECORRENTE FASE NEUTRO 1 | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
5FN2 | 50 51 - SOBRECORRENTE FASE NEUTRO 2 | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
5N | 50 51 - SOBRECORRENTE NEUTRO | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
5NBK | 50 51 - SOBRECORRENTE NEUTRO BACKUP | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
561F | 50 51 61 - FASE | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
51N | 51 - RELE DE TEMPO INVERSO COM SOBRECORRENTE AC (NEUTRO) | Enabled | FUNCÕES/43/PARALELISMO | ReadWrite | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS |  |  |  |  | PROTECAO DE SOBRECORRENTE COM CARACTERISTICA DE TEMPO INVERSO. ATRASO DE TEMPO DEPENDE DA MAGNITUDE DA CORRENTE. PROTECAO COORDENADA EM CASCATA COM RELES DOWNSTREAM.
51N | 51 - RELE DE TEMPO INVERSO COM SOBRECORRENTE AC (NEUTRO) | Enabled | FUNCÕES/43/PARALELISMO | Read | null@null___INCLUIDO@EXCLUIDO___Enabled_S_TS_SS
51F | 51 - RELE DE TEMPO INVERSO COM SOBRECORRENTE AC (FASE) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
51FA | 51 - RELE DE TEMPO INVERSO COM SOBRECORRENTE AC (FASE A) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
51FB | 51 - RELE DE TEMPO INVERSO COM SOBRECORRENTE AC (FASE B) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
51FC | 51 - RELE DE TEMPO INVERSO COM SOBRECORRENTE AC (FASE C) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
51CA | 51 - RELE DE TEMPO INVERSO COM SOBRECORRENTE AC (CORRENTE AUXILIAR) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
51F1 | 51 - RELE DE TEMPO INVERSO COM SOBRECORRENTE AC (FASE 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
51F2 | 51 - RELE DE TEMPO INVERSO COM SOBRECORRENTE AC (FASE 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
51FN | 51 - RELE DE TEMPO INVERSO COM SOBRECORRENTE AC (FASE-NEUTRO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
51NL | 51 - RELE DE TEMPO INVERSO COM SOBRECORRENTE AC (NEUTRO COM BLOQUEIO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
51N1 | 51 - RELE DE TEMPO INVERSO COM SOBRECORRENTE AC (NEUTRO ZONA 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
51N2 | 51 - RELE DE TEMPO INVERSO COM SOBRECORRENTE AC (NEUTRO ZONA 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
51V | 51 - RELE DE TEMPO INVERSO COM SOBRECORRENTE AC (TENSAO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
5161 | 51 - RELE DE TEMPO INVERSO COM SOBRECORRENTE AC (61) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
59 | 59 - RELE DE SOBRETENSAO | Enabled | FUNCÕES/43/PARALELISMO | ReadWrite | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS |  |  |  |  | MONITORA TENSAO DA REDE E OPERA QUANDO ESSA ULTRAPASSA VALOR PRE-AJUSTADO. PROTECAO CONTRA SOBRETENSAO E CONEXAO INDEVIDA DE CIRCUITOS EM CONDICOES ANORMAIS.
59 | 59 - RELE DE SOBRETENSAO | Enabled | FUNCÕES/43/PARALELISMO | Read | null@null___INCLUIDO@EXCLUIDO___Enabled_S_TS_SS
59A | 59 - RELE DE SOBRETENSAO (FASE A) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
59CD | 59 - RELE DE SOBRETENSAO (CORRENTE DIFERENCIAL) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
59E1 | 59 - RELE DE SOBRETENSAO (ESTAGIO 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
59E2 | 59 - RELE DE SOBRETENSAO (ESTAGIO 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
59E3 | 59 - RELE DE SOBRETENSAO (ESTAGIO 3) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
59E4 | 59 - RELE DE SOBRETENSAO (ESTAGIO 4) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
59E5 | 59 - RELE DE SOBRETENSAO (ESTAGIO 5) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
59I | 59 - RELE DE SOBRETENSAO (INTENSIDADE) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
59N | 59 - RELE DE SOBRETENSAO (NEUTRO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
59_T | 59 - RELE DE SOBRETENSAO (_T) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
61 | 61 - RELE DE RETORNO DE POTENCIA OU POTENCIA REVERSA | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  |  |  | DETECTA INVERSAO DE FLUXO DE POTENCIA ATIVA. PROTECAO DE GERADORES CONTRA POTENCIA REVERSA INDICANDO PERDA DE ATUACAO OU FALHA DE MAQUINA MOTRIZ.
61_1 | 61 - RELE DE RETORNO DE POTENCIA OU POTENCIA REVERSA (_1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
61_2 | 61 - RELE DE RETORNO DE POTENCIA OU POTENCIA REVERSA (_2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
61I | 61 - RELE DE RETORNO DE POTENCIA OU POTENCIA REVERSA (INTENSIDADE) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
61N | 61 - RELE DE RETORNO DE POTENCIA OU POTENCIA REVERSA (NEUTRO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
61T | 61 - RELE DE RETORNO DE POTENCIA OU POTENCIA REVERSA (TEMPO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
62BF | 62 - RELE DE ATRASO DE PARADA OU DESLIGAMENTO (BLOQUEIO FALHA DISJUNTOR) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  |  |  | FORNECE ATRASO DE TEMPO PROGRAMAVEL PARA OPERACOES DE PARADA OU DESLIGAMENTO. CONTROLA SEQUENCIA TEMPORIZADAS DE EVENTOS DE PROTECAO.
BFAT | 62 - FALHA DISJUNTOR BLOQUEIO AT | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
BFP1 | 62 - FALHA DISJUNTOR BLOQUEIO BARRA P1 | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
BFP2 | 62 - FALHA DISJUNTOR BLOQUEIO BARRA P2 | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
BFP3 | 62 - FALHA DISJUNTOR BLOQUEIO BARRA P3 | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
BFBT | 62 - FALHA DISJUNTOR BLOQUEIO ALIMENTADORES | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
63CA | 63 - RELE DE PRESSAO (CORRENTE AUXILIAR) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA |  |  |  |  | MONITORA PRESSAO DE GASES OU LIQUIDOS EM EQUIPAMENTOS (EX: TRANSFORMADORES COM CONSERVADOR). PROTECAO CONTRA AUMENTO ANORMAL DE PRESSAO INDICANDO FALHAS INTERNAS.
63A | 63 - RELE DE PRESSAO (FASE A) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
63TA | 63 - RELE DE PRESSAO (TEMPO A) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
63TC | 63 - RELE DE PRESSAO (TEMPO C) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
63CD | 63 - RELE DE PRESSAO (CORRENTE DIFERENCIAL) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
63C | 63 - RELE DE PRESSAO (FASE C) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
63TD | 63 - RELE DE PRESSAO (TEMPO DIFERENCIAL) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
63T | 63 - RELE DE PRESSAO (TEMPO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67FTD | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (FALHA TESTE DIRECIONAL) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  |  |  | PROTECAO DE SOBRECORRENTE DIRECCIONADA QUE OPERA APENAS PARA CORRENTES ACIMA DO AJUSTE EM DIRECAO ESPECIFICA. PERMITE COORDENACAO BIDIRECIONAL EM MALHAS DE DISTRIBUICAO.
67NTD | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (NEUTRO TEMPO DIRECIONAL) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67_1 | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (_1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67_2 | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (_2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67F | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (FASE) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67FA | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (FASE A) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67FB | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (FASE B) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67FC | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (FASE C) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67F1 | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (FASE 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67F2 | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (FASE 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67FT | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (FALHA TESTE) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67P1 | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (PILOT 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67P2 | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (PILOT 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67N | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (NEUTRO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67N1 | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (NEUTRO ZONA 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67N2 | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (NEUTRO ZONA 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67NT | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (NEUTRO TEMPO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67NT1 | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (NEUTRO TEMPO 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67NT2 | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (NEUTRO TEMPO 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67FTR | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (FALHA TESTE REVERSO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67NTR | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (NEUTRO TEMPO REVERSO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67 | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC | Enabled | FUNCÕES/43/PARALELISMO | ReadWrite | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS
67 | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC | Enabled | FUNCÕES/43/PARALELISMO | Read | null@null___INCLUIDO@EXCLUIDO___Enabled_S_TS_SS
67NX | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (NEUTRO AUXILIAR) | Enabled | FUNCÕES/43/PARALELISMO | ReadWrite | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS
67NX | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (NEUTRO AUXILIAR) | Enabled | FUNCÕES/43/PARALELISMO | Read | null@null___INCLUIDO@EXCLUIDO___Enabled_S_TS_SS
67_T | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (_T) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67FD | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (FD) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67ND | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (NEUTRO DIRECIONAL) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67FR | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (FALHA REVERSO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
67NR | 67 - RELE DE SOBRECORRENTE DIRECIONAL AC (NEUTRO REVERSO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
71H | 71 - RELE DE NIVEL DE LIQUIDO OU GAS (ALTO) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA |  |  |  |  | MONITORA NIVEL DE LIQUIDO OU GAS EM RESERVATORIOS E CONSERVADORES DE EQUIPAMENTOS. ALERTA OU DESLIGA EQUIPAMENTOS QUANDO NIVEL ESTA FORA DOS LIMITES NORMAIS.
71CH | 71 - RELE DE NIVEL DE LIQUIDO OU GAS (CHEIA) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
71HI | 71 - RELE DE NIVEL DE LIQUIDO OU GAS (LIMITE ALTO) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
71TH | 71 - RELE DE NIVEL DE LIQUIDO OU GAS (TEMPO ALTO) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
71L | 71 - RELE DE NIVEL DE LIQUIDO OU GAS (BAIXO) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
71CL | 71 - RELE DE NIVEL DE LIQUIDO OU GAS (LIMITE CHEIA) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
71LO | 71 - RELE DE NIVEL DE LIQUIDO OU GAS (LIMITE BAIXO) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
71TL | 71 - RELE DE NIVEL DE LIQUIDO OU GAS (TEMPO BAIXO) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
71 | 71 - RELE DE NIVEL DE LIQUIDO OU GAS | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
71C | 71 - RELE DE NIVEL DE LIQUIDO OU GAS (FASE C) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
71TC | 71 - RELE DE NIVEL DE LIQUIDO OU GAS (TEMPO C) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
71T | 71 - RELE DE NIVEL DE LIQUIDO OU GAS (TEMPO) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
78_T | 78 - RELE DE MEDICAO DE ANGULO DE FASE (_T) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  |  |  | MEDE E SUPERVISIONA ANGULO DE FASE ENTRE TENSOES OU CORRENTES. PROTECAO CONTRA DESVIOS DE FASE E DESINCRONISMO. USADO EM SISTEMAS DE PROTECAO DE ESTABILIDADE.
78VS | 78 - RELE DE MEDICAO DE ANGULO DE FASE (VERIFICACAO STATUS) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
79 | 79 - RELE DE RELIGA AUTOMATICA AC | ReclosingEnabled | FUNCÕES/43/PARALELISMO | ReadWrite | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS |  |  |  |  | COMANDA RELIGAMENTO AUTOMATICO APOS OPERACAO DE PROTECAO. RESTAURA CIRCUITO APOS FALHAS TRANSITORIAS. INCLUI ATRASOS E CONTADORES DE CICLOS DE RELIGA.
79 | 79 - RELE DE RELIGA AUTOMATICA AC | ReclosingEnabled | FUNCÕES/43/PARALELISMO | Read | null@null___INCLUIDO@EXCLUIDO___Enabled_S_TS_SS
79_1 | 79 - RELE DE RELIGA AUTOMATICA AC (_1) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
79LO | 79 - RELE DE RELIGA AUTOMATICA AC (LIMITE BAIXO) | RecloserLockout | PROT | Read | null@null___NORMAL@ATUADO___RecloserLockout_S_TS_SA
79OK | 79 - RELE DE RELIGA AUTOMATICA AC (CONFIRMACAO) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
79_EXC | 79 - RELE DE RELIGA AUTOMATICA AC (_EXC) | Custom | PROT | Write | null@EXCLUIR___null@null___ReclosingEnabled___admsINV_D_TC_SS
79_INC | 79 - RELE DE RELIGA AUTOMATICA AC (_INC) | Custom | PROT | Write | INCLUIR@null___null@null___ReclosingEnabled___admsINV_D_TC_SS
79RE | 79 - RELE DE RELIGA AUTOMATICA AC (RELIGA EXCLUIDA) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
79TF | 79 - RELE DE RELIGA AUTOMATICA AC (TESTE FALHA) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
81 | 81 - RELE DE FREQUENCIA | Enabled | FUNCÕES/43/PARALELISMO | ReadWrite | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS |  |  |  |  | MONITORA FREQUENCIA DA REDE. DETECTA SUB/SOBREFREQUENCIA INDICANDO DESBALANCEAMENTO GERADOR-CARGA. PROTECAO CONTRA INSTABILIDADE DO SISTEMA E FALHAS DE SUPRIMENTO.
81 | 81 - RELE DE FREQUENCIA | Enabled | FUNCÕES/43/PARALELISMO | Read | null@null___INCLUIDO@EXCLUIDO___Enabled_S_TS_SS
81SO | 81 - RELE DE FREQUENCIA (SOBRE) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
81O1 | 81 - RELE DE FREQUENCIA (SOBRE FREQUENCIA 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
81O2 | 81 - RELE DE FREQUENCIA (SOBRE FREQUENCIA 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
81SU | 81 - RELE DE FREQUENCIA (SUB) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
81_T | 81 - RELE DE FREQUENCIA (_T) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
81IE1 | 81 - RELE DE FREQUENCIA (IMPEDANCIA ENTRADA 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
81IE2 | 81 - RELE DE FREQUENCIA (IMPEDANCIA ENTRADA 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
81E1 | 81 - RELE DE FREQUENCIA (ESTAGIO 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
81E2 | 81 - RELE DE FREQUENCIA (ESTAGIO 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
81E3 | 81 - RELE DE FREQUENCIA (ESTAGIO 3) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
81E4 | 81 - RELE DE FREQUENCIA (ESTAGIO 4) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
81E5 | 81 - RELE DE FREQUENCIA (ESTAGIO 5) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
43TP | 43 - RELE DE TRANSFERENCIA MANUAL OU SELETOR (TIPO) | Custom | FUNCÕES/43/PARALELISMO | ReadWrite | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS
86 | 86 - RELE DE BLOQUEIO (TRIP-FREE) | Custom | PROT | Read | null@REARMAR___NORMAL@ATUADO___Custom_S_TS_SA |  |  |  |  | BLOQUEIA COMANDOS DE TRIP APOS OPERACAO. MANTEM ESTADO DE TRAVAMENTO ATE RESET MANUAL. PROTECAO CONTRA RELIGAMENTOS INTEMPESTIVOS.
86 | 86 - RELE DE BLOQUEIO (TRIP-FREE) | Custom | PROT | ReadWrite | REARMAR@null___NORMAL@ATUADO___Custom_S_TC_SA |  |  |  |  | Utilizado em transformadores, indica o defeito no equipamento.
86BF | 86 - RELE DE BLOQUEIO (TRIP-FREE) (BLOQUEIO FALHA DISJUNTOR) | Custom | PROT | Read | null@REARMAR___NORMAL@ATUADO___Custom_S_TS_SA |  |  |  |  | Utilizado em LTs, Barras e DJs, indica defeito no disjuntor
86BF | 86 - RELE DE BLOQUEIO (TRIP-FREE) (BLOQUEIO FALHA DISJUNTOR) | Custom | PROT | ReadWrite | REARMAR@null___NORMAL@ATUADO___Custom_S_TC_SA |  |  |  |  | Utilizado em LTs, Barras e DJs, indica defeito no disjuntor
86C | 86 - RELE DE BLOQUEIO (TRIP-FREE) (FASE C) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
86FL | 86 - RELE DE BLOQUEIO (TRIP-FREE) (FALHA LOCK) | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
87BL | 87 - RELE DE PROTECAO DIFERENCIAL (BLOQUEIO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  |  |  | COMPARA CORRENTES EM AMBOS OS LADOS DE UM EQUIPAMENTO (TRANSFORMADOR, GERADOR, LINHA). DETECTA FALHAS INTERNAS POR DESBALANCO DE CORRENTE DIFERENCIAL.
87A | 87 - RELE DE PROTECAO DIFERENCIAL (FASE A) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87B | 87 - RELE DE PROTECAO DIFERENCIAL (FASE B) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87C | 87 - RELE DE PROTECAO DIFERENCIAL (FASE C) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87_I | 87 - RELE DE PROTECAO DIFERENCIAL (_I) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87U | 87 - RELE DE PROTECAO DIFERENCIAL (U) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87U1 | 87 - RELE DE PROTECAO DIFERENCIAL (UNIDADE 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87U2 | 87 - RELE DE PROTECAO DIFERENCIAL (UNIDADE 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87R | 87 - RELE DE PROTECAO DIFERENCIAL (RECEPTOR) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87R1 | 87 - RELE DE PROTECAO DIFERENCIAL (RECEPTOR 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87R2 | 87 - RELE DE PROTECAO DIFERENCIAL (RECEPTOR 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87EF | 87 - RELE DE PROTECAO DIFERENCIAL (ENTRADA FALHA) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  |  |  | REF - Restricted Earth Fault
87RA | 87 - RELE DE PROTECAO DIFERENCIAL (RECEPTOR A) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87RB | 87 - RELE DE PROTECAO DIFERENCIAL (RECEPTOR B) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87RC | 87 - RELE DE PROTECAO DIFERENCIAL (RECEPTOR C) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87Q | 87 - RELE DE PROTECAO DIFERENCIAL (QUADRANTE) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87Q1 | 87 - RELE DE PROTECAO DIFERENCIAL (QUADRANTE 1) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87Q2 | 87 - RELE DE PROTECAO DIFERENCIAL (QUADRANTE 2) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
8751 | 87 - RELE DE PROTECAO DIFERENCIAL (51) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87TA | 87 - RELE DE PROTECAO DIFERENCIAL (TEMPO A) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87TB | 87 - RELE DE PROTECAO DIFERENCIAL (TEMPO B) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87TC | 87 - RELE DE PROTECAO DIFERENCIAL (TEMPO C) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87G | 87 - RELE DE PROTECAO DIFERENCIAL (GERADOR) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87 | 87 - RELE DE PROTECAO DIFERENCIAL | Enabled | FUNCÕES/43/PARALELISMO | ReadWrite | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS
87 | 87 - RELE DE PROTECAO DIFERENCIAL | Enabled | FUNCÕES/43/PARALELISMO | Read | null@null___INCLUIDO@EXCLUIDO___Enabled_S_TS_SS
87_T | 87 - RELE DE PROTECAO DIFERENCIAL (_T) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87TT | 87 - RELE DE PROTECAO DIFERENCIAL (TEMPO TEMPO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
87LT | 87 - RELE DE PROTECAO DIFERENCIAL (LIMITE TEMPO) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
8750 | 87 - RELE DE PROTECAO DIFERENCIAL (50) | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
90I | 90 - DISPOSITIVO REGULADOR (INTENSIDADE) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
90V | 90 - DISPOSITIVO REGULADOR (TENSAO) | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
COMA | 90 - POSICAO COMANDADO | Parallel | FUNCÕES/43/PARALELISMO | ReadWrite | null@COMANDADO___DESATIVADO@ATIVADO___Custom_S_TC_SS
COMA | 90 - POSICAO COMANDADO | Parallel | FUNCÕES/43/PARALELISMO | Read | null@null___DESATIVADO@ATIVADO___Custom_S_TS_SS
90DP | 90 - DISPOSITIVO REGULADOR (DISPOSITIVO PRIMARIO) | Custom | PROT | Read | null@null___NORMAL@DISCREPANCIA___Custom_S_TS_SA
90FU | 90 - DISPOSITIVO REGULADOR (FUSIVEL) | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
R90 | 90 - FUNCAO REGULADOR | Enabled | FUNCÕES/43/PARALELISMO | ReadWrite | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS
TAL | TAL - FUNCAO TRANSFERENCIA AUTOMATICA DE LINHA | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___INCLUIDO@EXCLUIDO___Custom_S_TS_SS
TPPM | TPPM - FUNCAO TRANSFERENCIA COM PARALELISMO MOMENTANEO | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___INCLUIDO@EXCLUIDO___Custom_S_TS_SS
R90 | 90 - FUNCAO REGULADOR | Enabled | FUNCÕES/43/PARALELISMO | Read | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TS_SS
INDI | 90 - POSICAO INDIVIDUAL | Custom | FUNCÕES/43/PARALELISMO | ReadWrite | null@MESTRE___DESATIVADO@ATIVADO___Custom_S_TC_SS
INDI | 90 - POSICAO INDIVIDUAL | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___DESATIVADO@ATIVADO___Custom_S_TS_SS
MEST | 90 - POSICAO MESTRE | Custom | FUNCÕES/43/PARALELISMO | ReadWrite | null@INDIVIDUAL___DESATIVADO@ATIVADO___Custom_S_TC_SS
MEST | 90 - POSICAO MESTRE | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___DESATIVADO@ATIVADO___Custom_S_TS_SS
94 | 94 - RELE DE DISPARO OU DISPARO LIVRE | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  |  |  | RELE AUXILIAR QUE COMANDA DISPARO FINAL DE DISJUNTORES. AMPLIFICA SINAL DE PROTECAO E OFERECE GARANTIA DE ABERTURA INDEPENDENTE DE OUTRAS PROTECOES (TRIP-FREE).
ABBN | ABERTURA PELA BOBINA DE NEUTRO | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
81U1 | 81 - RELE DE FREQUENCIA (UNIDADE 1) | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
81U2 | 81 - RELE DE FREQUENCIA (UNIDADE 2) | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
81U3 | 81 - RELE DE FREQUENCIA (SUB FREQUENCIA 3) | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
81U4 | 81 - RELE DE FREQUENCIA (SUB FREQUENCIA 4) | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
81U5 | 81 - RELE DE FREQUENCIA (SUB FREQUENCIA 5) | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ1 | AJUSTE PARA AL1 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ12 | AJUSTE PARA AL12 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ13 | AJUSTE PARA AL13 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ14 | AJUSTE PARA AL14 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ15 | AJUSTE PARA AL15 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ16 | AJUSTE PARA AL16 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ17 | AJUSTE PARA AL17 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ18 | AJUSTE PARA AL18 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ2 | AJUSTE PARA AL2 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ21 | AJUSTE PARA AL21 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ25 | AJUSTE PARA AL25 | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV
AJ26 | AJUSTE PARA AL26 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ27 | AJUSTE PARA AL27 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ28 | AJUSTE PARA AL28 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ3 | AJUSTE PARA AL3 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ31 | AJUSTE PARA AL31 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ32 | AJUSTE PARA AL32 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ33 | AJUSTE PARA AL33 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ34 | AJUSTE PARA AL34 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ4 | AJUSTE PARA AL4 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ5 | AJUSTE PARA AL5 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ6 | AJUSTE PARA AL6 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ7 | AJUSTE PARA AL7 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJ8 | AJUSTE PARA AL8 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
AJG1 | AJUSTE PARA GRUPO 1 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESATIVADO@ATIVADO___Custom_S_TS_SV
AJG1 | AJUSTE PARA GRUPO 1 | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TS_SV
AJG2 | AJUSTE PARA GRUPO 2 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESATIVADO@ATIVADO___Custom_S_TS_SV
AJG2 | AJUSTE PARA GRUPO 2 | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TS_SV
AJG3 | AJUSTE PARA GRUPO 3 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESATIVADO@ATIVADO___Custom_S_TS_SV
AJG3 | AJUSTE PARA GRUPO 3 | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TS_SV
AJG4 | AJUSTE PARA GRUPO 4 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESATIVADO@ATIVADO___Custom_S_TS_SV
AJG4 | AJUSTE PARA GRUPO 4 | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TS_SV
AJG5 | AJUSTE PARA GRUPO 5 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESATIVADO@ATIVADO___Custom_S_TS_SV
AJG5 | AJUSTE PARA GRUPO 5 | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TS_SV
AJG6 | AJUSTE PARA GRUPO 6 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESATIVADO@ATIVADO___Custom_S_TS_SV
AJG6 | AJUSTE PARA GRUPO 6 | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TS_SV
AJNM | AJUSTE PARA GRUPO NORMAL | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESATIVADO@ATIVADO___Custom_S_TS_SV
BATA | ALARME BATERIA | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
ALM | ALARME GERAL | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
PRES | ALARME PREDIAL | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TS_SV
PRES | ALARME PREDIAL | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESATIVADO@ATIVADO___Custom_S_TS_SV
PREX | ALARME PREDIAL PRESENCA EXTERNA | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SV
PRIN | ALARME PREDIAL PRESENCA INTERNA | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SV
PROL | ALARME PRESSAO DE OLEO | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
RETA | ALARME RETIFICADOR | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
SIRE | ALARME SONORO | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___NORMAL@DISPARADA___Custom_S_TS_SV
DSAB | ALARMES DESABILITADOS | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
85 | 85 - RELE DE PORTADORA OU FIO PILOTO | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA |  |  |  |  | COMUNICA STATUS DE PROTECAO ENTRE TERMINAIS DE LINHAS VIA PORTADORA OU FIO PILOTO. COORDENACAO DE PROTECAO DE ALTA VELOCIDADE ENTRE SUBESTACOES.
ANR | ANOMALIA REDE | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
ZERO | AUTO ZERO | Custom | FUNCÕES/43/PARALELISMO | Write | ZERAR@null___null@null___Custom_S_TC_SS
AUTO | FUNCAO AUTOMATISMO | Custom | FUNCÕES/43/PARALELISMO | ReadWrite | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS
AUTO | FUNCAO AUTOMATISMO | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___INCLUIDO@EXCLUIDO___Custom_S_TS_SS
AUTC | AUTOMATISMO | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
AUTD | AUTOMATISMO DESLIGA | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SS
AUTL | AUTOMATISMO LIGA | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SS
90VF | 90 - DISPOSITIVO REGULADOR (VERIFICACAO FALHA) | Enabled | FUNCÕES/43/PARALELISMO | ReadWrite | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS
90VF | 90 - DISPOSITIVO REGULADOR (VERIFICACAO FALHA) | Enabled | FUNCÕES/43/PARALELISMO | Read | null@null___INCLUIDO@EXCLUIDO___Enabled_S_TS_SS
BXAR | BAIXA PRESSAO AR COMPRIMIDO | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
SF6 | BAIXA PRESSAO SF6 | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
SF6A | ALARME BAIXA PRESSAO SF6 | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
SF6B | BLOQUEIO BAIXA PRESSAO SF6 | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
BADC | BATERIA EM DESCARGA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___CARGA@DESCARGA___Custom_S_TS_SB
B5M | BLOQUEIO 5 MINUTOS | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
BAB | BLOQUEIO ABERTURA BAIXO AR COMPRIMIDO | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
BCDC | BLOQUEIO CDC | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
BLA | BLOQUEIO COMANDO ABERTURA | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
BFC | BLOQUEIO COMANDO FECHAMENTO | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
BLDJ | BLOQUEIO DISJUNTOR | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
BSEC | BLOQUEIO MANOBRA SECCIONADORA | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
BLV | BLOQUEIO POR TENSAO DE RETORNO | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
ANP | ANOMALIA PROTECAO | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
BBAB | BOBINA ABERTURA | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
BBA1 | BOBINA ABERTURA 1 | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
BBA2 | BOBINA ABERTURA 2 | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
BAF1 | BOBINA ABERTURA FECHAMENTO 1 | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
BAF2 | BOBINA ABERTURA FECHAMENTO 2 | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
BBAF | BOBINA ABERTURA OU FECHAMENTO | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
BBFC | BOBINA FECHAMENTO | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
BAVL | CARREGAMENTO DA BATERIA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___FALHA@OPERANDO___Custom_S_TS_SB
CDAM | CDC AUTOMATICO MANUAL | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___AUTOMATICO@MANUAL___Custom_S_TS_SS
CDLA | CDC LOCAL AUTOMATICO | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___DESATIVADO@ATIVADO___Custom_S_TS_SS
CDLM | CDC LOCAL MANUAL | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___DESATIVADO@ATIVADO___Custom_S_TS_SS
CDCO | CDC MODO DE OPERACAO | Parallel | FUNCÕES/43/PARALELISMO | ReadWrite | MESTRE@INDIVIDUAL@COMANDO___MESTRE@INDIVIDUAL@COMANDO___Parallel___admsINV_D_TC
CDRA | CDC REMOTO AUTOMATICO | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___DESATIVADO@ATIVADO___Custom_S_TS_SS
CDRM | CDC REMOTO MANUAL | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___DESATIVADO@ATIVADO___Custom_S_TS_SS
DEFC | CENTRAL DE ALARME DEFEITO | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SP
VFCH | CHAVE GERAL VENTILACAO FORCADA | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SS
VFDE | CHAVE VENTILACAO FORCADA DESLIGADA | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___DESABILITOU@HABILITOU___Custom_S_TS_SS
VFMA | CHAVE VENTILACAO FORCADA MANUAL | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___DESABILITOU@HABILITOU___Custom_S_TS_SS
VFRE | CHAVE VENTILACAO FORCADA REMOTO | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___DESABILITOU@HABILITOU___Custom_S_TS_SS
CAB | CIRCUITO ABERTURA | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
CAB1 | CIRCUITO ABERTURA 1 | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
CAB2 | CIRCUITO ABERTURA 2 | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
CFC | CIRCUITO FECHAMENTO | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
CMD | COMANDO | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___REMOTO@LOCAL___Custom_S_TS_SS
CMD | COMANDO | Custom | FUNCÕES/43/PARALELISMO | ReadWrite | CMD_COS@null___REMOTO@LOCAL___Custom_S_TC_SS
FCRE | COMANDO FECHAMENTO REMOTO | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
CDC | COMUTADOR | TapIncrement | FUNCÕES/43/PARALELISMO | Write | AUMENTAR@DIMINUIR___null@null___TapIncrement_S_TC_SS
DCDC | DEFEITO CDC | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DCMD | DEFEITO COMANDO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DFDJ | DEFEITO DISJUNTOR | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB |  |  |  |  | Agrupamento de falhas: vcc comando, motor, vca e 43LR
DMOT | DEFEITO MOTOR | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
CDMT | DEFEITO MOTOR CDC | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DPT1 | DEFEITO PT100 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DR | DEFEITO RELE | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DR21 | DEFEITO RELE 21 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DR14 | DEFEITO RELE 2414 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DR25 | DEFEITO RELE 25 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DR67 | DEFEITO RELE 67 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DR81 | DEFEITO RELE 81 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DR87 | DEFEITO RELE 87 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DR90 | DEFEITO RELE 90 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DRRT | DEFEITO RELE ALTERNADO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DRPL | DEFEITO RELE MONITOR DE PARALELISMO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DRTM | DEFEITO RELE MONITORAMENTO DE TEMPERATURA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DRT1 | DEFEITO RELE MONITORAMENTO DE TEMPERATURA 1 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DRT2 | DEFEITO RELE MONITORAMENTO DE TEMPERATURA 2 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DRT3 | DEFEITO RELE MONITORAMENTO DE TEMPERATURA 3 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DRTMAVR | DEFEITO RELE MONITORAMENTO DE TEMPERATURA E AVR | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DRPR | DEFEITO RELE PRINCIPAL | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DREL | DEFEITO RELIGADOR | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DRET | DEFEITO RETIFICADOR | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DSEC | DEFEITO SECCIONADORA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DSEX | DEFEITO SENSOR EXTERNO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DSIM | DEFEITO SIMULTANEO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@DEFEITO___Custom_S_TS_SB
DHT | DHT - SECADOR DE SILICA | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
DIAF | DIAFRAGMA TRANSFORMADOR | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
DJA1 | DISJUNTOR NA | SwitchStatus | DJ | Read | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TS_SE |  |  |  |  | Usado para indicar o estado do retificador.
DJA1 | DISJUNTOR NA | SwitchStatus | DJ | ReadWrite | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE
DJF1 | DISJUNTOR NF (LIGADO/DESLIGADO/ABERTO/FECHADO) | SwitchStatus | DJ | Read | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TS_SE
DJF1 | DISJUNTOR NF | SwitchStatus | DJ | ReadWrite | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE
EST | ESTADO EQUIPAMENTO | Custom | FALHAS FCOM/VCA/VCC | Read | DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TS_SB
FLAF | FALHA ABERTURA OU FECHAMENTO | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
OLFL | FALHA FLUXO DE OLEO BOMBA | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
BBFL | FALHA BOMBAS OLEO | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
BPBR | BLOQUEIO PROTECAO DE BARRA | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
CDFL | FALHA CDC | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
FCOM | FALHA COMUNICACAO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FCAV | FALHA COMUNICACAO AVR RELE 90 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FCPR | FALHA COMUNICACAO PARALELISMO INTERNO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FC21 | FALHA COMUNICACAO RELE 21 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FC14 | FALHA COMUNICACAO RELE 2414 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FC25 | FALHA COMUNICACAO RELE 25 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FC67 | FALHA COMUNICACAO RELE 67 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FC87 | FALHA COMUNICACAO RELE 87 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FC90 | FALHA COMUNICACAO RELE 90 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FCRC | FALHA COMUNICACAO RELE CONTROLE | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FCTM | FALHA COMUNICACAO RELE MONITORAMENTO DE TEMPERATURA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FCT1 | FALHA COMUNICACAO RELE MONITORAMENTO DE TEMPERATURA 1 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FCT2 | FALHA COMUNICACAO RELE MONITORAMENTO DE TEMPERATURA 2 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FCT3 | FALHA COMUNICACAO RELE MONITORAMENTO DE TEMPERATURA 3 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FCPL | FALHA COMUNICACAO RELE MONITORAMENTO PARALELISMO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FCTL | FALHA CANAL TELEPROTECAO | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
FCTA | FALHA COMUNICACAO SENSOR TEMPERATURA AMBIENTE E UMIDADE | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FCSA | FALHA COMUNICACAO SERVICO AUXILIAR | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FCCA | FALHA COMUNICACAO SERVICO AUXILIAR VCA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FCCC | FALHA COMUNICACAO SERVICO AUXILIAR VCC | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FCSP | FALHA COMUNICACAO SPS | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FCM | FALHA COMUNICACAO TRANSDUTOR | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FCMP | FALHA COMUNICAO COMPRESSOR | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FCMR | FALHA COMUNICAO TRANSDUTOR RESERVA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FCMT | FALHA COMUTADOR | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
FLAB | FALHA DE ABERTURA | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
FLFC | FALHA DE FECHAMENTO | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
FIOL | FALHA FILTRO DE OLEO | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
OLFL | FALHA FLUXO DE OLEO | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
RLFU | FALHA FUSIVEL | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
FU1 | FALHA FUSIVEL 1 | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
FUTP | FALHA FUSIVEL TP | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
FALH | FALHA GERAL | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
GOOS | FALHA GOOSE | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FSIN | FALHA IRIG B - SINCRONISMO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FCRP | FALHA COMUNICACAO RELE PROTECAO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
RXER | FALHA RECEPCAO DADOS RX | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FSEC | FALHA SECCIONADORA | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
FSIH | FALHA SINCRONISMO HORA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FPAR | FALHA SINCRONISMO PARALELISMO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FVF | FALHA VENTILACAO FORCADA | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
FVF1 | FALHA VENTILACAO FORCADA 1 | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
FVF2 | FALHA VENTILACAO FORCADA 2 | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
ZHI | FALTA ALTA IMPEDANCIA | Custom | PROT | Read | null@null___NORMAL@FALTA___Custom_S_TS_SA
ZLO | FALTA BAIXA IMPEDANCIA | Custom | PROT | Read | null@null___NORMAL@FALTA___Custom_S_TS_SA
HIZ | FALTA DE ALTA IMPEDANCIA | Custom | PROT | Read | null@null___NORMAL@FALTA___Custom_S_TS_SA
HIF1A | FALTA DE ALTA IMPEDANCIA FASE A | Custom | PROT | Read | null@null___NORMAL@FALTA___Custom_S_TS_SA
HIF1B | FALTA DE ALTA IMPEDANCIA FASE B | Custom | PROT | Read | null@null___NORMAL@FALTA___Custom_S_TS_SA
HIF1C | FALTA DE ALTA IMPEDANCIA FASE C | Custom | PROT | Read | null@null___NORMAL@FALTA___Custom_S_TS_SA
FINT | FALTA INTERMITENTE | Custom | PROT | Read | null@null___NORMAL@FALTA___Custom_S_TS_SA
FPBR | FALTA POTENCIAL BARRA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
FPP1 | FALTA POTENCIAL BARRA P1 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
FPP2 | FALTA POTENCIAL BARRA P2 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
FVLT | FALTA POTENCIAL LT | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
VCAM | FALTA VCA PAINEL MEDICAO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
CAFL | FALTA VCA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
CACD | FALTA VCA COMUTADOR | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
CACO | FALTA VCA COMANDO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
CAMO | FALTA VCA MOTOR | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
CASC | FALTA VCA SECCIONADORA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
FVF3 | FALHA VENTILACAO FORCADA 3 | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
FVF4 | FALHA VENTILACAO FORCADA 4 | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
VFTP | TRIP FALHA REFRIGERACAO | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
CAVF | FALTA VCA VENTILACAO FORCADA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
CCFL | FALTA VCC | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
CCAB | FALTA VCC CIRCUITO ABERTURA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
CCA1 | FALTA VCC CIRCUITO ABERTURA 1 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
CCA2 | FALTA VCC CIRCUITO ABERTURA 2 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
CCFC | FALTA VCC CIRCUITO FECHAMENTO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
86CC | 86 - RELE DE BLOQUEIO (TRIP-FREE) (COMANDO CHAVEAMENTO) | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
CCCO | FALTA VCC COMANDO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
CCC1 | FALTA VCC COMANDO 1 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
CCC2 | FALTA VCC COMANDO 2 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
CCCM | FALTA VCC COMANDO MOTOR | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
CCMO | FALTA VCC MOTOR | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
CCPN | FALTA VCC PAINEL | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
CCSC | FALTA VCC SECCIONADORA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
CCCA | FALTA VCC VCA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
MCCA | FALTA VCC VCA MOLA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
VMTC | FALTA VCC VCA MOTOR COMANDO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALTA___Custom_S_TS_SB
FA | FASE A | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
FB | FASE B | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
FC | FASE C | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
FCBN | FECHAMENTO PELA BOBINA NEUTRO | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
FCSN | FECHAMENTO POR SINCRONISMO | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
FCSF | FECHAMENTO SOB FALTA | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
FGTE | FUGA TERRA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
SOTX | FUNCAO FECHAMENTO SOB FALTA | Enabled | FUNCÕES/43/PARALELISMO | Read | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TS_SS
PRTF | FALHA PROTECAO | Custom | PROT | Read | null@null___NORMAL@FALHA___Custom_S_TS_SA
SGF | FUNCAO SGF | Enabled | FUNCÕES/43/PARALELISMO | Read | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TS_SS
SGF | FUNCAO SGF | Enabled | FUNCÕES/43/PARALELISMO | ReadWrite | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS
TDS | FUNCAO TRIP DEFEITO SIMULTANEO | Enabled | FUNCÕES/43/PARALELISMO | ReadWrite | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS
AJST | GRUPO DE AJUSTE | Custom | ALARMES PREDIAIS/VF/GRUPO | Write | TROCA@null___null@null___Custom_S_TC_SV
G1 | GRUPO DE AJUSTE 1 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TS_SV
G1 | GRUPO DE AJUSTE 1 | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV
G2 | GRUPO DE AJUSTE 2 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TS_SV
G2 | GRUPO DE AJUSTE 2 | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV
G3 | GRUPO DE AJUSTE 3 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TS_SV
G3 | GRUPO DE AJUSTE 3 | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV
G4 | GRUPO DE AJUSTE 4 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TS_SV
G4 | GRUPO DE AJUSTE 4 | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV
G5 | GRUPO DE AJUSTE 5 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TS_SV
G5 | GRUPO DE AJUSTE 5 | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV
G6 | GRUPO DE AJUSTE 6 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TS_SV
G6 | GRUPO DE AJUSTE 6 | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV
81AJST | 81 - RELE DE FREQUENCIA (AJUSTE) | Custom | ALARMES PREDIAIS/VF/GRUPO | Write | TROCA@null___null@null___Custom_S_TC_SV
GRPO | GRUPO DE AJUSTE RELIGADOR | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | RELIGADOR@ALTERNATIVO___NORMAL@ALTERNATIVO___Custom_S_TC_SV |  |  |  |  | Utilizado em religadores (troca de ajustes)
AJGP | GRUPOS DE AJUSTE | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | G1@G2___GRUPO 1@GRUPO 2___Custom_S_TC_SV |  |  |  |  | Utilizado para grupo de ajustes de disjuntores de subtransmissão.
HLT | HOT LINE TAG | HotLineTag | FUNCÕES/43/PARALELISMO | Read | null@null___DESABILITADO@HABILITADO___HotLineTag_S_TS_SS |  |  |  |  | An intertrip protection relay is a relay used in power systems to initiate a trip (opening) of a circuit breaker at a remote location when a fault is detected at another location on the same circuit
HLT | HOT LINE TAG | HotLineTag | FUNCÕES/43/PARALELISMO | ReadWrite | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___HotLineTag_S_TC_SS |  |  |  |  | An intertrip protection relay is a relay used in power systems to initiate a trip (opening) of a circuit breaker at a remote location when a fault is detected at another location on the same circuit
ITFA | INTERTRIP FASE A | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
ITFB | INTERTRIP FASE B | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
ITFC | INTERTRIP FASE C | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
ITGE | INTERTRIP GERAL | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
LIBM | LIBERA MANOBRA | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___BLOQUEADA@LIBERADA___Custom_S_TS_SS
LMAB | LIBERA MANOBRA ABERTURA | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___BLOQUEADA@LIBERADA___Custom_S_TS_SS
LMFE | LIBERA MANOBRA FECHAMENTO | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___BLOQUEADA@LIBERADA___Custom_S_TS_SS
LMLO | LIBERA MANOBRA LOCAL | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___BLOQUEADA@LIBERADA___Custom_S_TS_SS
MLRE | MAL FUNCIONAMENTO | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
MANI | MANIVELA COMANDO MANUAL | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___EXTRAIDA@INSERIDA___Custom_S_TS_SS
MD | MINI DISJUNTOR | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MD38 | MINI DISJUNTOR 138KV | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MD13 | MINI DISJUNTOR 13KV | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MD23 | MINI DISJUNTOR 23KV | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MD69 | MINI DISJUNTOR 69KV | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MDBC | MINI DISJUNTOR BARRA PAINEL | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MDBP | MINI DISJUNTOR BARRA PATIO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MDCD | MINI DISJUNTOR CDC | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MDCM | MINI DISJUNTOR COMANDO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MDFA | MINI DISJUNTOR FASE A | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MDFB | MINI DISJUNTOR FASE B | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MDFC | MINI DISJUNTOR FASE C | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MDLT | MINI DISJUNTOR LT | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MDLC | MINI DISJUNTOR LT PAINEL | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MDLP | MINI DISJUNTOR LT PATIO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MDOL | MINI DISJUNTOR OLEO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MDPM | MINI DISJUNTOR PAINEL MEDICAO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MDTP | MINI DISJUNTOR TP | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MDTM | MINI DISJUNTOR TP MEDICAO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MDMT | MINI DISJUNTOR TP MEDICAO CDC | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MDPN | MINI DISJUNTOR TP PAINEL | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MDCA | MINI DISJUNTOR VCA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MDCC | MINI DISJUNTOR VCC | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB
MTRF | MODULO TRANSFERIDO | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SS
MOLA | MOLA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB
MLCC | FALTA VCC OU MOLA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
NEGT | NEGATIVADO A TERRA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
N | NEUTRO | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
OI | OPERACAO INDEVIDA SECCIONADORA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
OAUT | OPERAÇÃO PELO AUTOMATISMO | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
PPOT | PERDA DE POTENCIAL | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
PVRF | PERDA DE TENSAO DE REFERENCIA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
PALT | PERFIL DE AJUSTE ALTERNATIVO | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TS_SV
PALT | PERFIL DE AJUSTE ALTERNATIVO | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV
PNOR | PERFIL DE AJUSTE NORMAL | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TS_SV
PNOR | PERFIL DE AJUSTE NORMAL | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV
PERP | PERMISSAO PARALELISMO | Custom | FUNCÕES/43/PARALELISMO | Read | null@null___NÃO PERMITIDO@PERMITIDO___Custom_S_TS_SS
P51F | PICK UP 51F | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
P51N | PICK UP 51N | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
PORT | PORTA SUBESTACAO | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___ABERTO@FECHADO___Custom_S_TS_SP
PORU | PORTA UTR | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___ABERTO@FECHADO___Custom_S_TS_SP
PORO | PORTAO SUBESTACAO | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___ABERTO@FECHADO___Custom_S_TS_SP
DJIE | POSICAO DISJUNTOR EXTRAIVEL | Custom | DEFEITOS | Read | null@null___EXTRAIDO@INSERIDO___Custom_S_TS_SI
POST | POSITIVO A TERRA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
PBEX | FUNCAO PROTECAO DE BARRA | Enabled | FUNCÕES/43/PARALELISMO | Read | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TS_SS
PROT | PROTECAO BLOQUEADA | Custom | PROT | Read | DESBLOQUEAR@BLOQUEAR___NORMAL@BLOQUEADA___Enabled___admsINV_S_TS_SA
PB | PROTECAO DE BARRA | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  |  |  | Funciona como um 50 da barra (quando há defeito na barra e não nos alimentadores). Atua com um tempo pré-determinado (geralmente 150ms) e é utilizado para diminuir o tempo de atuação sobre o defeito (devido os tempos de seletividade).
PBF | PROTECAO DE BARRA FASE | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  |  |  | Funciona como um 50 da barra (quando há defeito na barra e não nos alimentadores). Atua com um tempo pré-determinado (geralmente 150ms) e é utilizado para diminuir o tempo de atuação sobre o defeito (devido os tempos de seletividade).
PBF1 | PROTECAO DE BARRA FASE E1 | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  |  |  | Funciona como um 50 da barra (quando há defeito na barra e não nos alimentadores). Atua com um tempo pré-determinado (geralmente 150ms) e é utilizado para diminuir o tempo de atuação sobre o defeito (devido os tempos de seletividade).
PBF2 | PROTECAO DE BARRA FASE E2 | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  |  |  | Funciona como um 50 da barra (quando há defeito na barra e não nos alimentadores). Atua com um tempo pré-determinado (geralmente 150ms) e é utilizado para diminuir o tempo de atuação sobre o defeito (devido os tempos de seletividade).
PBN | PROTECAO DE BARRA NEUTRO | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  |  |  | Funciona como um 50 da barra (quando há defeito na barra e não nos alimentadores). Atua com um tempo pré-determinado (geralmente 150ms) e é utilizado para diminuir o tempo de atuação sobre o defeito (devido os tempos de seletividade).
PBN1 | PROTECAO DE BARRA NEUTRO 1 | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  |  |  | Funciona como um 50 da barra (quando há defeito na barra e não nos alimentadores). Atua com um tempo pré-determinado (geralmente 150ms) e é utilizado para diminuir o tempo de atuação sobre o defeito (devido os tempos de seletividade).
PBN2 | PROTECAO DE BARRA NEUTRO 2 | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  |  |  | Funciona como um 50 da barra (quando há defeito na barra e não nos alimentadores). Atua com um tempo pré-determinado (geralmente 150ms) e é utilizado para diminuir o tempo de atuação sobre o defeito (devido os tempos de seletividade).
PB1 | PROTECAO DE BARRA P1 | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
PB2 | PROTECAO DE BARRA P2 | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
TPNO | PROTECAO NAO TRANSFERIDA | Custom | PROT | Read | null@null___NORMAL@INCOMPLETA___Custom_S_TS_SA
RGBL | RELIGADOR BLOQUEADO | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
ICC | RESET CORRENTE DE CURTO CIRCUITO | Custom | FUNCÕES/43/PARALELISMO | Write | RESET@null___null@null___Custom_S_TC_SS
CTPC | RETORNO DE TENSAO DA PCH | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
MEMB | RUPTURA MEMBRANA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
SCAR | SECADOR DE AR | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
SECB | SECCIONADORA BYPASS | SwitchStatus | DJ BC/SEC | Read | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TS_SO
SECB | SECCIONADORA BYPASS | SwitchStatus | DJ BC/SEC | ReadWrite | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO
SECC | SECCIONADORA CARGA | SwitchStatus | DJ BC/SEC | Read | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TS_SO
SECC | SECCIONADORA CARGA | SwitchStatus | DJ BC/SEC | ReadWrite | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO
SECF | SECCIONADORA FONTE | SwitchStatus | DJ BC/SEC | Read | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TS_SO
SECF | SECCIONADORA FONTE | SwitchStatus | DJ BC/SEC | ReadWrite | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO
SECI | SECCIONADORA INTERBARRAS | SwitchStatus | DJ BC/SEC | Read | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TS_SO
SECI | SECCIONADORA INTERBARRAS | SwitchStatus | DJ BC/SEC | ReadWrite | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO
SECL | SECCIONADORA INTERLINHAS | SwitchStatus | DJ BC/SEC | Read | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TS_SO
SECL | SECCIONADORA INTERLINHAS | SwitchStatus | DJ BC/SEC | ReadWrite | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO
SECG | SECCIONADORA TERRA | SwitchStatus | DJ BC/SEC | Read | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TS_SO
SECG | SECCIONADORA TERRA | SwitchStatus | DJ BC/SEC | ReadWrite | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO
SECT | SECCIONADORA TRANSFERENCIA | SwitchStatus | DJ BC/SEC | Read | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TS_SO
SECT | SECCIONADORA TRANSFERENCIA | SwitchStatus | DJ BC/SEC | ReadWrite | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO
FUMA | SENSOR FUMACA | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SV
SEXT | SENSOR PRESENCA EXTERNO | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SV
SINT | SENSOR PRESENCA INTERNO | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SV
STMP | SENSOR TEMPERATURA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
SFAB | SF6 BLOQUEIO ABERTURA | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
SFFC | SF6 BLOQUEIO FECHAMENTO | Custom | DEFEITOS | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SI
SOBC | SOBRECARGA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
BAHI | TENSAO ALTA BATERIA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
BATL | TENSAO BAIXA BATERIA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
RVTL | TENSAO BAIXA RELE 90 | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
TPOK | PROTECAO TRANSFERIDA | Custom | PROT | Read | null@null___NORMAL@COMPLETA___Custom_S_TS_SA
DTT | TRANSFERENCIA DE TRIP | Custom | PROT | Read | null@null___OPERANDO@BLOQUEADO___Custom_S_TS_SA
DTTT | TRANSFERENCIA DE TRIP TRIFASICO | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
TRIP | TRIP | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
SIMD | TRIP DEFEITO SIMULTANEO | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
TEXT | TRIP EXTERNO | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
RXTR | TRIP EXTERNO RECEBIDO | Custom | PROT | Read | null@null___NORMAL@RECEBIDO___Custom_S_TS_SA
TXTR | TRIP EXTERNO TRANSMITIDO | Custom | PROT | Read | null@null___NORMAL@TRANSMITIDO___Custom_S_TS_SA
SOTF | TRIP FECHAMENTO SOB FALTA | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
TRAL | TRIP PARA ALIMENTADORES | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
TPIN | TRANSFERENCIA DE PROTECAO | Custom | PROT | Read | null@null___COMPLETA@INCOMPLETA___Custom_S_TS_SA
TRPR | TRIP RECEBIDO | Custom | PROT | Read | null@null___NORMAL@RECEBIDO___Custom_S_TS_SA
SGFT | TRIP SGF | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
SGT2 | TRIP SGF E2 | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
TRPT | TRIP TRANSMITIDO | Custom | PROT | Read | null@null___NORMAL@TRANSMITIDO___Custom_S_TS_SA
REFE | VARIAÇÃO DA TENSAO DE REFERÊNCIA POR MVA | Custom | FUNCÕES/43/PARALELISMO | ReadWrite | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS
CAAL | VCA ALARME | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
CAAQ | VCA AQUECIMENTO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
CAFI | VCA MOTOR DO FILTRO DO OLEO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
CASA | VCA SERVICO AUXILIAR | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
CCAL | VCC ALARME | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
CCHI | VCC ALTA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
CCLO | VCC BAIXA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB
LDF | LOCALIZADOR DE FALTA | RelayTrip | PROT | Read | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA
POTT | TRIP POR TELEPROTECAO | Custom | PROT | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SA
FLAR | FALHA FLUXO AR | Custom | DEFEITOS | Read | null@null___NORMAL@FALHA___Custom_S_TS_SI
BOMB | ESTADO BOMBA OLEO | Custom | FALHAS FCOM/VCA/VCC | Read | DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TS_SB
VF | VENTILACAO FORCADA | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TS_SV
VF | VENTILACAO FORCADA | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TC_SV
VF1 | VENTILACAO FORCADA 1 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TS_SV
VF1 | VENTILACAO FORCADA 1 | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TC_SV
VF2 | VENTILACAO FORCADA 2 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TS_SV
VF2 | VENTILACAO FORCADA 2 | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TC_SV
VF3 | VENTILACAO FORCADA 3 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TS_SV
VF3 | VENTILACAO FORCADA 3 | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TC_SV
VF4 | VENTILACAO FORCADA 4 | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TS_SV
VF4 | VENTILACAO FORCADA 4 | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TC_SV
VFAM | VENTILACAO FORCADA AUTOMATICA MANUAL | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | AUTOMATICO@MANUAL___AUTOMATICO@MANUAL___Custom___admsINV_S_TS_SV
VFAR | VENTILACAO FORCADA AUTOMATICO REMOTO | Custom | ALARMES PREDIAIS/VF/GRUPO | Read | null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV
FCRT | FALHA COMUNICACAO RELE REGULADOR DE TENSAO | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
FLNR | FALHA NEUTRO RESSONANTE | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
MNAT | OPERACAO DO NEUTRO RESSONANTE | Custom | FUNCÕES/43/PARALELISMO | ReadWrite | MANUAL@AUTOMATICO___MANUAL@AUTOMATICO___Custom_S_TC_SS
MOD | MODO DE OPERAÇÃO | Custom | ALARMES PREDIAIS/VF/GRUPO | ReadWrite | RELIGADOR@CHAVE___RELIGADOR@CHAVE___Custom___S_TC_SS
LIGAR | COMANDO LIGAR | Custom | DJ | Read | null@LIGAR___null@LIGADO___SwitchStatus_S_TC_SE
DESLIGAR | COMANDO DESLIGAR | Custom | DJ | Read | DESLIGAR@null___null@DESLIGADO___SwitchStatus_S_TC_SE
C13 | CHAVE SELETORA 13 KV | Custom | DJ | Read | DESLIGAR@null___null@DESLIGADO___SwitchStatus_S_TC_SE
C23 | CHAVE SELETORA 23 KV | Custom | DJ | Read | DESLIGAR@null___null@DESLIGADO___SwitchStatus_S_TC_SE
C69 | CHAVE SELETORA 69 KV | Custom | DJ | Read | DESLIGAR@null___null@DESLIGADO___SwitchStatus_S_TC_SE
C138 | CHAVE SELETORA 138 KV | Custom | DJ | Read | DESLIGAR@null___null@DESLIGADO___SwitchStatus_S_TC_SE
FCMM | FALHA COMUNICACAO MULTIMEDIDOR | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@FALHA___Custom_S_TS_SB
VCPB | VCC PROTECAO BARRA | Custom | FALHAS FCOM/VCA/VCC | Read | null@null___NORMAL@ATUADO___Custom_S_TS_SB

## AnalogSignals
SINAL | DESCRIÇÃO NOVA | SIGNAL TYPE | TIPO DE MEDIÇÃO | UNIDADE DE EXIBIÇÃO | FASES | LADO | DIREÇÃO DO FLUXO | FUNCIONAMENTO
IN61 | 61 - CORRENTE DE DESEQUILIBRO | Valor Medido | Corrente | A | N
ANG | ANGULO | Valor Medido | Ângulo de Tensão | Grau | L1 L2 L3
OPER | CONTAGEM DE OPERACOES | Contagem de Operação | Discreto | - | L1 L2 L3
IOUT | CORRENTE CARGA | Valor Medido | Corrente | A | L1 L2 L3
IACC | CORRENTE CURTO CIRCUITO FASE A | Gravador de Falha | Corrente | A | L1
IBCC | CORRENTE CURTO CIRCUITO FASE B | Gravador de Falha | Corrente | A | L2
ICCC | CORRENTE CURTO CIRCUITO FASE C | Gravador de Falha | Corrente | A | L3
INCC | CORRENTE CURTO CIRCUITO NEUTRO | Gravador de Falha | Corrente | A | N
IA | CORRENTE FASE A | Valor Medido | Corrente | A | L1
IB | CORRENTE FASE B | Valor Medido | Corrente | A | L2
IC | CORRENTE FASE C | Valor Medido | Corrente | A | L3
IN | CORRENTE NEUTRO | Valor Medido | Corrente | A | N
KMDF | DISTANCIA DEFEITO | Custom | Comprimento | Km | L1 L2 L3
FP | FATOR DE POTENCIA | Valor Medido | Fator de Potência | Padrão | L1 L2 L3
FREQ | FREQUENCIA | Valor Medido | Frequência | Hz | L1 L2 L3
FUGA | FUGA A TERRA | Valor Medido | Corrente | A | L1 L2 L3
S | POTENCIA APARENTE | Valor Medido | Potência Aparente | MVA | L1 L2 L3
P | POTENCIA ATIVA | Valor Medido | Potência Ativa | MW | L1 L2 L3
Q | POTENCIA REATIVA | Valor Medido | Potência Reativa | MVAR | L1 L2 L3
TPAM | TEMPERATURA AMBIENTE | Valor Medido | Temperatura | C | L1 L2 L3
TPBT | TEMPERATURA BATERIAS | Valor Medido | Temperatura | C | L1 L2 L3
TENR | TEMPERATURA ENROLAMENTO | Valor Medido | Temperatura | C | L1 L2 L3
TSCO | TEMPERATURA SALA DE COMANDO | Valor Medido | Temperatura | C | L1 L2 L3
TOLE | TEMPERATURA OLEO | Valor Medido | Temperatura | C | L1 L2 L3
TOL2 | TEMPERATURA OLEO 2 | Valor Medido | Temperatura | C | L1 L2 L3
V | TENSAO | Valor Medido | Tensão | kV | L1 L2 L3
V | TENSAO | Valor Medido | Tensão | V | L1 L2 L3 |  |  | Serviço auxiliar
VA_B | TENSAO BARRA FASE A | Valor Medido | Tensão | kV | L1
VB_B | TENSAO BARRA FASE B | Valor Medido | Tensão | kV | L2
VC_B | TENSAO BARRA FASE C | Valor Medido | Tensão | kV | L3
VBAT | TENSAO BATERIAS | Valor Medido | Tensão | V | L1 L2 L3
VCC | TENSAO CORRENTE CONTINUA | Valor Medido | Tensão | V | L1 L2 L3
VCC1 | TENSAO CORRENTE CONTINUA 1 | Valor Medido | Tensão | V | L1 L2 L3
VCC2 | TENSAO CORRENTE CONTINUA 2 | Valor Medido | Tensão | V | L1 L2 L3
VIN | TENSAO DE ENTRADA | Valor Medido | Tensão | V | L1 L2 L3
VABI | TENSAO FASE AB - LADO FONTE | Valor Medido | Tensão | kV | L1 L2
VBCI | TENSAO FASE BC - LADO FONTE | Valor Medido | Tensão | kV | L2 L3
VCAI | TENSAO FASE CA - LADO FONTE | Valor Medido | Tensão | kV | L1 L3
VREF | TENSAO DE REFERENCIA | Valor Medido | Tensão | V | L1 L2 L3
VOUT | TENSAO DE SAIDA | Valor Medido | Tensão | V | L1 L2 L3
VA | TENSAO FASE A | Valor Medido | Tensão | kV | L1
VA | TENSAO FASE A | Valor Medido | Tensão | V | L1 |  |  | Serviço auxiliar
VB | TENSAO FASE B | Valor Medido | Tensão | kV | L2
VB | TENSAO FASE B | Valor Medido | Tensão | V | L2 |  |  | Serviço auxiliar
VC | TENSAO FASE C | Valor Medido | Tensão | kV | L3
VC | TENSAO FASE C | Valor Medido | Tensão | V | L3 |  |  | Serviço auxiliar
VAB | TENSAO FASE AB | Valor Medido | Tensão | kV | L1 L2
VAB | TENSAO FASE AB | Valor Medido | Tensão | V | L1 L2 |  |  | Serviço auxiliar
VBC | TENSAO FASE BC | Valor Medido | Tensão | kV | L2 L3
VBC | TENSAO FASE BC | Valor Medido | Tensão | V | L2 L3 |  |  | Serviço auxiliar
VCA | TENSAO FASE CA | Valor Medido | Tensão | kV | L1 L3
VCA | TENSAO FASE CA | Valor Medido | Tensão | V | L1 L3 |  |  | Serviço auxiliar
VA_L | TENSAO LINHA FASE A | Valor Medido | Tensão | kV | L1
VB_L | TENSAO LINHA FASE B | Valor Medido | Tensão | kV | L2
VC_L | TENSAO LINHA FASE C | Valor Medido | Tensão | kV | L3
UMID | UMIDADE | Custom | Umidade | % | L1 L2 L3
ADIF | 25 - DIFERENCA ANGULO | Valor Medido | Ângulo de Tensão | Grau | L1 L2 L3
VDIF | 25 - DIFERENCA TENSAO | Valor Medido | Tensão | kV | L1 L2 L3
FDIF | 25 - DIFERENCA FREQUENCIA | Valor Medido | Frequência | Hz | L1 L2 L3
VABX | TENSAO FASE AB - LADO CARGA | Valor Medido | Tensão | kV | L1 L2
VBCX | TENSAO FASE BC - LADO CARGA | Valor Medido | Tensão | kV | L2 L3
VCAX | TENSAO FASE CA - LADO CARGA | Valor Medido | Tensão | kV | L1 L3

## DE->PARA
SINAL | DESCRIÇÃO NOVA
90 | R90
20T87T | 2087T
21_1 | 21Z1
21_2 | 21Z2
21_3 | 21Z3
21_4 | 21Z4
2646_T | TOED
2649T | TOED
27_1 | 27E1
27_2 | 27E2
27_B | 27BR
27L | 27LT
43CD | RLCD
50B1 | 50_1
50B2 | 50_2
59_1 | 59E1
59_2 | 59E2
5CDC | 50CD
63C | 63CD
63CT | 63TC
63T | 63TD
67EX | 67
67T1 | 67FT
67T2 | 67FT
81_1 | 81E1
81_2 | 81E2
81_TRIP | 81_T
86BFCC | 86CC
86T | 86
87RF | 87EF
90PI | MANUT
ABRE | TEXT
AJ81U1 | 81U1
AJ81U2 | 81U2
AJ81U3 | 81U3
AJ81U4 | 81U4
AJ81U5 | 81U5
AUTC | AUTO
BAFU | BATA
BASD | MANUT
BB | BBAF
BFCC | 86CC
BLQR | 79LO
CAA2 | CAFL
CAA5 | CAFL
CCCFA1 | BBAF
CDCA | CACD
CDCL | RLCD
CDCO_CTRL
CDMA | CDAM
COMANDADO | COMA
DFT1 | DRT1
DJRT | EST
DSA1 | EST
DSA2 | EST
FCAMB | FCTA
FCM1 | FCT1
FCM2 | FCT2
FCSPS | FCSP
FUGA | FGTE
INDIVIDUAL | INDI
LDF | MANUT
LDFD | 21D
LIBF | LMFE
LMFA | LMAB
M69C | MDTP
MDP1 | MDTP
MDP2 | MDTP
MDTF | MTRF
MDTP1 | MDTP
MDTP2 | MDTP
MENB | MEMB
MESTRE | MEST
OIBP | OI
PARALELO | MANUT
PRTA | TPOK
RELD | DREL
RTLG | MDCA
SECPT | SECT
SOBR | SOBC
TOED1 | VERIFICAR
TOED2 | VERIFICAR
TPEX | TEXT
TR87 | 87TT
VCAM | 27CA
94 | TEXT
TRIPE | TEXT
TRIPEXT | TEXT
CDLR | RLCD
FVBA | FPBR
2649_T | TOED
G1_G2 | AJGP
61A | 61
FCRHT | FCTA
BMBO | BBFL
BMB | BBFL
BPLI | BOMB
FLBB | OLFL
OFL | OLFL

## Severidades
DETALHADO |  |  |  |  | RESUMIDO
MM | SEVERIDADE | COLORAÇÃO SUMÁRIO | USO | TEXTO | UTILIZAÇÃO | SIGLA | SEVERIDADE | COLORAÇÃO SUMÁRIO
| 1 | SEVERIDADE | ALARME EMERGENCIAL MUST (105%) | ALISUP EMER MUST | DJ | SE/ST/E2 | 2 | SEVERIDADE
|  |  | ALARME CONTRATADO MUST (100%) | ALISUP CONTR MUST | DEFEITOS | SI | 3 | SEVERIDADE
SE/ST/E2 | 2 | SEVERIDADE | ESTADO DJs (exceto BC) - EVENTO | ALESTC | PROT | SA/DA/A1 | 4 | SEVERIDADE
SI | 3 | SEVERIDADE | DRET, DR, Alarmes limites VCC, Bobinas e circuitos de abertura e fechamento | ALESTS | ALARMES PREDIAIS/VF/GRUPO | SV/SP/DV/DP | 5 | SEVERIDADE
SA/DA/A1 | 4 | SEVERIDADE | TRIP: PROTEÇÕES: 86, 50, 51, 26, 49, 27, 87, 20, 63, ... | ALESTS/ALESTC | DJ BC/SEC | SC/SO | 6 | SEVERIDADE
SV/SP/DV/DP | 5 | SEVERIDADE | ALARMES PREDIAIS, PORTAS, SENSOR DE PRESENÇA E DEFUMAÇA; VF | ALESTS/ALESTC | FALHAS FCOM/VCA/VCC | SB/DB | 7 | SEVERIDADE
SC/SO | 6 | SEVERIDADE | ESTADO DJs BC / ESTADO SECCIONADORAS | ALESTS/ALESTC | FUNCÕES/43/PARALELISMO | SS/DS | 8 | SEVERIDADE
SB/DB | 7 | SEVERIDADE | FALHA DE COMUNICAÇÃO (RELÉS); FALHA VF; FALHA VCC | ALESTS
SS/DS | 8 | SEVERIDADE | 43TC, 43LR, PERMISSÃO DE PARALELISMO | ALESTS/ALESTC
ST | 9 | SEVERIDADE | FALHA DE COMUNICAÇÃO (UTR) | UTRRES
|  |  | COMANDO VARREDURA | CNEXEC
|  |  | FALHA DE CONEXÃO (LINK) | LNKNR
- | 10 | SEVERIDADE | COMANDOS | COPER
- |  |  | LIMITE DE DADOS EMERGENCIAL (Tensões/Corrente) | ALISUP EMER/CEXSIM
- |  |  | LIMITE DE DADOS OPERACIONAL (Tensões/Corrente) | ALISUP OPER/CEXSIM
- |  |  | ATUALIZAÇÃO DE EQUIPES E PLANOS DE MANOBRAS | -
| 11 | SEVERIDADE | EXECUÇÃO DE COMANDOS COM SUCESSO | CEXEC
|  |  | LIMITE DE DADOS OPERACIONAL (Tensões) | ALISUP EMER
|  |  | LIMITE DE DADOS EMERGENCIAL (Tensões) | ALISUP OPER
| 12 | SEVERIDADE | ALARME OPERACIONAL MUST (95%) | ALISUP OPER MUST
|  |  | ALARME DE FATOR DE POTÊNCIA | ALIFP
- | 13 | SEVERIDADE | ALARME DE POTÊNCIA (Sobrecarga) | ALISUP EMER/OPER
| 14 | SEVERIDADE | Informações dos servidores e máquinas
| 15 | SEVERIDADE
- | 16 | SEVERIDADE | RECONHECIMENTO/ARQUIVAMENTO ALARMES

## Information
Signal type | Meas. type | Element | Notes
Custom | (any) | PowerSystemResource | Custom signal types (none of the ADMS-recognized types). Additional enumerations can be used for project-specific purposes, as well as for different message mappings.
Custom1... Custom100
SwitchStatus | SwitchStatus | Switch | Switch or rack status (1=Open, 2=Closed). Initial=Switch.normalValue
Read/Write |  | PortableCell
Local/Remote | Status | Switch | A switch, tap changer or RTU is switched into local manual control, and cannot be remotely operated (however, its status can be read). (2=Closed=Local, 1=Open=Remote)
Read |  | CompositeSwitch
TapChanger
RemoteUnit
PortableCell
RegulatingControl
OperationCount | Discrete | Switch | Total count of switch or tap changer operations since last reset. Initial=0
Read |  | TapChanger
TapPosition | Discrete | TapChanger | Absolute tap position. Initial=TapChanger.neutralStep
Read/Write |  | PetersenCoil
TapIncrement | Status | TapChanger | Tap position increment: 1/Open=Lower, 2/Close=Raise. Initial=Error=0.
Write |  | PetersenCoil
Enabled | Status | RegulatingControl | Enabled operation of Sectionalizer, RegulatingControl or RelayStage. (2=Closed=Auto, 1=Open=Manual).
Read/Write |  | ControlLimit
ControlSettings
ProtectionEquipment
RelayStage
RecloseStage
DistanceRelayStage
Sectionalizer
InterlockingScheme
RegulatingControlGroup
ProtectionGroup
LoadBonus | Status | RegulatingControl | Load bonus activated (2=Closed=On, 1=Open=Off) on a voltage regulator's RegulatingControl. Applicable only when a ControlLimit of type LoadBonus exists.
Read/Write
ReclosingEnabled | Status | ProtectionEquipment (only reclosing) | Enabled (2=Closed) reclosing operation of a ProtectionEquipment which models a reclosing relay.
Read/Write |  | Breaker
(only reclosing)
RecloserLockout | Status | ProtectionEquipment | Recloser locked out. (1=Open=Not locked, 2=Closed=Locked)
Read |  | (only reclosing)
ControlActiveSetting | Discrete | RegulatingControl | 1-based index of active relay settings, control settings, or regulating control within a group. Initial=1, except for RegulatingControl where Initial=0 (=ControlSettingType.Normal).
Read/Write |  | RelayStage
RecloseStage
DistanceRelayStage
ProtectionEquipment
ProtectionGroup
RegulatingControlGroup
Refresh | Status | RegulatingControl | Refreshes the value of a regulator setting (write-only). Introduced for closed loop control.
Read/Write; Manual only | Discrete
VoltageIndex1 | Discrete | PowerTransformer | For dual-voltage transformers: 1-based index of the selected voltage at the primary side (1) or secondary side (2). Initial=1
VoltageIndex2
Read/Write; Manual only
LoadFlowEnabled | Discrete | Substation | Specifies if state estimation is enabled for all sources within the substation or transmission network (2), load flow only (1), or none (0). If absent, State Estimation is enabled.
Read/Write; Manual only |  | TransmissionNetwork
TemporaryFault | Status | Switch | A temporary fault current flow had been detected (2=Closed) by a fault recorder or fault indicator, but the condition was reset. Initial=Open
Read/Write |  | FaultIndicator
ACLineSegment
CurrentTransformer
FaultStatus | Status | Switch | A permanent fault current flow has been detected (2=Closed) by a fault recorder or fault indicator. Attribute phases describes the measured phases. Initial=Open
Read/Write |  | FaultIndicator
ACLineSegment
CurrentTransformer
FanStatus | Status | PowerTransformer | Status of transformer's cooling fan. (2=Closed=On)
Read/Write
OilPumpStatus | Status | Transformer | Status of transformer's cooling oil pump. (2=Closed=On)
Read/Write
HotLineTag | Status | Breaker (with reclosing relay) | Hot line tag (both automatic and manual reclosing disabled) 2=Closed=tag placed (reclosing disabled), 1=Open=tag off
Read/Write |  | CompositeSwitch
MaxOpCount | Discrete | Switch | Maximum user-specified allowed daily count of switch or tap changer operations. If the signal is absent or has value of zero, VVO uses value specified in the profile.
Read/Write, Manual only |  | TapChanger
HourlyOpCount | Discrete | Switch | Hourly count (since x:00 min) of switch or tap changer operations. Initial=0
Read |  | TapChanger
DailyOpCount | Discrete | Switch | Daily count (since midnight) of switch or tap changer operations. Initial=0
Read |  | TapChanger
MonthlyOpCount | Discrete | Switch | Monthly count (since 1st) of switch or tap changer operations. Initial=0
Read |  | TapChanger
UnderFrequencyAlarm | Status | Substation | An underfrequency alarm is raised for the substation. (1=Open=Alarm off 2=Closed=Alarm on)
Read, Remote only |  | ProtectingEquipment (Underfrequency only)
Forward | Status | ProtectedSwitch | For directable devices, specifies that the current or power flows in "forward" (2=Closed) (usually, downstream) or 1=Open=reverse direction.
Read |  | FaultIndicator
RegulatingControl
RelayTrip | Status | RelayStage | Indicates that a particular relay or protection recorded a fault (2=Closed=trip) and caused the breaker to trip. Initial=Open
Read |  | RecloseStage
DistanceRelayStage
ProtectingEquipment
ReverseMode | Discrete | RegulatingControl | Voltage regulators only: Indicates how the regulator behaves in case of reverse power flow (ReverseOperation enum) (Initial=Block=0)
Read/Write
SourceStatus | Status | EnergySource | Energization status of an energy source (1=Open=Passive, 2=Closed=Active) (type=Status)
Read/Write |  | Interconnection
GroupStatus | Status | DERGroup | Energization status of a DERGroup (1=Open=Disonnected, 2=Closed=Connected). If generators within the group have mixed status, it does not affect the group status. (type=Status)
Read/Write
Parallel | Status | RegulatingControl | Voltage regulators only: when 1=Open . indicates that the regulator is not in slave (parallel) operation in respect to the RegulatingControlGroup it belongs to. When the signal is 2=Closed or absent, the regulator acts in slave mode.
Read/Write
PowerOn | Status | ACLineSegment | Indicates presence (Closed=2) or absence (Open=1) of voltage at the sensor location.
Read |  | PowerTransformer2W
CurrentTransformer
Switch
ServiceDeliveryPoint
ServiceLocation
FaultIndicator
Manageable | Status | EnergyConsumer | Specifies that the customer (Yes=Closed=2) may be disconnected by the utility.
Read/Write |  | ServiceDeliveryPoint
ServiceLocation
Malfunctioning | Status | PowerTransformer | Indicates an alarm/failure (Closed=2) of a piece of equipment that renders it unsuitable for normal operation. (Motor failure, Buchholz relay operation etc.)
Read |  | Switch
TapChanger
ProtectionEquipment
Capacitor
CompositeSwitch
WeightingFactor | Discrete | Capacitor | Specifies preferred priority of the Capacitor for operation by Var control algorithm. Capacitors with greatest weight are operated first.
Read/Write, Manual only |  | CapacitorBank

## DMS Signal Explanation
MatchingString | DMS Matching template | signalType | measurementType | phaseCode & sideMeasured | signalType | Description | measurementType | Description | PhaseCode | Description | Error Report |  | Protocols | Unique device | Unique identifier | Choice of Unique device | Choice of Unique identifier | ICCP Point Role | ICCP INPUT Point Type | ICCP OUTPUT Point Type | ICCP Point Scope | Delete | Invert In/Out bits | Point type | Point category
| SWSABC | SwitchStatus | SwitchStatus | ABC | SwitchStatus | Switch or rack status | SwitchStatus | A discrete signal describing switch status -- open/close/error/transit. | ABC | Phases ABC, side measured : None (No winding is applicable) | Sheet name | No of errors | DNP_V3.0 | Substation | Name | 1 | 1 | client | DV_Real | DEV_Real | ICC |  | yes | telemetered | analog
| SWSA | SwitchStatus | SwitchStatus | A | Local | A switch, tap changer or RTU is switched into local manual control, and cannot be remotely operated (however, its status can be read). | Status | A discrete signal with on/off (true/false) value. | A | Phases A, side measured : None (No winding is applicable) |  | 1 | IEC 104 | Feeder | Alias |  |  | server | DV_State | DEV_Command | VCC | DELETE | no | calculated | status
| SWSB | SwitchStatus | SwitchStatus | B | OperationCount | Total count of switch or tap changer operations since last reset. | Discrete | A discrete signal with a range of integer values | B | Phases B, side measured : None (No winding is applicable) |  |  | ICCP | Feeder Object |  |  |  | client/server | DV_Discrete | DEV_Discrete |  |  |  | manual entry
| SWSC | SwitchStatus | SwitchStatus | C | FaultStatus | Fault current flow is detected (2=Closed) by a fault recorder or fault indicator. | Voltage | Voltage | C | Phases C, side measured : None (No winding is applicable) |  |  |  | Bank |  |  |  | none | DV_StateSupp |  |  |  |  | remote param
| LOCREMABC | Local | Status | ABC | MaxOpCount | Maximal allowed daily count of switch or tap changer operations. If zero, VVO uses value specified in the profile. | VoltageAngle | Voltage angle. Typically, this is not a physical measurement but a pseudo-measurement imported from e.g. EMS estimator. | AB | Phases AB, side measured : None (No winding is applicable) |  |  |  | Bay |  |  |  |  | DV_RealQuality
| LOCREMA | Local | Status | A | HourlyOpCount | Hourly count (since x:00 min) of switch or tap changer operations. Initial=0 | Frequency | Frequency | BC | Phases BC, side measured : None (No winding is applicable) | [8 empty] | DV_StateQuality
| LOCREMB | Local | Status | B | DailyOpCount | Daily count (since midnight) of switch or tap changer operations. Initial=0 | RelativeVoltage | Voltage expressed as relative value of base voltage. Default unit is %, other applicable units are p.u and base 120 | AC | Phases AC, side measured : None (No winding is applicable) | [8 empty] | DV_DiscreteQuality
| LOCREMC | Local | Status | C | MonthlyOpCount | Monthly count (since 1st) of switch or tap changer operations. Initial=0 | Current | Current | ABCPrimary | Phases ABC, side measured : Primary (first terminal) | [8 empty] | DV_StateSuppQuality
| OPCNTABC | OperationCount | Discrete | ABC | PowerOn | Indicates presence or absence of voltage at the sensor location. | ActivePower | Active power | ABPrimary | Phases AB, side measured : Primary (first terminal) | [8 empty] | DV_RealQualityTimeTag
| OPCNTA | OperationCount | Discrete | A | Forward | For directable devices, specifies that the current or power flows in "forward" (usually, downstream) direction. | ApparentPower | Apparent power | BCPrimary | Phases BC, side measured : Primary (first terminal) | [8 empty] | DV_StateQualityTimeTag
| OPCNTB | OperationCount | Discrete | B | HotLineTag | For reclosers, specifies that both automatic and manual reclosing are disabled | CosPhi | Power factor (cos(phi)) | ACPrimary | Phases AC, side measured : Primary (first terminal) | [8 empty] | DV_DiscreteQualityTimeTag
| OPCNTC | OperationCount | Discrete | C | DiscreteSignalType.Custom | A custom type (none of the DMS recognized types) | ActiveEnergy | Active energy | APrimary | Phases A, side measured : Primary (first terminal) | [8 empty] | DV_StateSuppQualityTimeTag
| FLTSTABC | FaultStatus | Status | ABC | MeasuredValue | An analog measured value. | ReactiveEnergy | Reactive energy | BPrimary | Phases B, side measured : Primary (first terminal) | [8 empty] | DV_RealExtended
| FLTSTA | FaultStatus | Status | A | FaultRecorder | Recorded value of fault current or voltage | CurrentAngle | Current angle provided from fault recorder or IEDs. Default unit is degree. | CPrimary | Phases C, side measured : Primary (first terminal) | [8 empty] | DV_StateExtended
| FLTSTB | FaultStatus | Status | B | AnalogSignalType.Custom | A custom type (none of the DMS recognized types) | Temperature | Temperature [°C] of an element (for equipment) or of air (for a weather region) | ABCSecondary | Phases ABC, side measured : Secondary (second terminal) | [8 empty] | DV_DiscreteExtended
| FLTSTC | FaultStatus | Status | C | Enabled | Enabled operation of Sectionalizer, RegulatingControl or RelayStage | Unitless | An analog quantity which is unitless, or not otherwise in the list of supported types | ABSecondary | Phases AB, side measured : Secondary (second terminal) | [8 empty] | DV_StateSuppExtended
| MAXOPCNTABC | MaxOpCount | Discrete | ABC | TapPosition | Absolute tap position | ReactivePower | Reactive power | BCSecondary | Phases BC, side measured : Secondary (second terminal) | [8 empty] | DV_RealQualityTimeTagExtended
| MAXOPCNTA | MaxOpCount | Discrete | A | TapIncrement | Tap raise/lower: Tap position increment (commanding only) | Time | Time period | ACSecondary | Phases AC, side measured : Secondary (second terminal) | [8 empty] | DV_StateQualityTimeTagExtended
| MAXOPCNTB | MaxOpCount | Discrete | B | PhaseShift | Measured or set phase angle on a phase-shifting tap changer | Humidity | Relative humidity [%] | ASecondary | Phases A, side measured : Secondary (second terminal) | [8 empty] | DV_DiscreteQualityTimeTagExtended
| MAXOPCNTC | MaxOpCount | Discrete | C | ReverseMode | Voltage regulators only: Indicates how the regulator behaves in case of reverse power flow | WindSpeed | Wind speed [km/h] | BSecondary | Phases B, side measured : Secondary (second terminal) | [8 empty] | DV_StateSuppQualityTimeTagExtended
| HOUROPCNTABC | HourlyOpCount | Discrete | ABC | Parallel | A voltage regulator is in parallel (slave) operation with another regulator | FeelsLike | Feels like: Equivalent temperature [°C] | CSecondary | Phases C, side measured : Secondary (second terminal)
| HOUROPCNTA | HourlyOpCount | Discrete | A | ControlActiveSetting | Active setting of a relay stage or regulating control. | SunshineMinutes | Sunshine minutes per hour | ABCTertiary | Phases ABC, side measured : Tertiary (applicable on three winding transformer only)
| HOUROPCNTB | HourlyOpCount | Discrete | B | ControlDelay | Initial delay of a regulating control or relay stage | SkyCover | Sky cover [%] | ATertiary | Phases A, side measured : Tertiary (applicable on three winding transformer only)
| HOUROPCNTC | HourlyOpCount | Discrete | C | ControlLimitHigh | High value of a ControlLimit | Length | Physical length | BTertiary | Phases B, side measured : Tertiary (applicable on three winding transformer only)
| DAILYPCNTABC | DailyOpCount | Discrete | ABC | ControlLimitLow | Low value of a ControlLimit | CrossSection | CrossSection | CTertiary | Phases C, side measured : Tertiary (applicable on three winding transformer only)
| DAILYOPCNTA | DailyOpCount | Discrete | A | ControlSetValue | Set point (target) of a RegulatingControl or RelayStage. | Impedance | Impedance, resistance or reactance [Ω] | N | Neutral
| DAILYOPCNTB | DailyOpCount | Discrete | B | ControlBandwidth | Bandwidth of a regulating control. The type must be the same as in the corresponding ControlSetValue signal | Admittance | Admittance, conductance or susceptance [S] | NPrimary | Neutral, side measured : Primary (first terminal)
| DAILYOPCNTC | DailyOpCount | Discrete | C | ControlSubDelay | Subsequent delay of a regulating control | ImpedancePerLength | Impedance, resistance or reactance per unit length [Ω/km] | NSecondary | Neutral, side measured : Secondary (second terminal)
| MONTOPCNTABC | MonthlyOpCount | Discrete | ABC | ControlSlopeReal | Real compensation | AdmittancePerLength | Admittance, conductance or susceptance per unit length [S/km] | Ntertiary | Neutral, side measured : Tertiary (applicable on three winding transformer only)
| MONTOPCNTA | MonthlyOpCount | Discrete | A | ControlSlopeImag | Imaginary compensation | Percent | A percentage value
| MONTOPCNTB | MonthlyOpCount | Discrete | B | RelayTrip | Indicates that a particular relay recorded a fault and caused the breaker to trip | Money | Money unit. The unit symbol is taken from system locale information.
| MONTOPCNTC | MonthlyOpCount | Discrete | C | ReclosingEnabled | Enabled reclosing operation on a ProtectionEquipment | Insolation | Insolation
| PWRONABC | PowerOn | Status | ABC | RecloserLockout | Recloser locked out | RotationSpeed | Speed of a rotational machine
| PWRONA | PowerOn | Status | A | RecloseDelay | Reclosing delay of a reclosing relay stage | Mass | Mass
| PWRONB | PowerOn | Status | B | UnderFrequencyAlarm | An underfrequency alarm was issued for the substation. | FailureRate | Annual number of faults
| PWRONC | PowerOn | Status | C | FanStatus | Status of transformer's cooling fan | SoilTemperature | Soil temperature [°C] at 1m depth. Used for default weather on WeatherRegion.
| FRWRDABC | Forward | Status | ABC | OilPumpStatus | Status of transformer's cooling oil pump | OilTemperature | Oil temperature [°C] of a PowerTransformer.
| FRWRDA | Forward | Status | A | SourceStatus | Energization status of an EnergySource or Interconnection | HotSpotTemperature | Temperature [°C] of a hotspot on a PowerTransformer winding.
| FRWRDB | Forward | Status | B | FaultCurrentSub | Value of subtransient fault current at source, calculated by an external (EMS) system. | AbsoluteDateTime | Date and time expressed in absolute terms. Internally stored as Windows filetime (number of 100-nanosecond since midnight, January 1, 1601 UTC)
| FRWRDC | Forward | Status | C | FaultAngleSub | Angle of subtransient fault current at source, calculated by an external (EMS) system. | LatLong | A pair of latitude/longitude coordinates expressed in degrees
| HLTAGABC | HotLineTag | Status | ABC | FaultCurrentTrans | Value of subtransient fault current at source, calculated by an external (EMS) system.
| HLTAGA | HotLineTag | Status | A | FaultAngleTrans | Angle of subtransient fault current at source, calculated by an external (EMS) system.
| HLTAGB | HotLineTag | Status | B | BellwetherMeter | A meter remotely accessed through AMI, used for average measurement on consumers (ServicePoint).
| HLTAGC | HotLineTag | Status | C | WeatherData | Weather measurement. Must be associated with a WeatherRegion
| CUSTDISABC | DiscreteSignalType.Custom | Status | ABC
| CUSTDISA | DiscreteSignalType.Custom | Status | A
| CUSTDISB | DiscreteSignalType.Custom | Status | B
| CUSTDISC | DiscreteSignalType.Custom | Status | C
| VOLTABC | MeasuredValue | Voltage | ABC
| VOLTAB | MeasuredValue | Voltage | AB
| VOLTBC | MeasuredValue | Voltage | BC
| VOLTAC | MeasuredValue | Voltage | AC
| VOLTA | MeasuredValue | Voltage | A
| VOLTB | MeasuredValue | Voltage | B
| VOLTC | MeasuredValue | Voltage | C
| VOLTANGABC | MeasuredValue | VoltageAngle | ABC
| VOLTANGAB | MeasuredValue | VoltageAngle | AB
| VOLTANGBC | MeasuredValue | VoltageAngle | BC
| VOLTANGAC | MeasuredValue | VoltageAngle | AC
| VOLTANGA | MeasuredValue | VoltageAngle | A
| VOLTANGB | MeasuredValue | VoltageAngle | B
| VOLTANGC | MeasuredValue | VoltageAngle | C
| FREQ | MeasuredValue | Frequency | ABC
| RELVOLTABC | MeasuredValue | RelativeVoltage | ABC
| RELVOLTAB | MeasuredValue | RelativeVoltage | AB
| RELVOLTAC | MeasuredValue | RelativeVoltage | BC
| RELVOLTBC | MeasuredValue | RelativeVoltage | AC
| RELVOLTA | MeasuredValue | RelativeVoltage | A
| RELVOLTB | MeasuredValue | RelativeVoltage | B
| RELVOLTC | MeasuredValue | RelativeVoltage | C
| AMPABC | MeasuredValue | Current | ABC
| AMPA | MeasuredValue | Current | A
| AMPB | MeasuredValue | Current | B
| AMPC | MeasuredValue | Current | C
| AMPN | MeasuredValue | Current | N
| MWABC | MeasuredValue | ActivePower | ABC
| MWA | MeasuredValue | ActivePower | A
| MWB | MeasuredValue | ActivePower | B
| MWC | MeasuredValue | ActivePower | C
| MVARABC | MeasuredValue | ReactivePower | ABC
| MVARA | MeasuredValue | ReactivePower | A
| MVARB | MeasuredValue | ReactivePower | B
| MVARC | MeasuredValue | ReactivePower | C
| MVAABC | MeasuredValue | ApparentPower | ABC
| COSPHIABC | MeasuredValue | CosPhi | ABC
| COSPHIA | MeasuredValue | CosPhi | A
| COSPHIB | MeasuredValue | CosPhi | B
| COSPHIC | MeasuredValue | CosPhi | C
| MWHABC | MeasuredValue | ActiveEnergy | ABC
| MWHA | MeasuredValue | ActiveEnergy | A
| MWHB | MeasuredValue | ActiveEnergy | B
| MWHC | MeasuredValue | ActiveEnergy | C
| MVARHABC | MeasuredValue | ReactiveEnergy | ABC
| MVARHA | MeasuredValue | ReactiveEnergy | A
| MVARHB | MeasuredValue | ReactiveEnergy | B
| MVARHC | MeasuredValue | ReactiveEnergy | C
| FLTRCDRVOLTABC | FaultRecorder | Voltage | ABC
| FLTRCDRVOLTA | FaultRecorder | Voltage | A
| FLTRCDRVOLTB | FaultRecorder | Voltage | B
| FLTRCDRVOLTC | FaultRecorder | Voltage | C
| FLTRCDRAMPABC | FaultRecorder | Current | ABC
| FLTRCDRAMPA | FaultRecorder | Current | A
| FLTRCDRAMPB | FaultRecorder | Current | B
| FLTRCDRAMPC | FaultRecorder | Current | C
| FLTRCDRVOLTANGABC | FaultRecorder | VoltageAngle | ABC
| FLTRCDRVOLTANGA | FaultRecorder | VoltageAngle | A
| FLTRCDRVOLTANGB | FaultRecorder | VoltageAngle | B
| FLTRCDRVOLTANGC | FaultRecorder | VoltageAngle | C
| FLTRCDRAMPANGABC | FaultRecorder | CurrentAngle | ABC
| FLTRCDRAMPANGA | FaultRecorder | CurrentAngle | A
| FLTRCDRAMPANGB | FaultRecorder | CurrentAngle | B
| FLTRCDRAMPANGC | FaultRecorder | CurrentAngle | C
| TMPABC | MeasuredValue | Temperature | ABC
| TMPA | MeasuredValue | Temperature | A
| TMPB | MeasuredValue | Temperature | B
| TMPC | MeasuredValue | Temperature | C
| CUSTANLM1ABC | AnalogSignalType.Custom | Unitless | ABC
| CUSTANLM1A | AnalogSignalType.Custom | Unitless | A
| CUSTANLM1B | AnalogSignalType.Custom | Unitless | B
| CUSTANLM1C | AnalogSignalType.Custom | Unitless | C
| CUSTANLM2ABC | AnalogSignalType.Custom | Voltage | ABC
| CUSTANLM2A | AnalogSignalType.Custom | Voltage | A
| CUSTANLM2B | AnalogSignalType.Custom | Voltage | B
| CUSTANLM2C | AnalogSignalType.Custom | Voltage | C
| CUSTANLM3ABC | AnalogSignalType.Custom | Current | ABC
| CUSTANLM3A | AnalogSignalType.Custom | Current | A
| CUSTANLM3B | AnalogSignalType.Custom | Current | B
| CUSTANLM3C | AnalogSignalType.Custom | Current | C
| CUSTANLM3N | AnalogSignalType.Custom | Current | N
| CUSTANLM4ABC | AnalogSignalType.Custom | ActivePower | ABC
| CUSTANLM4A | AnalogSignalType.Custom | ActivePower | A
| CUSTANLM4B | AnalogSignalType.Custom | ActivePower | B
| CUSTANLM4C | AnalogSignalType.Custom | ActivePower | C
| CUSTANLM5ABC | AnalogSignalType.Custom | ReactivePower | ABC
| CUSTANLM5A | AnalogSignalType.Custom | ReactivePower | A
| CUSTANLM5B | AnalogSignalType.Custom | ReactivePower | B
| CUSTANLM5C | AnalogSignalType.Custom | ReactivePower | C
| CUSTANLM6ABC | AnalogSignalType.Custom | Frequency | ABC
| CUSTANLM6A | AnalogSignalType.Custom | Frequency | A
| CUSTANLM6B | AnalogSignalType.Custom | Frequency | B
| CUSTANLM6C | AnalogSignalType.Custom | Frequency | C
| CUSTANLM7ABC | AnalogSignalType.Custom | Temperature | ABC
| CUSTANLM7A | AnalogSignalType.Custom | Temperature | A
| CUSTANLM7B | AnalogSignalType.Custom | Temperature | B
| CUSTANLM7C | AnalogSignalType.Custom | Temperature | C
| CUSTANLM8ABC | AnalogSignalType.Custom | ActiveEnergy | ABC
| CUSTANLM8A | AnalogSignalType.Custom | ActiveEnergy | A
| CUSTANLM8B | AnalogSignalType.Custom | ActiveEnergy | B
| CUSTANLM8C | AnalogSignalType.Custom | ActiveEnergy | C
| CUSTANLM9ABC | AnalogSignalType.Custom | ReactiveEnergy | ABC
| CUSTANLM9A | AnalogSignalType.Custom | ReactiveEnergy | A
| CUSTANLM9B | AnalogSignalType.Custom | ReactiveEnergy | B
| CUSTANLM9C | AnalogSignalType.Custom | ReactiveEnergy | C
| CUSTANLM10ABC | AnalogSignalType.Custom | ApparentPower | ABC
| CUSTANLM10A | AnalogSignalType.Custom | ApparentPower | A
| CUSTANLM10B | AnalogSignalType.Custom | ApparentPower | B
| CUSTANLM10C | AnalogSignalType.Custom | ApparentPower | C
| CUSTANLM11ABC | AnalogSignalType.Custom | VoltageAngle | ABC
| CUSTANLM11A | AnalogSignalType.Custom | VoltageAngle | A
| CUSTANLM11B | AnalogSignalType.Custom | VoltageAngle | B
| CUSTANLM11C | AnalogSignalType.Custom | VoltageAngle | C
| CUSTANLM12ABC | AnalogSignalType.Custom | Time | ABC
| CUSTANLM12A | AnalogSignalType.Custom | Time | A
| CUSTANLM12B | AnalogSignalType.Custom | Time | B
| CUSTANLM12C | AnalogSignalType.Custom | Time | C
| CUSTANLM13ABC | AnalogSignalType.Custom | Humidity | ABC
| CUSTANLM13A | AnalogSignalType.Custom | Humidity | A
| CUSTANLM13B | AnalogSignalType.Custom | Humidity | B
| CUSTANLM13C | AnalogSignalType.Custom | Humidity | C
| CUSTANLM14ABC | AnalogSignalType.Custom | WindSpeed | ABC
| CUSTANLM14A | AnalogSignalType.Custom | WindSpeed | A
| CUSTANLM14B | AnalogSignalType.Custom | WindSpeed | B
| CUSTANLM14C | AnalogSignalType.Custom | WindSpeed | C
| CUSTANLM15ABC | AnalogSignalType.Custom | FeelsLike | ABC
| CUSTANLM15A | AnalogSignalType.Custom | FeelsLike | A
| CUSTANLM15B | AnalogSignalType.Custom | FeelsLike | B
| CUSTANLM15C | AnalogSignalType.Custom | FeelsLike | C
| CUSTANLM16ABC | AnalogSignalType.Custom | SunshineMinutes | ABC
| CUSTANLM16A | AnalogSignalType.Custom | SunshineMinutes | A
| CUSTANLM16B | AnalogSignalType.Custom | SunshineMinutes | B
| CUSTANLM16C | AnalogSignalType.Custom | SunshineMinutes | C
| CUSTANLM17ABC | AnalogSignalType.Custom | SkyCover | ABC
| CUSTANLM17A | AnalogSignalType.Custom | SkyCover | A
| CUSTANLM17B | AnalogSignalType.Custom | SkyCover | B
| CUSTANLM17C | AnalogSignalType.Custom | SkyCover | C
| CUSTANLM18ABC | AnalogSignalType.Custom | Length | ABC
| CUSTANLM18A | AnalogSignalType.Custom | Length | A
| CUSTANLM18B | AnalogSignalType.Custom | Length | B
| CUSTANLM18C | AnalogSignalType.Custom | Length | C
| CUSTANLM19ABC | AnalogSignalType.Custom | CrossSection | ABC
| CUSTANLM19A | AnalogSignalType.Custom | CrossSection | A
| CUSTANLM19B | AnalogSignalType.Custom | CrossSection | B
| CUSTANLM19C | AnalogSignalType.Custom | CrossSection | C
| CUSTANLM20ABC | AnalogSignalType.Custom | Impedance | ABC
| CUSTANLM20A | AnalogSignalType.Custom | Impedance | A
| CUSTANLM20B | AnalogSignalType.Custom | Impedance | B
| CUSTANLM20C | AnalogSignalType.Custom | Impedance | C
| CUSTANLM21ABC | AnalogSignalType.Custom | Admittance | ABC
| CUSTANLM21A | AnalogSignalType.Custom | Admittance | A
| CUSTANLM21B | AnalogSignalType.Custom | Admittance | B
| CUSTANLM21C | AnalogSignalType.Custom | Admittance | C
| CUSTANLM22ABC | AnalogSignalType.Custom | ImpedancePerLength | ABC
| CUSTANLM22A | AnalogSignalType.Custom | ImpedancePerLength | A
| CUSTANLM22B | AnalogSignalType.Custom | ImpedancePerLength | B
| CUSTANLM22C | AnalogSignalType.Custom | ImpedancePerLength | C
| CUSTANLM23ABC | AnalogSignalType.Custom | AdmittancePerLength | ABC
| CUSTANLM23A | AnalogSignalType.Custom | AdmittancePerLength | A
| CUSTANLM23B | AnalogSignalType.Custom | AdmittancePerLength | B
| CUSTANLM23C | AnalogSignalType.Custom | AdmittancePerLength | C
| CUSTANLM24ABC | AnalogSignalType.Custom | Percent | ABC
| CUSTANLM24A | AnalogSignalType.Custom | Percent | A
| CUSTANLM24B | AnalogSignalType.Custom | Percent | B
| CUSTANLM24C | AnalogSignalType.Custom | Percent | C
| CUSTANLM25ABC | AnalogSignalType.Custom | Money | ABC
| CUSTANLM25A | AnalogSignalType.Custom | Money | A
| CUSTANLM25B | AnalogSignalType.Custom | Money | B
| CUSTANLM25C | AnalogSignalType.Custom | Money | C
| CUSTANLM26ABC | AnalogSignalType.Custom | RelativeVoltage | ABC
| CUSTANLM26A | AnalogSignalType.Custom | RelativeVoltage | A
| CUSTANLM26B | AnalogSignalType.Custom | RelativeVoltage | B
| CUSTANLM26C | AnalogSignalType.Custom | RelativeVoltage | C
| CUSTANLM27ABC | AnalogSignalType.Custom | Insolation | ABC
| CUSTANLM27A | AnalogSignalType.Custom | Insolation | A
| CUSTANLM27B | AnalogSignalType.Custom | Insolation | B
| CUSTANLM27C | AnalogSignalType.Custom | Insolation | C
| CUSTANLM28ABC | AnalogSignalType.Custom | CurrentAngle | ABC
| CUSTANLM28A | AnalogSignalType.Custom | CurrentAngle | A
| CUSTANLM28B | AnalogSignalType.Custom | CurrentAngle | B
| CUSTANLM28C | AnalogSignalType.Custom | CurrentAngle | C
| CUSTANLM29ABC | AnalogSignalType.Custom | RotationSpeed | ABC
| CUSTANLM29A | AnalogSignalType.Custom | RotationSpeed | A
| CUSTANLM29B | AnalogSignalType.Custom | RotationSpeed | B
| CUSTANLM29C | AnalogSignalType.Custom | RotationSpeed | C
| CUSTANLM30ABC | AnalogSignalType.Custom | Mass | ABC
| CUSTANLM30A | AnalogSignalType.Custom | Mass | A
| CUSTANLM30B | AnalogSignalType.Custom | Mass | B
| CUSTANLM30C | AnalogSignalType.Custom | Mass | C
| CUSTANLM31ABC | AnalogSignalType.Custom | FailureRate | ABC
| CUSTANLM31A | AnalogSignalType.Custom | FailureRate | A
| CUSTANLM31B | AnalogSignalType.Custom | FailureRate | B
| CUSTANLM31C | AnalogSignalType.Custom | FailureRate | C
| CUSTANLM32ABC | AnalogSignalType.Custom | SoilTemperature | ABC
| CUSTANLM32A | AnalogSignalType.Custom | SoilTemperature | A
| CUSTANLM32B | AnalogSignalType.Custom | SoilTemperature | B
| CUSTANLM32C | AnalogSignalType.Custom | SoilTemperature | C
| CUSTANLM33ABC | AnalogSignalType.Custom | OilTemperature | ABC
| CUSTANLM33A | AnalogSignalType.Custom | OilTemperature | A
| CUSTANLM33B | AnalogSignalType.Custom | OilTemperature | B
| CUSTANLM33C | AnalogSignalType.Custom | OilTemperature | C
| CUSTANLM34ABC | AnalogSignalType.Custom | HotSpotTemperature | ABC
| CUSTANLM34A | AnalogSignalType.Custom | HotSpotTemperature | A
| CUSTANLM34B | AnalogSignalType.Custom | HotSpotTemperature | B
| CUSTANLM34C | AnalogSignalType.Custom | HotSpotTemperature | C
| CUSTANLM35ABC | AnalogSignalType.Custom | AbsoluteDateTime | ABC
| CUSTANLM35A | AnalogSignalType.Custom | AbsoluteDateTime | A
| CUSTANLM35B | AnalogSignalType.Custom | AbsoluteDateTime | B
| CUSTANLM35C | AnalogSignalType.Custom | AbsoluteDateTime | C
| CUSTANLM36ABC | AnalogSignalType.Custom | LatLong | ABC
| CUSTANLM36A | AnalogSignalType.Custom | LatLong | A
| CUSTANLM36B | AnalogSignalType.Custom | LatLong | B
| CUSTANLM36C | AnalogSignalType.Custom | LatLong | C
| VOLTABCPRIM | MeasuredValue | Voltage | ABCPrimary
| VOLTABPRIM | MeasuredValue | Voltage | ABPrimary
| VOLTBCPRIM | MeasuredValue | Voltage | BCPrimary
| VOLTACPRIM | MeasuredValue | Voltage | ACPrimary
| VOLTAPRIM | MeasuredValue | Voltage | APrimary
| VOLTBPRIM | MeasuredValue | Voltage | BPrimary
| VOLTCPRIM | MeasuredValue | Voltage | CPrimary
| VOLTANGABCPRIM | MeasuredValue | VoltageAngle | ABCPrimary
| VOLTANGABPRIM | MeasuredValue | VoltageAngle | ABPrimary
| VOLTANGBCPRIM | MeasuredValue | VoltageAngle | BCPrimary
| VOLTANGACPRIM | MeasuredValue | VoltageAngle | ACPrimary
| VOLTANGAPRIM | MeasuredValue | VoltageAngle | APrimary
| VOLTANGBPRIM | MeasuredValue | VoltageAngle | BPrimary
| VOLTANGCPRIM | MeasuredValue | VoltageAngle | CPrimary
| FREQPRIM | MeasuredValue | Frequency | ABCPrimary
| RELVOLTABCPRIM | MeasuredValue | RelativeVoltage | ABCPrimary
| RELVOLTABPRIM | MeasuredValue | RelativeVoltage | ABPrimary
| RELVOLTACPRIM | MeasuredValue | RelativeVoltage | BCPrimary
| RELVOLTBCPRIM | MeasuredValue | RelativeVoltage | ACPrimary
| RELVOLTAPRIM | MeasuredValue | RelativeVoltage | APrimary
| RELVOLTBPRIM | MeasuredValue | RelativeVoltage | BPrimary
| RELVOLTCPRIM | MeasuredValue | RelativeVoltage | CPrimary
| AMPABCPRIM | MeasuredValue | Current | ABCPrimary
| AMPAPRIM | MeasuredValue | Current | APrimary
| AMPBPRIM | MeasuredValue | Current | BPrimary
| AMPCPRIM | MeasuredValue | Current | CPrimary
| AMPNPRIM | MeasuredValue | Current | NPrimary
| MWABCPRIM | MeasuredValue | ActivePower | ABCPrimary
| MWAPRIM | MeasuredValue | ActivePower | APrimary
| MWBPRIM | MeasuredValue | ActivePower | BPrimary
| MWCPRIM | MeasuredValue | ActivePower | CPrimary
| MVARABCPRIM | MeasuredValue | ReactivePower | ABCPrimary
| MVARAPRIM | MeasuredValue | ReactivePower | APrimary
| MVARBPRIM | MeasuredValue | ReactivePower | BPrimary
| MVARCPRIM | MeasuredValue | ReactivePower | CPrimary
| MVAABCPRIM | MeasuredValue | ApparentPower | ABCPrimary
| COSPHIABCPRIM | MeasuredValue | CosPhi | ABCPrimary
| COSPHIAPRIM | MeasuredValue | CosPhi | APrimary
| COSPHIBPRIM | MeasuredValue | CosPhi | BPrimary
| COSPHICPRIM | MeasuredValue | CosPhi | CPrimary
| MWHABCPRIM | MeasuredValue | ActiveEnergy | ABCPrimary
| MWHAPRIM | MeasuredValue | ActiveEnergy | APrimary
| MWHBPRIM | MeasuredValue | ActiveEnergy | BPrimary
| MWHCPRIM | MeasuredValue | ActiveEnergy | CPrimary
| MVARHABCPRIM | MeasuredValue | ReactiveEnergy | ABCPrimary
| MVARHAPRIM | MeasuredValue | ReactiveEnergy | APrimary
| MVARHBPRIM | MeasuredValue | ReactiveEnergy | BPrimary
| MVARHCPRIM | MeasuredValue | ReactiveEnergy | CPrimary
| FLTRCDRVOLTABCPRIM | FaultRecorder | Voltage | ABCPrimary
| FLTRCDRVOLTAPRIM | FaultRecorder | Voltage | APrimary
| FLTRCDRVOLTBPRIM | FaultRecorder | Voltage | BPrimary
| FLTRCDRVOLTCPRIM | FaultRecorder | Voltage | CPrimary
| FLTRCDRAMPABCPRIM | FaultRecorder | Current | ABCPrimary
| FLTRCDRAMPAPRIM | FaultRecorder | Current | APrimary
| FLTRCDRAMPBPRIM | FaultRecorder | Current | BPrimary
| FLTRCDRAMPCPRIM | FaultRecorder | Current | CPrimary
| FLTRCDRVOLTANGABCPRIM | FaultRecorder | VoltageAngle | ABCPrimary
| FLTRCDRVOLTANGAPRIM | FaultRecorder | VoltageAngle | APrimary
| FLTRCDRVOLTANGBPRIM | FaultRecorder | VoltageAngle | BPrimary
| FLTRCDRVOLTANGCPRIM | FaultRecorder | VoltageAngle | CPrimary
| FLTRCDRAMPANGABCPRIM | FaultRecorder | CurrentAngle | ABCPrimary
| FLTRCDRAMPANGAPRIM | FaultRecorder | CurrentAngle | APrimary
| FLTRCDRAMPANGBPRIM | FaultRecorder | CurrentAngle | BPrimary
| FLTRCDRAMPANGCPRIM | FaultRecorder | CurrentAngle | CPrimary
| TMPABCPRIM | MeasuredValue | Temperature | ABCPrimary
| TMPAPRIM | MeasuredValue | Temperature | APrimary
| TMPBPRIM | MeasuredValue | Temperature | BPrimary
| TMPCPRIM | MeasuredValue | Temperature | CPrimary
| CUSTANLM1ABCPRIM | AnalogSignalType.Custom | Unitless | ABCPrimary
| CUSTANLM1APRIM | AnalogSignalType.Custom | Unitless | APrimary
| CUSTANLM1BPRIM | AnalogSignalType.Custom | Unitless | BPrimary
| CUSTANLM1CPRIM | AnalogSignalType.Custom | Unitless | CPrimary
| CUSTANLM2ABCPRIM | AnalogSignalType.Custom | Voltage | ABCPrimary
| CUSTANLM2APRIM | AnalogSignalType.Custom | Voltage | APrimary
| CUSTANLM2BPRIM | AnalogSignalType.Custom | Voltage | BPrimary
| CUSTANLM2CPRIM | AnalogSignalType.Custom | Voltage | CPrimary
| CUSTANLM3ABCPRIM | AnalogSignalType.Custom | Current | ABCPrimary
| CUSTANLM3APRIM | AnalogSignalType.Custom | Current | APrimary
| CUSTANLM3BPRIM | AnalogSignalType.Custom | Current | BPrimary
| CUSTANLM3CPRIM | AnalogSignalType.Custom | Current | CPrimary
| CUSTANLM3NPRIM | AnalogSignalType.Custom | Current | NPrimary
| CUSTANLM4ABCPRIM | AnalogSignalType.Custom | ActivePower | ABCPrimary
| CUSTANLM4APRIM | AnalogSignalType.Custom | ActivePower | APrimary
| CUSTANLM4BPRIM | AnalogSignalType.Custom | ActivePower | BPrimary
| CUSTANLM4CPRIM | AnalogSignalType.Custom | ActivePower | CPrimary
| CUSTANLM5ABCPRIM | AnalogSignalType.Custom | ReactivePower | ABCPrimary
| CUSTANLM5APRIM | AnalogSignalType.Custom | ReactivePower | APrimary
| CUSTANLM5BPRIM | AnalogSignalType.Custom | ReactivePower | BPrimary
| CUSTANLM5CPRIM | AnalogSignalType.Custom | ReactivePower | CPrimary
| CUSTANLM6ABCPRIM | AnalogSignalType.Custom | Frequency | ABCPrimary
| CUSTANLM6APRIM | AnalogSignalType.Custom | Frequency | APrimary
| CUSTANLM6BPRIM | AnalogSignalType.Custom | Frequency | BPrimary
| CUSTANLM6CPRIM | AnalogSignalType.Custom | Frequency | CPrimary
| CUSTANLM7ABCPRIM | AnalogSignalType.Custom | Temperature | ABCPrimary
| CUSTANLM7APRIM | AnalogSignalType.Custom | Temperature | APrimary
| CUSTANLM7BPRIM | AnalogSignalType.Custom | Temperature | BPrimary
| CUSTANLM7CPRIM | AnalogSignalType.Custom | Temperature | CPrimary
| CUSTANLM8ABCPRIM | AnalogSignalType.Custom | ActiveEnergy | ABCPrimary
| CUSTANLM8APRIM | AnalogSignalType.Custom | ActiveEnergy | APrimary
| CUSTANLM8BPRIM | AnalogSignalType.Custom | ActiveEnergy | BPrimary
| CUSTANLM8CPRIM | AnalogSignalType.Custom | ActiveEnergy | CPrimary
| CUSTANLM9ABCPRIM | AnalogSignalType.Custom | ReactiveEnergy | ABCPrimary
| CUSTANLM9APRIM | AnalogSignalType.Custom | ReactiveEnergy | APrimary
| CUSTANLM9BPRIM | AnalogSignalType.Custom | ReactiveEnergy | BPrimary
| CUSTANLM9CPRIM | AnalogSignalType.Custom | ReactiveEnergy | CPrimary
| CUSTANLM10ABCPRIM | AnalogSignalType.Custom | ApparentPower | ABCPrimary
| CUSTANLM10APRIM | AnalogSignalType.Custom | ApparentPower | APrimary
| CUSTANLM10BPRIM | AnalogSignalType.Custom | ApparentPower | BPrimary
| CUSTANLM10CPRIM | AnalogSignalType.Custom | ApparentPower | CPrimary
| CUSTANLM11ABCPRIM | AnalogSignalType.Custom | VoltageAngle | ABCPrimary
| CUSTANLM11APRIM | AnalogSignalType.Custom | VoltageAngle | APrimary
| CUSTANLM11BPRIM | AnalogSignalType.Custom | VoltageAngle | BPrimary
| CUSTANLM11CPRIM | AnalogSignalType.Custom | VoltageAngle | CPrimary
| CUSTANLM12ABCPRIM | AnalogSignalType.Custom | Time | ABCPrimary
| CUSTANLM12APRIM | AnalogSignalType.Custom | Time | APrimary
| CUSTANLM12BPRIM | AnalogSignalType.Custom | Time | BPrimary
| CUSTANLM12CPRIM | AnalogSignalType.Custom | Time | CPrimary
| CUSTANLM13ABCPRIM | AnalogSignalType.Custom | Humidity | ABCPrimary
| CUSTANLM13APRIM | AnalogSignalType.Custom | Humidity | APrimary
| CUSTANLM13BPRIM | AnalogSignalType.Custom | Humidity | BPrimary
| CUSTANLM13CPRIM | AnalogSignalType.Custom | Humidity | CPrimary
| CUSTANLM14ABCPRIM | AnalogSignalType.Custom | WindSpeed | ABCPrimary
| CUSTANLM14APRIM | AnalogSignalType.Custom | WindSpeed | APrimary
| CUSTANLM14BPRIM | AnalogSignalType.Custom | WindSpeed | BPrimary
| CUSTANLM14CPRIM | AnalogSignalType.Custom | WindSpeed | CPrimary
| CUSTANLM15ABCPRIM | AnalogSignalType.Custom | FeelsLike | ABCPrimary
| CUSTANLM15APRIM | AnalogSignalType.Custom | FeelsLike | APrimary
| CUSTANLM15BPRIM | AnalogSignalType.Custom | FeelsLike | BPrimary
| CUSTANLM15CPRIM | AnalogSignalType.Custom | FeelsLike | CPrimary
| CUSTANLM16ABCPRIM | AnalogSignalType.Custom | SunshineMinutes | ABCPrimary
| CUSTANLM16APRIM | AnalogSignalType.Custom | SunshineMinutes | APrimary
| CUSTANLM16BPRIM | AnalogSignalType.Custom | SunshineMinutes | BPrimary
| CUSTANLM16CPRIM | AnalogSignalType.Custom | SunshineMinutes | CPrimary
| CUSTANLM17ABCPRIM | AnalogSignalType.Custom | SkyCover | ABCPrimary
| CUSTANLM17APRIM | AnalogSignalType.Custom | SkyCover | APrimary
| CUSTANLM17BPRIM | AnalogSignalType.Custom | SkyCover | BPrimary
| CUSTANLM17CPRIM | AnalogSignalType.Custom | SkyCover | CPrimary
| CUSTANLM18ABCPRIM | AnalogSignalType.Custom | Length | ABCPrimary
| CUSTANLM18APRIM | AnalogSignalType.Custom | Length | APrimary
| CUSTANLM18BPRIM | AnalogSignalType.Custom | Length | BPrimary
| CUSTANLM18CPRIM | AnalogSignalType.Custom | Length | CPrimary
| CUSTANLM19ABCPRIM | AnalogSignalType.Custom | CrossSection | ABCPrimary
| CUSTANLM19APRIM | AnalogSignalType.Custom | CrossSection | APrimary
| CUSTANLM19BPRIM | AnalogSignalType.Custom | CrossSection | BPrimary
| CUSTANLM19CPRIM | AnalogSignalType.Custom | CrossSection | CPrimary
| CUSTANLM20ABCPRIM | AnalogSignalType.Custom | Impedance | ABCPrimary
| CUSTANLM20APRIM | AnalogSignalType.Custom | Impedance | APrimary
| CUSTANLM20BPRIM | AnalogSignalType.Custom | Impedance | BPrimary
| CUSTANLM20CPRIM | AnalogSignalType.Custom | Impedance | CPrimary
| CUSTANLM21ABCPRIM | AnalogSignalType.Custom | Admittance | ABCPrimary
| CUSTANLM21APRIM | AnalogSignalType.Custom | Admittance | APrimary
| CUSTANLM21BPRIM | AnalogSignalType.Custom | Admittance | BPrimary
| CUSTANLM21CPRIM | AnalogSignalType.Custom | Admittance | CPrimary
| CUSTANLM22ABCPRIM | AnalogSignalType.Custom | ImpedancePerLength | ABCPrimary
| CUSTANLM22APRIM | AnalogSignalType.Custom | ImpedancePerLength | APrimary
| CUSTANLM22BPRIM | AnalogSignalType.Custom | ImpedancePerLength | BPrimary
| CUSTANLM22CPRIM | AnalogSignalType.Custom | ImpedancePerLength | CPrimary
| CUSTANLM23ABCPRIM | AnalogSignalType.Custom | AdmittancePerLength | ABCPrimary
| CUSTANLM23APRIM | AnalogSignalType.Custom | AdmittancePerLength | APrimary
| CUSTANLM23BPRIM | AnalogSignalType.Custom | AdmittancePerLength | BPrimary
| CUSTANLM23CPRIM | AnalogSignalType.Custom | AdmittancePerLength | CPrimary
| CUSTANLM24ABCPRIM | AnalogSignalType.Custom | Percent | ABCPrimary
| CUSTANLM24APRIM | AnalogSignalType.Custom | Percent | APrimary
| CUSTANLM24BPRIM | AnalogSignalType.Custom | Percent | BPrimary
| CUSTANLM24CPRIM | AnalogSignalType.Custom | Percent | CPrimary
| CUSTANLM25ABCPRIM | AnalogSignalType.Custom | Money | ABCPrimary
| CUSTANLM25APRIM | AnalogSignalType.Custom | Money | APrimary
| CUSTANLM25BPRIM | AnalogSignalType.Custom | Money | BPrimary
| CUSTANLM25CPRIM | AnalogSignalType.Custom | Money | CPrimary
| CUSTANLM26ABCPRIM | AnalogSignalType.Custom | RelativeVoltage | ABCPrimary
| CUSTANLM26APRIM | AnalogSignalType.Custom | RelativeVoltage | APrimary
| CUSTANLM26BPRIM | AnalogSignalType.Custom | RelativeVoltage | BPrimary
| CUSTANLM26CPRIM | AnalogSignalType.Custom | RelativeVoltage | CPrimary
| CUSTANLM27ABCPRIM | AnalogSignalType.Custom | Insolation | ABCPrimary
| CUSTANLM27APRIM | AnalogSignalType.Custom | Insolation | APrimary
| CUSTANLM27BPRIM | AnalogSignalType.Custom | Insolation | BPrimary
| CUSTANLM27CPRIM | AnalogSignalType.Custom | Insolation | CPrimary
| CUSTANLM28ABCPRIM | AnalogSignalType.Custom | CurrentAngle | ABCPrimary
| CUSTANLM28APRIM | AnalogSignalType.Custom | CurrentAngle | APrimary
| CUSTANLM28BPRIM | AnalogSignalType.Custom | CurrentAngle | BPrimary
| CUSTANLM28CPRIM | AnalogSignalType.Custom | CurrentAngle | CPrimary
| CUSTANLM29ABCPRIM | AnalogSignalType.Custom | RotationSpeed | ABCPrimary
| CUSTANLM29APRIM | AnalogSignalType.Custom | RotationSpeed | APrimary
| CUSTANLM29BPRIM | AnalogSignalType.Custom | RotationSpeed | BPrimary
| CUSTANLM29CPRIM | AnalogSignalType.Custom | RotationSpeed | CPrimary
| CUSTANLM30ABCPRIM | AnalogSignalType.Custom | Mass | ABCPrimary
| CUSTANLM30APRIM | AnalogSignalType.Custom | Mass | APrimary
| CUSTANLM30BPRIM | AnalogSignalType.Custom | Mass | BPrimary
| CUSTANLM30CPRIM | AnalogSignalType.Custom | Mass | CPrimary
| CUSTANLM31ABCPRIM | AnalogSignalType.Custom | FailureRate | ABCPrimary
| CUSTANLM31APRIM | AnalogSignalType.Custom | FailureRate | APrimary
| CUSTANLM31BPRIM | AnalogSignalType.Custom | FailureRate | BPrimary
| CUSTANLM31CPRIM | AnalogSignalType.Custom | FailureRate | CPrimary
| CUSTANLM32ABCPRIM | AnalogSignalType.Custom | SoilTemperature | ABCPrimary
| CUSTANLM32APRIM | AnalogSignalType.Custom | SoilTemperature | APrimary
| CUSTANLM32BPRIM | AnalogSignalType.Custom | SoilTemperature | BPrimary
| CUSTANLM32CPRIM | AnalogSignalType.Custom | SoilTemperature | CPrimary
| CUSTANLM33ABCPRIM | AnalogSignalType.Custom | OilTemperature | ABCPrimary
| CUSTANLM33APRIM | AnalogSignalType.Custom | OilTemperature | APrimary
| CUSTANLM33BPRIM | AnalogSignalType.Custom | OilTemperature | BPrimary
| CUSTANLM33CPRIM | AnalogSignalType.Custom | OilTemperature | CPrimary
| CUSTANLM34ABCPRIM | AnalogSignalType.Custom | HotSpotTemperature | ABCPrimary
| CUSTANLM34APRIM | AnalogSignalType.Custom | HotSpotTemperature | APrimary
| CUSTANLM34BPRIM | AnalogSignalType.Custom | HotSpotTemperature | BPrimary
| CUSTANLM34CPRIM | AnalogSignalType.Custom | HotSpotTemperature | CPrimary
| CUSTANLM35ABCPRIM | AnalogSignalType.Custom | AbsoluteDateTime | ABCPrimary
| CUSTANLM35APRIM | AnalogSignalType.Custom | AbsoluteDateTime | APrimary
| CUSTANLM35BPRIM | AnalogSignalType.Custom | AbsoluteDateTime | BPrimary
| CUSTANLM35CPRIM | AnalogSignalType.Custom | AbsoluteDateTime | CPrimary
| CUSTANLM36ABCPRIM | AnalogSignalType.Custom | LatLong | ABCPrimary
| CUSTANLM36APRIM | AnalogSignalType.Custom | LatLong | APrimary
| CUSTANLM36BPRIM | AnalogSignalType.Custom | LatLong | BPrimary
| CUSTANLM36CPRIM | AnalogSignalType.Custom | LatLong | CPrimary
| VOLTABCSEC | MeasuredValue | Voltage | ABCSecondary
| VOLTABSEC | MeasuredValue | Voltage | ABSecondary
| VOLTBCSEC | MeasuredValue | Voltage | BCSecondary
| VOLTACSEC | MeasuredValue | Voltage | ACSecondary
| VOLTASEC | MeasuredValue | Voltage | ASecondary
| VOLTBSEC | MeasuredValue | Voltage | BSecondary
| VOLTCSEC | MeasuredValue | Voltage | CSecondary
| VOLTANGABCSEC | MeasuredValue | VoltageAngle | ABCSecondary
| VOLTANGABSEC | MeasuredValue | VoltageAngle | ABSecondary
| VOLTANGBCSEC | MeasuredValue | VoltageAngle | BCSecondary
| VOLTANGACSEC | MeasuredValue | VoltageAngle | ACSecondary
| VOLTANGASEC | MeasuredValue | VoltageAngle | ASecondary
| VOLTANGBSEC | MeasuredValue | VoltageAngle | BSecondary
| VOLTANGCSEC | MeasuredValue | VoltageAngle | CSecondary
| FREQSEC | MeasuredValue | Frequency | ABCSecondary
| RELVOLTABCSEC | MeasuredValue | RelativeVoltage | ABCSecondary
| RELVOLTABSEC | MeasuredValue | RelativeVoltage | ABSecondary
| RELVOLTACSEC | MeasuredValue | RelativeVoltage | BCSecondary
| RELVOLTBCSEC | MeasuredValue | RelativeVoltage | ACSecondary
| RELVOLTASEC | MeasuredValue | RelativeVoltage | ASecondary
| RELVOLTBSEC | MeasuredValue | RelativeVoltage | BSecondary
| RELVOLTCSEC | MeasuredValue | RelativeVoltage | CSecondary
| AMPABCSEC | MeasuredValue | Current | ABCSecondary
| AMPASEC | MeasuredValue | Current | ASecondary
| AMPBSEC | MeasuredValue | Current | BSecondary
| AMPCSEC | MeasuredValue | Current | CSecondary
| AMPNSEC | MeasuredValue | Current | NSecondary
| MWABCSEC | MeasuredValue | ActivePower | ABCSecondary
| MWASEC | MeasuredValue | ActivePower | ASecondary
| MWBSEC | MeasuredValue | ActivePower | BSecondary
| MWCSEC | MeasuredValue | ActivePower | CSecondary
| MVARABCSEC | MeasuredValue | ReactivePower | ABCSecondary
| MVARASEC | MeasuredValue | ReactivePower | ASecondary
| MVARBSEC | MeasuredValue | ReactivePower | BSecondary
| MVARCSEC | MeasuredValue | ReactivePower | CSecondary
| MVAABCSEC | MeasuredValue | ApparentPower | ABCSecondary
| COSPHIABCSEC | MeasuredValue | CosPhi | ABCSecondary
| COSPHIASEC | MeasuredValue | CosPhi | ASecondary
| COSPHIBSEC | MeasuredValue | CosPhi | BSecondary
| COSPHICSEC | MeasuredValue | CosPhi | CSecondary
| MWHABCSEC | MeasuredValue | ActiveEnergy | ABCSecondary
| MWHASEC | MeasuredValue | ActiveEnergy | ASecondary
| MWHBSEC | MeasuredValue | ActiveEnergy | BSecondary
| MWHCSEC | MeasuredValue | ActiveEnergy | CSecondary
| MVARHABCSEC | MeasuredValue | ReactiveEnergy | ABCSecondary
| MVARHASEC | MeasuredValue | ReactiveEnergy | ASecondary
| MVARHBSEC | MeasuredValue | ReactiveEnergy | BSecondary
| MVARHCSEC | MeasuredValue | ReactiveEnergy | CSecondary
| FLTRCDRVOLTABCSEC | FaultRecorder | Voltage | ABCSecondary
| FLTRCDRVOLTASEC | FaultRecorder | Voltage | ASecondary
| FLTRCDRVOLTBSEC | FaultRecorder | Voltage | BSecondary
| FLTRCDRVOLTCSEC | FaultRecorder | Voltage | CSecondary
| FLTRCDRAMPABCSEC | FaultRecorder | Current | ABCSecondary
| FLTRCDRAMPASEC | FaultRecorder | Current | ASecondary
| FLTRCDRAMPBSEC | FaultRecorder | Current | BSecondary
| FLTRCDRAMPCSEC | FaultRecorder | Current | CSecondary
| FLTRCDRVOLTANGABCSEC | FaultRecorder | VoltageAngle | ABCSecondary
| FLTRCDRVOLTANGASEC | FaultRecorder | VoltageAngle | ASecondary
| FLTRCDRVOLTANGBSEC | FaultRecorder | VoltageAngle | BSecondary
| FLTRCDRVOLTANGCSEC | FaultRecorder | VoltageAngle | CSecondary
| FLTRCDRAMPANGABCSEC | FaultRecorder | CurrentAngle | ABCSecondary
| FLTRCDRAMPANGASEC | FaultRecorder | CurrentAngle | ASecondary
| FLTRCDRAMPANGBSEC | FaultRecorder | CurrentAngle | BSecondary
| FLTRCDRAMPANGCSEC | FaultRecorder | CurrentAngle | CSecondary
| TMPABCSEC | MeasuredValue | Temperature | ABCSecondary
| TMPASEC | MeasuredValue | Temperature | ASecondary
| TMPBSEC | MeasuredValue | Temperature | BSecondary
| TMPCSEC | MeasuredValue | Temperature | CSecondary
| CUSTANLM1ABCSEC | AnalogSignalType.Custom | Unitless | ABCSecondary
| CUSTANLM1ASEC | AnalogSignalType.Custom | Unitless | ASecondary
| CUSTANLM1BSEC | AnalogSignalType.Custom | Unitless | BSecondary
| CUSTANLM1CSEC | AnalogSignalType.Custom | Unitless | CSecondary
| CUSTANLM2ABCSEC | AnalogSignalType.Custom | Voltage | ABCSecondary
| CUSTANLM2ASEC | AnalogSignalType.Custom | Voltage | ASecondary
| CUSTANLM2BSEC | AnalogSignalType.Custom | Voltage | BSecondary
| CUSTANLM2CSEC | AnalogSignalType.Custom | Voltage | CSecondary
| CUSTANLM3ABCSEC | AnalogSignalType.Custom | Current | ABCSecondary
| CUSTANLM3ASEC | AnalogSignalType.Custom | Current | ASecondary
| CUSTANLM3BSEC | AnalogSignalType.Custom | Current | BSecondary
| CUSTANLM3CSEC | AnalogSignalType.Custom | Current | CSecondary
| CUSTANLM3NSEC | AnalogSignalType.Custom | Current | NSecondary
| CUSTANLM4ABCSEC | AnalogSignalType.Custom | ActivePower | ABCSecondary
| CUSTANLM4ASEC | AnalogSignalType.Custom | ActivePower | ASecondary
| CUSTANLM4BSEC | AnalogSignalType.Custom | ActivePower | BSecondary
| CUSTANLM4CSEC | AnalogSignalType.Custom | ActivePower | CSecondary
| CUSTANLM5ABCSEC | AnalogSignalType.Custom | ReactivePower | ABCSecondary
| CUSTANLM5ASEC | AnalogSignalType.Custom | ReactivePower | ASecondary
| CUSTANLM5BSEC | AnalogSignalType.Custom | ReactivePower | BSecondary
| CUSTANLM5CSEC | AnalogSignalType.Custom | ReactivePower | CSecondary
| CUSTANLM6ABCSEC | AnalogSignalType.Custom | Frequency | ABCSecondary
| CUSTANLM6ASEC | AnalogSignalType.Custom | Frequency | ASecondary
| CUSTANLM6BSEC | AnalogSignalType.Custom | Frequency | BSecondary
| CUSTANLM6CSEC | AnalogSignalType.Custom | Frequency | CSecondary
| CUSTANLM7ABCSEC | AnalogSignalType.Custom | Temperature | ABCSecondary
| CUSTANLM7ASEC | AnalogSignalType.Custom | Temperature | ASecondary
| CUSTANLM7BSEC | AnalogSignalType.Custom | Temperature | BSecondary
| CUSTANLM7CSEC | AnalogSignalType.Custom | Temperature | CSecondary
| CUSTANLM8ABCSEC | AnalogSignalType.Custom | ActiveEnergy | ABCSecondary
| CUSTANLM8ASEC | AnalogSignalType.Custom | ActiveEnergy | ASecondary
| CUSTANLM8BSEC | AnalogSignalType.Custom | ActiveEnergy | BSecondary
| CUSTANLM8CSEC | AnalogSignalType.Custom | ActiveEnergy | CSecondary
| CUSTANLM9ABCSEC | AnalogSignalType.Custom | ReactiveEnergy | ABCSecondary
| CUSTANLM9ASEC | AnalogSignalType.Custom | ReactiveEnergy | ASecondary
| CUSTANLM9BSEC | AnalogSignalType.Custom | ReactiveEnergy | BSecondary
| CUSTANLM9CSEC | AnalogSignalType.Custom | ReactiveEnergy | CSecondary
| CUSTANLM10ABCSEC | AnalogSignalType.Custom | ApparentPower | ABCSecondary
| CUSTANLM10ASEC | AnalogSignalType.Custom | ApparentPower | ASecondary
| CUSTANLM10BSEC | AnalogSignalType.Custom | ApparentPower | BSecondary
| CUSTANLM10CSEC | AnalogSignalType.Custom | ApparentPower | CSecondary
| CUSTANLM11ABCSEC | AnalogSignalType.Custom | VoltageAngle | ABCSecondary
| CUSTANLM11ASEC | AnalogSignalType.Custom | VoltageAngle | ASecondary
| CUSTANLM11BSEC | AnalogSignalType.Custom | VoltageAngle | BSecondary
| CUSTANLM11CSEC | AnalogSignalType.Custom | VoltageAngle | CSecondary
| CUSTANLM12ABCSEC | AnalogSignalType.Custom | Time | ABCSecondary
| CUSTANLM12ASEC | AnalogSignalType.Custom | Time | ASecondary
| CUSTANLM12BSEC | AnalogSignalType.Custom | Time | BSecondary
| CUSTANLM12CSEC | AnalogSignalType.Custom | Time | CSecondary
| CUSTANLM13ABCSEC | AnalogSignalType.Custom | Humidity | ABCSecondary
| CUSTANLM13ASEC | AnalogSignalType.Custom | Humidity | ASecondary
| CUSTANLM13BSEC | AnalogSignalType.Custom | Humidity | BSecondary
| CUSTANLM13CSEC | AnalogSignalType.Custom | Humidity | CSecondary
| CUSTANLM14ABCSEC | AnalogSignalType.Custom | WindSpeed | ABCSecondary
| CUSTANLM14ASEC | AnalogSignalType.Custom | WindSpeed | ASecondary
| CUSTANLM14BSEC | AnalogSignalType.Custom | WindSpeed | BSecondary
| CUSTANLM14CSEC | AnalogSignalType.Custom | WindSpeed | CSecondary
| CUSTANLM15ABCSEC | AnalogSignalType.Custom | FeelsLike | ABCSecondary
| CUSTANLM15ASEC | AnalogSignalType.Custom | FeelsLike | ASecondary
| CUSTANLM15BSEC | AnalogSignalType.Custom | FeelsLike | BSecondary
| CUSTANLM15CSEC | AnalogSignalType.Custom | FeelsLike | CSecondary
| CUSTANLM16ABCSEC | AnalogSignalType.Custom | SunshineMinutes | ABCSecondary
| CUSTANLM16ASEC | AnalogSignalType.Custom | SunshineMinutes | ASecondary
| CUSTANLM16BSEC | AnalogSignalType.Custom | SunshineMinutes | BSecondary
| CUSTANLM16CSEC | AnalogSignalType.Custom | SunshineMinutes | CSecondary
| CUSTANLM17ABCSEC | AnalogSignalType.Custom | SkyCover | ABCSecondary
| CUSTANLM17ASEC | AnalogSignalType.Custom | SkyCover | ASecondary
| CUSTANLM17BSEC | AnalogSignalType.Custom | SkyCover | BSecondary
| CUSTANLM17CSEC | AnalogSignalType.Custom | SkyCover | CSecondary
| CUSTANLM18ABCSEC | AnalogSignalType.Custom | Length | ABCSecondary
| CUSTANLM18ASEC | AnalogSignalType.Custom | Length | ASecondary
| CUSTANLM18BSEC | AnalogSignalType.Custom | Length | BSecondary
| CUSTANLM18CSEC | AnalogSignalType.Custom | Length | CSecondary
| CUSTANLM19ABCSEC | AnalogSignalType.Custom | CrossSection | ABCSecondary
| CUSTANLM19ASEC | AnalogSignalType.Custom | CrossSection | ASecondary
| CUSTANLM19BSEC | AnalogSignalType.Custom | CrossSection | BSecondary
| CUSTANLM19CSEC | AnalogSignalType.Custom | CrossSection | CSecondary
| CUSTANLM20ABCSEC | AnalogSignalType.Custom | Impedance | ABCSecondary
| CUSTANLM20ASEC | AnalogSignalType.Custom | Impedance | ASecondary
| CUSTANLM20BSEC | AnalogSignalType.Custom | Impedance | BSecondary
| CUSTANLM20CSEC | AnalogSignalType.Custom | Impedance | CSecondary
| CUSTANLM21ABCSEC | AnalogSignalType.Custom | Admittance | ABCSecondary
| CUSTANLM21ASEC | AnalogSignalType.Custom | Admittance | ASecondary
| CUSTANLM21BSEC | AnalogSignalType.Custom | Admittance | BSecondary
| CUSTANLM21CSEC | AnalogSignalType.Custom | Admittance | CSecondary
| CUSTANLM22ABCSEC | AnalogSignalType.Custom | ImpedancePerLength | ABCSecondary
| CUSTANLM22ASEC | AnalogSignalType.Custom | ImpedancePerLength | ASecondary
| CUSTANLM22BSEC | AnalogSignalType.Custom | ImpedancePerLength | BSecondary
| CUSTANLM22CSEC | AnalogSignalType.Custom | ImpedancePerLength | CSecondary
| CUSTANLM23ABCSEC | AnalogSignalType.Custom | AdmittancePerLength | ABCSecondary
| CUSTANLM23ASEC | AnalogSignalType.Custom | AdmittancePerLength | ASecondary
| CUSTANLM23BSEC | AnalogSignalType.Custom | AdmittancePerLength | BSecondary
| CUSTANLM23CSEC | AnalogSignalType.Custom | AdmittancePerLength | CSecondary
| CUSTANLM24ABCSEC | AnalogSignalType.Custom | Percent | ABCSecondary
| CUSTANLM24ASEC | AnalogSignalType.Custom | Percent | ASecondary
| CUSTANLM24BSEC | AnalogSignalType.Custom | Percent | BSecondary
| CUSTANLM24CSEC | AnalogSignalType.Custom | Percent | CSecondary
| CUSTANLM25ABCSEC | AnalogSignalType.Custom | Money | ABCSecondary
| CUSTANLM25ASEC | AnalogSignalType.Custom | Money | ASecondary
| CUSTANLM25BSEC | AnalogSignalType.Custom | Money | BSecondary
| CUSTANLM25CSEC | AnalogSignalType.Custom | Money | CSecondary
| CUSTANLM26ABCSEC | AnalogSignalType.Custom | RelativeVoltage | ABCSecondary
| CUSTANLM26ASEC | AnalogSignalType.Custom | RelativeVoltage | ASecondary
| CUSTANLM26BSEC | AnalogSignalType.Custom | RelativeVoltage | BSecondary
| CUSTANLM26CSEC | AnalogSignalType.Custom | RelativeVoltage | CSecondary
| CUSTANLM27ABCSEC | AnalogSignalType.Custom | Insolation | ABCSecondary
| CUSTANLM27ASEC | AnalogSignalType.Custom | Insolation | ASecondary
| CUSTANLM27BSEC | AnalogSignalType.Custom | Insolation | BSecondary
| CUSTANLM27CSEC | AnalogSignalType.Custom | Insolation | CSecondary
| CUSTANLM28ABCSEC | AnalogSignalType.Custom | CurrentAngle | ABCSecondary
| CUSTANLM28ASEC | AnalogSignalType.Custom | CurrentAngle | ASecondary
| CUSTANLM28BSEC | AnalogSignalType.Custom | CurrentAngle | BSecondary
| CUSTANLM28CSEC | AnalogSignalType.Custom | CurrentAngle | CSecondary
| CUSTANLM29ABCSEC | AnalogSignalType.Custom | RotationSpeed | ABCSecondary
| CUSTANLM29ASEC | AnalogSignalType.Custom | RotationSpeed | ASecondary
| CUSTANLM29BSEC | AnalogSignalType.Custom | RotationSpeed | BSecondary
| CUSTANLM29CSEC | AnalogSignalType.Custom | RotationSpeed | CSecondary
| CUSTANLM30ABCSEC | AnalogSignalType.Custom | Mass | ABCSecondary
| CUSTANLM30ASEC | AnalogSignalType.Custom | Mass | ASecondary
| CUSTANLM30BSEC | AnalogSignalType.Custom | Mass | BSecondary
| CUSTANLM30CSEC | AnalogSignalType.Custom | Mass | CSecondary
| CUSTANLM31ABCSEC | AnalogSignalType.Custom | FailureRate | ABCSecondary
| CUSTANLM31ASEC | AnalogSignalType.Custom | FailureRate | ASecondary
| CUSTANLM31BSEC | AnalogSignalType.Custom | FailureRate | BSecondary
| CUSTANLM31CSEC | AnalogSignalType.Custom | FailureRate | CSecondary
| CUSTANLM32ABCSEC | AnalogSignalType.Custom | SoilTemperature | ABCSecondary
| CUSTANLM32ASEC | AnalogSignalType.Custom | SoilTemperature | ASecondary
| CUSTANLM32BSEC | AnalogSignalType.Custom | SoilTemperature | BSecondary
| CUSTANLM32CSEC | AnalogSignalType.Custom | SoilTemperature | CSecondary
| CUSTANLM33ABCSEC | AnalogSignalType.Custom | OilTemperature | ABCSecondary
| CUSTANLM33ASEC | AnalogSignalType.Custom | OilTemperature | ASecondary
| CUSTANLM33BSEC | AnalogSignalType.Custom | OilTemperature | BSecondary
| CUSTANLM33CSEC | AnalogSignalType.Custom | OilTemperature | CSecondary
| CUSTANLM34ABCSEC | AnalogSignalType.Custom | HotSpotTemperature | ABCSecondary
| CUSTANLM34ASEC | AnalogSignalType.Custom | HotSpotTemperature | ASecondary
| CUSTANLM34BSEC | AnalogSignalType.Custom | HotSpotTemperature | BSecondary
| CUSTANLM34CSEC | AnalogSignalType.Custom | HotSpotTemperature | CSecondary
| CUSTANLM35ABCSEC | AnalogSignalType.Custom | AbsoluteDateTime | ABCSecondary
| CUSTANLM35ASEC | AnalogSignalType.Custom | AbsoluteDateTime | ASecondary
| CUSTANLM35BSEC | AnalogSignalType.Custom | AbsoluteDateTime | BSecondary
| CUSTANLM35CSEC | AnalogSignalType.Custom | AbsoluteDateTime | CSecondary
| CUSTANLM36ABCSEC | AnalogSignalType.Custom | LatLong | ABCSecondary
| CUSTANLM36ASEC | AnalogSignalType.Custom | LatLong | ASecondary
| CUSTANLM36BSEC | AnalogSignalType.Custom | LatLong | BSecondary
| CUSTANLM36CSEC | AnalogSignalType.Custom | LatLong | CSecondary
| ENBLABC | Enabled | Status | ABC
| ENBLA | Enabled | Status | A
| ENBLB | Enabled | Status | B
| ENBLC | Enabled | Status | C
| TCHPOSABC | TapPosition | Discrete | ABC
| TCHPOSA | TapPosition | Discrete | A
| TCHPOSB | TapPosition | Discrete | B
| TCHPOSC | TapPosition | Discrete | C
| TCHINCABC | TapIncrement | Status | ABC
| TCHINCA | TapIncrement | Status | A
| TCHINCB | TapIncrement | Status | B
| TCHINCC | TapIncrement | Status | C
| PHSHIFTABC | PhaseShift | CurrentAngle | ABC
| REVMODEABC | ReverseMode | Discrete | ABC
| REVMODEA | ReverseMode | Discrete | A
| REVMODEB | ReverseMode | Discrete | B
| REVMODEC | ReverseMode | Discrete | C
| PARALLELABC | Parallel | Status | ABC
| PARALLELA | Parallel | Status | A
| PARALLELB | Parallel | Status | B
| PARALLELC | Parallel | Status | C
| LBONUSABC | Enabled | Status | ABC
| LBONUSA | Enabled | Status | A
| LBONUSB | Enabled | Status | B
| LBONUSC | Enabled | Status | C
| CTRLACTSETTABC | ControlActiveSetting | Discrete | ABC
| CTRLACTSETTA | ControlActiveSetting | Discrete | A
| CTRLACTSETTB | ControlActiveSetting | Discrete | B
| CTRLACTSETTC | ControlActiveSetting | Discrete | C
| CTRLDLYABC | ControlDelay | Time | ABC
| CTRLDLYA | ControlDelay | Time | A
| CTRLDLYB | ControlDelay | Time | B
| CTRLDLYC | ControlDelay | Time | C
| CTRLLMTHGHVOLTABC | ControlLimitHigh | Voltage | ABC
| CTRLLMTHGHVOLTA | ControlLimitHigh | Voltage | A
| CTRLLMTHGHVOLTB | ControlLimitHigh | Voltage | B
| CTRLLMTHGHVOLTC | ControlLimitHigh | Voltage | C
| CTRLLMTHGHRELVOLTABC | ControlLimitHigh | RelativeVoltage | ABC
| CTRLLMTHGHRELVOLTA | ControlLimitHigh | RelativeVoltage | A
| CTRLLMTHGHRELVOLTB | ControlLimitHigh | RelativeVoltage | B
| CTRLLMTHGHRELVOLTC | ControlLimitHigh | RelativeVoltage | C
| CTRLLMTHGHAMPABC | ControlLimitHigh | Current | ABC
| CTRLLMTHGHAMPA | ControlLimitHigh | Current | A
| CTRLLMTHGHAMPB | ControlLimitHigh | Current | B
| CTRLLMTHGHAMPC | ControlLimitHigh | Current | C
| CTRLLMTHGHMWABC | ControlLimitHigh | ActivePower | ABC
| CTRLLMTHGHMWA | ControlLimitHigh | ActivePower | A
| CTRLLMTHGHMWB | ControlLimitHigh | ActivePower | B
| CTRLLMTHGHMWC | ControlLimitHigh | ActivePower | C
| CTRLLMTHGHMVAABC | ControlLimitHigh | ReactivePower | ABC
| CTRLLMTHGHMVAA | ControlLimitHigh | ReactivePower | A
| CTRLLMTHGHMVAB | ControlLimitHigh | ReactivePower | B
| CTRLLMTHGHMWAC | ControlLimitHigh | ReactivePower | C
| CTRLLMTHGHCOSPHIABC | ControlLimitHigh | CosPhi | ABC
| CTRLLMTHGHCOSPHIA | ControlLimitHigh | CosPhi | A
| CTRLLMTHGHCOSPHIB | ControlLimitHigh | CosPhi | B
| CTRLLMTHGHCOSPHIC | ControlLimitHigh | CosPhi | C
| CTRLLMTHGHTEMPABC | ControlLimitHigh | Temperature | ABC
| CTRLLMTHGHTEMPA | ControlLimitHigh | Temperature | A
| CTRLLMTHGHTEMPB | ControlLimitHigh | Temperature | B
| CTRLLMTHGHTEMPC | ControlLimitHigh | Temperature | C
| CTRLLMTLOWVOLTABC | ControlLimitLow | Voltage | ABC
| CTRLLMTLOWVOLTA | ControlLimitLow | Voltage | A
| CTRLLMTLOWVOLTB | ControlLimitLow | Voltage | B
| CTRLLMTLOWVOLTC | ControlLimitLow | Voltage | C
| CTRLLMTLOWRELVOLTABC | ControlLimitLow | RelativeVoltage | ABC
| CTRLLMTLOWRELVOLTA | ControlLimitLow | RelativeVoltage | A
| CTRLLMTLOWRELVOLTB | ControlLimitLow | RelativeVoltage | B
| CTRLLMTLOWRELVOLTC | ControlLimitLow | RelativeVoltage | C
| CTRLLMTLOWAMPABC | ControlLimitLow | Current | ABC
| CTRLLMTLOWAMPA | ControlLimitLow | Current | A
| CTRLLMTLOWAMPB | ControlLimitLow | Current | B
| CTRLLMTLOWAMPC | ControlLimitLow | Current | C
| CTRLLMTLOWMWABC | ControlLimitLow | ActivePower | ABC
| CTRLLMTLOWMWA | ControlLimitLow | ActivePower | A
| CTRLLMTLOWMWB | ControlLimitLow | ActivePower | B
| CTRLLMTLOWMWC | ControlLimitLow | ActivePower | C
| CTRLLMTLOWMVAABC | ControlLimitLow | ReactivePower | ABC
| CTRLLMTLOWMVAA | ControlLimitLow | ReactivePower | A
| CTRLLMTLOWMVAB | ControlLimitLow | ReactivePower | B
| CTRLLMTLOWMWAC | ControlLimitLow | ReactivePower | C
| CTRLLMTLOWCOSPHIABC | ControlLimitLow | CosPhi | ABC
| CTRLLMTLOWCOSPHIA | ControlLimitLow | CosPhi | A
| CTRLLMTLOWCOSPHIB | ControlLimitLow | CosPhi | B
| CTRLLMTLOWCOSPHIC | ControlLimitLow | CosPhi | C
| CTRLLMTLOWTEMPABC | ControlLimitLow | Temperature | ABC
| CTRLLMTLOWTEMPA | ControlLimitLow | Temperature | A
| CTRLLMTLOWTEMPB | ControlLimitLow | Temperature | B
| CTRLLMTLOWTEMPC | ControlLimitLow | Temperature | C
| CTRLSETVALVOLTABC | ControlSetValue | Voltage | ABC
| CTRLSETVALVOLTA | ControlSetValue | Voltage | A
| CTRLSETVALVOLTB | ControlSetValue | Voltage | B
| CTRLSETVALVOLTC | ControlSetValue | Voltage | C
| CTRLSETVALRELVOLTABC | ControlSetValue | RelativeVoltage | ABC
| CTRLSETVALRELVOLTA | ControlSetValue | RelativeVoltage | A
| CTRLSETVALRELVOLTB | ControlSetValue | RelativeVoltage | B
| CTRLSETVALRELVOLTC | ControlSetValue | RelativeVoltage | C
| CTRLSETVALAMPABC | ControlSetValue | Current | ABC
| CTRLSETVALAMPA | ControlSetValue | Current | A
| CTRLSETVALAMPB | ControlSetValue | Current | B
| CTRLSETVALAMPC | ControlSetValue | Current | C
| CTRLSETVALMWABC | ControlSetValue | ActivePower | ABC
| CTRLSETVALMWA | ControlSetValue | ActivePower | A
| CTRLSETVALMWB | ControlSetValue | ActivePower | B
| CTRLSETVALMWC | ControlSetValue | ActivePower | C
| CTRLSETVALMVARABC | ControlSetValue | ReactivePower | ABC
| CTRLSETVALMVARA | ControlSetValue | ReactivePower | A
| CTRLSETVALMVARB | ControlSetValue | ReactivePower | B
| CTRLSETVALMVARC | ControlSetValue | ReactivePower | C
| CTRLSETVALCOSPHIABC | ControlSetValue | CosPhi | ABC
| CTRLSETVALCOSPHIA | ControlSetValue | CosPhi | A
| CTRLSETVALCOSPHIB | ControlSetValue | CosPhi | B
| CTRLSETVALCOSPHIC | ControlSetValue | CosPhi | C
| CTRLSETVALIMPABC | ControlSetValue | Impedance | ABC
| CTRLSETVALIMPA | ControlSetValue | Impedance | A
| CTRLSETVALIMPB | ControlSetValue | Impedance | B
| CTRLSETVALIMPC | ControlSetValue | Impedance | C
| CTRLSETVALPCNTABC | ControlSetValue | Percent | ABC
| CTRLBDTHVOLTABC | ControlBandwidth | Voltage | ABC
| CTRLBDTHVOLTA | ControlBandwidth | Voltage | A
| CTRLBDTHVOLTB | ControlBandwidth | Voltage | B
| CTRLBDTHVOLTC | ControlBandwidth | Voltage | C
| CTRLBDTHRELVOLTABC | ControlBandwidth | RelativeVoltage | ABC
| CTRLBDTHRELVOLTA | ControlBandwidth | RelativeVoltage | A
| CTRLBDTHRELVOLTB | ControlBandwidth | RelativeVoltage | B
| CTRLBDTHRELVOLTC | ControlBandwidth | RelativeVoltage | C
| CTRLBDTHAMPABC | ControlBandwidth | Current | ABC
| CTRLBDTHAMPA | ControlBandwidth | Current | A
| CTRLBDTHAMPB | ControlBandwidth | Current | B
| CTRLBDTHAMPC | ControlBandwidth | Current | C
| CTRLBDTHMWABC | ControlBandwidth | ActivePower | ABC
| CTRLBDTHMWA | ControlBandwidth | ActivePower | A
| CTRLBDTHMWB | ControlBandwidth | ActivePower | B
| CTRLBDTHMWC | ControlBandwidth | ActivePower | C
| CTRLBDTHMVARABC | ControlBandwidth | ReactivePower | ABC
| CTRLBDTHMVARA | ControlBandwidth | ReactivePower | A
| CTRLBDTHMVARB | ControlBandwidth | ReactivePower | B
| CTRLBDTHMVARC | ControlBandwidth | ReactivePower | C
| CTRLBDTHCOSPHIABC | ControlBandwidth | CosPhi | ABC
| CTRLBDTHCOSPHIA | ControlBandwidth | CosPhi | A
| CTRLBDTHCOSPHIB | ControlBandwidth | CosPhi | B
| CTRLBDTHCOSPHIC | ControlBandwidth | CosPhi | C
| CTRLSUBDLYABC | ControlSubDelay | Time | ABC
| CTRLSUBDLYA | ControlSubDelay | Time | A
| CTRLSUBDLYB | ControlSubDelay | Time | B
| CTRLSUBDLYC | ControlSubDelay | Time | C
| CTRLSLPREUNTLSABC | ControlSlopeReal | Unitless | ABC
| CTRLSLPREUNTLSA | ControlSlopeReal | Unitless | A
| CTRLSLPREUNTLSB | ControlSlopeReal | Unitless | B
| CTRLSLPREUNTLSC | ControlSlopeReal | Unitless | C
| CTRLSLPREIMPABC | ControlSlopeReal | Impedance | ABC
| CTRLSLPREIMPA | ControlSlopeReal | Impedance | A
| CTRLSLPREIMPB | ControlSlopeReal | Impedance | B
| CTRLSLPREIMPC | ControlSlopeReal | Impedance | C
| CTRLSLPREPCNTABC | ControlSlopeReal | Percent | ABC
| CTRLSLPREPCNTA | ControlSlopeReal | Percent | A
| CTRLSLPREPCNTB | ControlSlopeReal | Percent | B
| CTRLSLPREPCNTC | ControlSlopeReal | Percent | C
| CTRLSLPRERELVOLTABC | ControlSlopeReal | RelativeVoltage | ABC
| CTRLSLPRERELVOLTA | ControlSlopeReal | RelativeVoltage | A
| CTRLSLPRERELVOLTB | ControlSlopeReal | RelativeVoltage | B
| CTRLSLPRERELVOLTC | ControlSlopeReal | RelativeVoltage | C
| CTRLSLPIMUNTLSABC | ControlSlopeImag | Unitless | ABC
| CTRLSLPIMUNTLSA | ControlSlopeImag | Unitless | A
| CTRLSLPIMUNTLSB | ControlSlopeImag | Unitless | B
| CTRLSLPIMUNTLSC | ControlSlopeImag | Unitless | C
| CTRLSLPIMIMPABC | ControlSlopeImag | Impedance | ABC
| CTRLSLPIMIMPA | ControlSlopeImag | Impedance | A
| CTRLSLPIMIMPB | ControlSlopeImag | Impedance | B
| CTRLSLPIMIMPC | ControlSlopeImag | Impedance | C
| CTRLSLPIMRELVOLTABC | ControlSlopeImag | RelativeVoltage | ABC
| CTRLSLPIMRELVOLTA | ControlSlopeImag | RelativeVoltage | A
| CTRLSLPIMRELVOLTB | ControlSlopeImag | RelativeVoltage | B
| CTRLSLPIMRELVOLTC | ControlSlopeImag | RelativeVoltage | C
| RELTRIPABC | RelayTrip | Status | ABC
| RELTRIPA | RelayTrip | Status | A
| RELTRIPB | RelayTrip | Status | B
| RELTRIPC | RelayTrip | Status | C
| RELTRIPN | RelayTrip | Status | N
| RECLENBLABC | ReclosingEnabled | Status | ABC
| RECLENBLA | ReclosingEnabled | Status | A
| RECLENBLB | ReclosingEnabled | Status | B
| RECLENBLC | ReclosingEnabled | Status | C
| RECLLCKTABC | RecloserLockout | Status | ABC
| RECLLCKTA | RecloserLockout | Status | A
| RECLLCKTB | RecloserLockout | Status | B
| RECLLCKTC | RecloserLockout | Status | C
| RECLDLYABC | RecloseDelay | Time | ABC
| RECLDLYA | RecloseDelay | Time | A
| RECLDLYB | RecloseDelay | Time | B
| RECLDLYC | RecloseDelay | Time | C
| UNFREQ | UnderFrequencyAlarm | Status | ABC
| FANSTABC | FanStatus | Status | ABC
| FANSTA | FanStatus | Status | A
| FANSTB | FanStatus | Status | B
| FANSTC | FanStatus | Status | C
| OILPUMPSTABC | OilPumpStatus | Status | ABC
| OILPUMPSTA | OilPumpStatus | Status | A
| OILPUMPSTB | OilPumpStatus | Status | B
| OILPUMPSTC | OilPumpStatus | Status | C
| OILTMP | MeasuredValue | OilTemperature | ABC
| HOTSPOTTMP | MeasuredValue | HotSpotTemperature | ABC
| OILTMPPRIM | MeasuredValue | OilTemperature | ABCPrimary
| HOTSPOTTMPPRIM | MeasuredValue | HotSpotTemperature | ABCPrimary
| OILTMPSEC | MeasuredValue | OilTemperature | ABCSecondary
| HOTSPOTTMPSEC | MeasuredValue | HotSpotTemperature | ABCSecondary
| AMPABCTERT | MeasuredValue | Current | ABCTertiary
| AMPATERT | MeasuredValue | Current | ATertiary
| AMPBTERT | MeasuredValue | Current | BTertiary
| AMPCTERT | MeasuredValue | Current | CTertiary
| AMPNTERT | MeasuredValue | Current | NTertiary
| MWABCTERT | MeasuredValue | ActivePower | ABCTertiary
| MWATERT | MeasuredValue | ActivePower | ATertiary
| MWBTERT | MeasuredValue | ActivePower | BTertiary
| MWCTERT | MeasuredValue | ActivePower | CTertiary
| MVARABCTERT | MeasuredValue | ReactivePower | ABCTertiary
| MVARATERT | MeasuredValue | ReactivePower | ATertiary
| MVARBTERT | MeasuredValue | ReactivePower | BTertiary
| MVARCTERT | MeasuredValue | ReactivePower | CTertiary
| MVAABCTERT | MeasuredValue | ApparentPower | ABCTertiary
| COSPHIABCTERT | MeasuredValue | CosPhi | ABCTertiary
| COSPHIATERT | MeasuredValue | CosPhi | ATertiary
| COSPHIBTERT | MeasuredValue | CosPhi | BTertiary
| COSPHICTERT | MeasuredValue | CosPhi | CTertiary
| MWHABCTERT | MeasuredValue | ActiveEnergy | ABCTertiary
| MWHATERT | MeasuredValue | ActiveEnergy | ATertiary
| MWHBTERT | MeasuredValue | ActiveEnergy | BTertiary
| MWHCTERT | MeasuredValue | ActiveEnergy | CTertiary
| MVARHABCTERT | MeasuredValue | ReactiveEnergy | ABCTertiary
| MVARHATERT | MeasuredValue | ReactiveEnergy | ATertiary
| MVARHBTERT | MeasuredValue | ReactiveEnergy | BTertiary
| MVARHCTERT | MeasuredValue | ReactiveEnergy | CTertiary
| OILTMPTERT | MeasuredValue | OilTemperature | ABCTertiary
| HOTSPOTTMPTERT | MeasuredValue | HotSpotTemperature | ABCTertiary
| TMPABCTERT | MeasuredValue | Temperature | ABCTertiary
| TMPATERT | MeasuredValue | Temperature | ATertiary
| TMPBTERT | MeasuredValue | Temperature | BTertiary
| TMPCTERT | MeasuredValue | Temperature | CTertiary
| CUSTANLM1ABCTERT | AnalogSignalType.Custom | Unitless | ABCTertiary
| CUSTANLM1ATERT | AnalogSignalType.Custom | Unitless | ATertiary
| CUSTANLM1BTERT | AnalogSignalType.Custom | Unitless | BTertiary
| CUSTANLM1CTERT | AnalogSignalType.Custom | Unitless | CTertiary
| CUSTANLM2ABCTERT | AnalogSignalType.Custom | Voltage | ABCTertiary
| CUSTANLM2ATERT | AnalogSignalType.Custom | Voltage | ATertiary
| CUSTANLM2BTERT | AnalogSignalType.Custom | Voltage | BTertiary
| CUSTANLM2CTERT | AnalogSignalType.Custom | Voltage | CTertiary
| CUSTANLM3ABCTERT | AnalogSignalType.Custom | Current | ABCTertiary
| CUSTANLM3ATERT | AnalogSignalType.Custom | Current | ATertiary
| CUSTANLM3BTERT | AnalogSignalType.Custom | Current | BTertiary
| CUSTANLM3CTERT | AnalogSignalType.Custom | Current | CTertiary
| CUSTANLM3NTERT | AnalogSignalType.Custom | Current | NTertiary
| CUSTANLM4ABCTERT | AnalogSignalType.Custom | ActivePower | ABCTertiary
| CUSTANLM4ATERT | AnalogSignalType.Custom | ActivePower | ATertiary
| CUSTANLM4BTERT | AnalogSignalType.Custom | ActivePower | BTertiary
| CUSTANLM4CTERT | AnalogSignalType.Custom | ActivePower | CTertiary
| CUSTANLM5ABCTERT | AnalogSignalType.Custom | ReactivePower | ABCTertiary
| CUSTANLM5ATERT | AnalogSignalType.Custom | ReactivePower | ATertiary
| CUSTANLM5BTERT | AnalogSignalType.Custom | ReactivePower | BTertiary
| CUSTANLM5CTERT | AnalogSignalType.Custom | ReactivePower | CTertiary
| CUSTANLM6ABCTERT | AnalogSignalType.Custom | Frequency | ABCTertiary
| CUSTANLM6ATERT | AnalogSignalType.Custom | Frequency | ATertiary
| CUSTANLM6BTERT | AnalogSignalType.Custom | Frequency | BTertiary
| CUSTANLM6CTERT | AnalogSignalType.Custom | Frequency | CTertiary
| CUSTANLM7ABCTERT | AnalogSignalType.Custom | Temperature | ABCTertiary
| CUSTANLM7ATERT | AnalogSignalType.Custom | Temperature | ATertiary
| CUSTANLM7BTERT | AnalogSignalType.Custom | Temperature | BTertiary
| CUSTANLM7CTERT | AnalogSignalType.Custom | Temperature | CTertiary
| CUSTANLM8ABCTERT | AnalogSignalType.Custom | ActiveEnergy | ABCTertiary
| CUSTANLM8ATERT | AnalogSignalType.Custom | ActiveEnergy | ATertiary
| CUSTANLM8BTERT | AnalogSignalType.Custom | ActiveEnergy | BTertiary
| CUSTANLM8CTERT | AnalogSignalType.Custom | ActiveEnergy | CTertiary
| CUSTANLM9ABCTERT | AnalogSignalType.Custom | ReactiveEnergy | ABCTertiary
| CUSTANLM9ATERT | AnalogSignalType.Custom | ReactiveEnergy | ATertiary
| CUSTANLM9BTERT | AnalogSignalType.Custom | ReactiveEnergy | BTertiary
| CUSTANLM9CTERT | AnalogSignalType.Custom | ReactiveEnergy | CTertiary
| CUSTANLM10ABCTERT | AnalogSignalType.Custom | ApparentPower | ABCTertiary
| CUSTANLM10ATERT | AnalogSignalType.Custom | ApparentPower | ATertiary
| CUSTANLM10BTERT | AnalogSignalType.Custom | ApparentPower | BTertiary
| CUSTANLM10CTERT | AnalogSignalType.Custom | ApparentPower | CTertiary
| CUSTANLM11ABCTERT | AnalogSignalType.Custom | VoltageAngle | ABCTertiary
| CUSTANLM11ATERT | AnalogSignalType.Custom | VoltageAngle | ATertiary
| CUSTANLM11BTERT | AnalogSignalType.Custom | VoltageAngle | BTertiary
| CUSTANLM11CTERT | AnalogSignalType.Custom | VoltageAngle | CTertiary
| CUSTANLM12ABCTERT | AnalogSignalType.Custom | Time | ABCTertiary
| CUSTANLM12ATERT | AnalogSignalType.Custom | Time | ATertiary
| CUSTANLM12BTERT | AnalogSignalType.Custom | Time | BTertiary
| CUSTANLM12CTERT | AnalogSignalType.Custom | Time | CTertiary
| CUSTANLM13ABCTERT | AnalogSignalType.Custom | Humidity | ABCTertiary
| CUSTANLM13ATERT | AnalogSignalType.Custom | Humidity | ATertiary
| CUSTANLM13BTERT | AnalogSignalType.Custom | Humidity | BTertiary
| CUSTANLM13CTERT | AnalogSignalType.Custom | Humidity | CTertiary
| CUSTANLM14ABCTERT | AnalogSignalType.Custom | WindSpeed | ABCTertiary
| CUSTANLM14ATERT | AnalogSignalType.Custom | WindSpeed | ATertiary
| CUSTANLM14BTERT | AnalogSignalType.Custom | WindSpeed | BTertiary
| CUSTANLM14CTERT | AnalogSignalType.Custom | WindSpeed | CTertiary
| CUSTANLM15ABCTERT | AnalogSignalType.Custom | FeelsLike | ABCTertiary
| CUSTANLM15ATERT | AnalogSignalType.Custom | FeelsLike | ATertiary
| CUSTANLM15BTERT | AnalogSignalType.Custom | FeelsLike | BTertiary
| CUSTANLM15CTERT | AnalogSignalType.Custom | FeelsLike | CTertiary
| CUSTANLM16ABCTERT | AnalogSignalType.Custom | SunshineMinutes | ABCTertiary
| CUSTANLM16ATERT | AnalogSignalType.Custom | SunshineMinutes | ATertiary
| CUSTANLM16BTERT | AnalogSignalType.Custom | SunshineMinutes | BTertiary
| CUSTANLM16CTERT | AnalogSignalType.Custom | SunshineMinutes | CTertiary
| CUSTANLM17ABCTERT | AnalogSignalType.Custom | SkyCover | ABCTertiary
| CUSTANLM17ATERT | AnalogSignalType.Custom | SkyCover | ATertiary
| CUSTANLM17BTERT | AnalogSignalType.Custom | SkyCover | BTertiary
| CUSTANLM17CTERT | AnalogSignalType.Custom | SkyCover | CTertiary
| CUSTANLM18ABCTERT | AnalogSignalType.Custom | Length | ABCTertiary
| CUSTANLM18ATERT | AnalogSignalType.Custom | Length | ATertiary
| CUSTANLM18BTERT | AnalogSignalType.Custom | Length | BTertiary
| CUSTANLM18CTERT | AnalogSignalType.Custom | Length | CTertiary
| CUSTANLM19ABCTERT | AnalogSignalType.Custom | CrossSection | ABCTertiary
| CUSTANLM19ATERT | AnalogSignalType.Custom | CrossSection | ATertiary
| CUSTANLM19BTERT | AnalogSignalType.Custom | CrossSection | BTertiary
| CUSTANLM19CTERT | AnalogSignalType.Custom | CrossSection | CTertiary
| CUSTANLM20ABCTERT | AnalogSignalType.Custom | Impedance | ABCTertiary
| CUSTANLM20ATERT | AnalogSignalType.Custom | Impedance | ATertiary
| CUSTANLM20BTERT | AnalogSignalType.Custom | Impedance | BTertiary
| CUSTANLM20CTERT | AnalogSignalType.Custom | Impedance | CTertiary
| CUSTANLM21ABCTERT | AnalogSignalType.Custom | Admittance | ABCTertiary
| CUSTANLM21ATERT | AnalogSignalType.Custom | Admittance | ATertiary
| CUSTANLM21BTERT | AnalogSignalType.Custom | Admittance | BTertiary
| CUSTANLM21CTERT | AnalogSignalType.Custom | Admittance | CTertiary
| CUSTANLM22ABCTERT | AnalogSignalType.Custom | ImpedancePerLength | ABCTertiary
| CUSTANLM22ATERT | AnalogSignalType.Custom | ImpedancePerLength | ATertiary
| CUSTANLM22BTERT | AnalogSignalType.Custom | ImpedancePerLength | BTertiary
| CUSTANLM22CTERT | AnalogSignalType.Custom | ImpedancePerLength | CTertiary
| CUSTANLM23ABCTERT | AnalogSignalType.Custom | AdmittancePerLength | ABCTertiary
| CUSTANLM23ATERT | AnalogSignalType.Custom | AdmittancePerLength | ATertiary
| CUSTANLM23BTERT | AnalogSignalType.Custom | AdmittancePerLength | BTertiary
| CUSTANLM23CTERT | AnalogSignalType.Custom | AdmittancePerLength | CTertiary
| CUSTANLM24ABCTERT | AnalogSignalType.Custom | Percent | ABCTertiary
| CUSTANLM24ATERT | AnalogSignalType.Custom | Percent | ATertiary
| CUSTANLM24BTERT | AnalogSignalType.Custom | Percent | BTertiary
| CUSTANLM24CTERT | AnalogSignalType.Custom | Percent | CTertiary
| CUSTANLM25ABCTERT | AnalogSignalType.Custom | Money | ABCTertiary
| CUSTANLM25ATERT | AnalogSignalType.Custom | Money | ATertiary
| CUSTANLM25BTERT | AnalogSignalType.Custom | Money | BTertiary
| CUSTANLM25CTERT | AnalogSignalType.Custom | Money | CTertiary
| CUSTANLM26ABCTERT | AnalogSignalType.Custom | RelativeVoltage | ABCTertiary
| CUSTANLM26ATERT | AnalogSignalType.Custom | RelativeVoltage | ATertiary
| CUSTANLM26BTERT | AnalogSignalType.Custom | RelativeVoltage | BTertiary
| CUSTANLM26CTERT | AnalogSignalType.Custom | RelativeVoltage | CTertiary
| CUSTANLM27ABCTERT | AnalogSignalType.Custom | Insolation | ABCTertiary
| CUSTANLM27ATERT | AnalogSignalType.Custom | Insolation | ATertiary
| CUSTANLM27BTERT | AnalogSignalType.Custom | Insolation | BTertiary
| CUSTANLM27CTERT | AnalogSignalType.Custom | Insolation | CTertiary
| CUSTANLM28ABCTERT | AnalogSignalType.Custom | CurrentAngle | ABCTertiary
| CUSTANLM28ATERT | AnalogSignalType.Custom | CurrentAngle | ATertiary
| CUSTANLM28BTERT | AnalogSignalType.Custom | CurrentAngle | BTertiary
| CUSTANLM28CTERT | AnalogSignalType.Custom | CurrentAngle | CTertiary
| CUSTANLM29ABCTERT | AnalogSignalType.Custom | RotationSpeed | ABCTertiary
| CUSTANLM29ATERT | AnalogSignalType.Custom | RotationSpeed | ATertiary
| CUSTANLM29BTERT | AnalogSignalType.Custom | RotationSpeed | BTertiary
| CUSTANLM29CTERT | AnalogSignalType.Custom | RotationSpeed | CTertiary
| CUSTANLM30ABCTERT | AnalogSignalType.Custom | Mass | ABCTertiary
| CUSTANLM30ATERT | AnalogSignalType.Custom | Mass | ATertiary
| CUSTANLM30BTERT | AnalogSignalType.Custom | Mass | BTertiary
| CUSTANLM30CTERT | AnalogSignalType.Custom | Mass | CTertiary
| CUSTANLM31ABCTERT | AnalogSignalType.Custom | FailureRate | ABCTertiary
| CUSTANLM31ATERT | AnalogSignalType.Custom | FailureRate | ATertiary
| CUSTANLM31BTERT | AnalogSignalType.Custom | FailureRate | BTertiary
| CUSTANLM31CTERT | AnalogSignalType.Custom | FailureRate | CTertiary
| CUSTANLM32ABCTERT | AnalogSignalType.Custom | SoilTemperature | ABCTertiary
| CUSTANLM32ATERT | AnalogSignalType.Custom | SoilTemperature | ATertiary
| CUSTANLM32BTERT | AnalogSignalType.Custom | SoilTemperature | BTertiary
| CUSTANLM32CTERT | AnalogSignalType.Custom | SoilTemperature | CTertiary
| CUSTANLM33ABCTERT | AnalogSignalType.Custom | OilTemperature | ABCTertiary
| CUSTANLM33ATERT | AnalogSignalType.Custom | OilTemperature | ATertiary
| CUSTANLM33BTERT | AnalogSignalType.Custom | OilTemperature | BTertiary
| CUSTANLM33CTERT | AnalogSignalType.Custom | OilTemperature | CTertiary
| CUSTANLM34ABCTERT | AnalogSignalType.Custom | HotSpotTemperature | ABCTertiary
| CUSTANLM34ATERT | AnalogSignalType.Custom | HotSpotTemperature | ATertiary
| CUSTANLM34BTERT | AnalogSignalType.Custom | HotSpotTemperature | BTertiary
| CUSTANLM34CTERT | AnalogSignalType.Custom | HotSpotTemperature | CTertiary
| CUSTANLM35ABCTERT | AnalogSignalType.Custom | AbsoluteDateTime | ABCTertiary
| CUSTANLM35ATERT | AnalogSignalType.Custom | AbsoluteDateTime | ATertiary
| CUSTANLM35BTERT | AnalogSignalType.Custom | AbsoluteDateTime | BTertiary
| CUSTANLM35CTERT | AnalogSignalType.Custom | AbsoluteDateTime | CTertiary
| CUSTANLM36ABCTERT | AnalogSignalType.Custom | LatLong | ABCTertiary
| CUSTANLM36ATERT | AnalogSignalType.Custom | LatLong | ATertiary
| CUSTANLM36BTERT | AnalogSignalType.Custom | LatLong | BTertiary
| CUSTANLM36CTERT | AnalogSignalType.Custom | LatLong | CTertiary
| SOURCESTABC | SourceStatus | Status | ABC
| SOURCESTA | SourceStatus | Status | A
| SOURCESTB | SourceStatus | Status | B
| SOURCESTC | SourceStatus | Status | C
| FLTAMPSUB | FaultCurrentSub | Current | ABC
| FLTANGSUB | FaultAngleSub | CurrentAngle | ABC
| FLTAMPTRANS | FaultCurrentTrans | Current | ABC
| FLTANGTRANS | FaultAngleTrans | CurrentAngle | ABC
| BLWTRAMPABC | BellwetherMeter | Current | ABC
| BLWTRAMPA | BellwetherMeter | Current | A
| BLWTRAMPB | BellwetherMeter | Current | B
| BLWTRAMPC | BellwetherMeter | Current | C
| BLWTRMWABC | BellwetherMeter | ActivePower | ABC
| BLWTRMWA | BellwetherMeter | ActivePower | A
| BLWTRMWB | BellwetherMeter | ActivePower | B
| BLWTRMWC | BellwetherMeter | ActivePower | C
| BLWTRMVARABC | BellwetherMeter | ActivePower | ABC
| BLWTRMVARA | BellwetherMeter | ActivePower | A
| BLWTRMVARB | BellwetherMeter | ActivePower | B
| BLWTRMVARC | BellwetherMeter | ActivePower | C
| BLWTRMVAABC | BellwetherMeter | ApparentPower | ABC
| BLWTRMVAA | BellwetherMeter | ApparentPower | A
| BLWTRMVAB | BellwetherMeter | ApparentPower | B
| BLWTRMVAC | BellwetherMeter | ApparentPower | C
| BLWTRCOSPHIABC | BellwetherMeter | CosPhi | ABC
| BLWTRCOSPHIA | BellwetherMeter | CosPhi | A
| BLWTRCOSPHIB | BellwetherMeter | CosPhi | B
| BLWTRCOSPHIC | BellwetherMeter | CosPhi | C
| BLWTRMWHABC | BellwetherMeter | ActiveEnergy | ABC
| BLWTRMWHA | BellwetherMeter | ActiveEnergy | A
| BLWTRMWHB | BellwetherMeter | ActiveEnergy | B
| BLWTRMWHC | BellwetherMeter | ActiveEnergy | C
| BLWTRMVARHABC | BellwetherMeter | ReactiveEnergy | ABC
| BLWTRMVARHA | BellwetherMeter | ReactiveEnergy | A
| BLWTRMVARHB | BellwetherMeter | ReactiveEnergy | B
| BLWTRMVARHC | BellwetherMeter | ReactiveEnergy | C
| BLWTRVOLTABC | BellwetherMeter | Voltage | ABC
| BLWTRVOLTAB | BellwetherMeter | Voltage | AB
| BLWTRVOLTBC | BellwetherMeter | Voltage | BC
| BLWTRVOLTAC | BellwetherMeter | Voltage | AC
| BLWTRVOLTA | BellwetherMeter | Voltage | A
| BLWTRVOLTB | BellwetherMeter | Voltage | B
| BLWTRVOLTC | BellwetherMeter | Voltage | C
| BLWTRVOLTANGABC | BellwetherMeter | VoltageAngle | ABC
| BLWTRVOLTANGAB | BellwetherMeter | VoltageAngle | AB
| BLWTRVOLTANGBC | BellwetherMeter | VoltageAngle | BC
| BLWTRVOLTANGAC | BellwetherMeter | VoltageAngle | AC
| BLWTRVOLTANGA | BellwetherMeter | VoltageAngle | A
| BLWTRVOLTANGB | BellwetherMeter | VoltageAngle | B
| BLWTRVOLTANGC | BellwetherMeter | VoltageAngle | C
| BLWTRFREQ | BellwetherMeter | Frequency | ABC
| BLWTRRELVOLTABC | BellwetherMeter | RelativeVoltage | ABC
| BLWTRRELVOLTAB | BellwetherMeter | RelativeVoltage | AB
| BLWTRRELVOLTBC | BellwetherMeter | RelativeVoltage | BC
| BLWTRRELVOLTAC | BellwetherMeter | RelativeVoltage | AC
| BLWTRRELVOLTA | BellwetherMeter | RelativeVoltage | A
| BLWTRRELVOLTB | BellwetherMeter | RelativeVoltage | B
| BLWTRRELVOLTC | BellwetherMeter | RelativeVoltage | C
| BLWTRTMP | BellwetherMeter | Temperature | ABC
| BLWTROILTMP | BellwetherMeter | OilTemperature | ABC
| BLWTRHOTSPOTTMP | BellwetherMeter | HotSpotTemperature | ABC
| WTHRDATATEMP | WeatherData | Temperature | ABC
| WTHRDATAHMDT | WeatherData | Humidity | ABC
| WTHRDATAWNDSPD | WeatherData | WindSpeed | ABC
| WTHRDATAFLSLK | WeatherData | FeelsLike | ABC
| WTHRDATASUNMIN | WeatherData | SunshineMinutes | ABC
| WTHRDATASKYCOV | WeatherData | SkyCover | ABC
| WTHRDATAINSL | WeatherData | Insolation | ABC
| WTHRDATASLTEMP | WeatherData | SoilTemperature | ABC

## Message Mapping
Name | Alias | State (Message) | Value | SCADA Value | Commanding message | Color | Abnormal Status | Allow Manual Override | Alarm Catalog | Coluna1 | Severidade
DI_null@null___NORMAL@ATUADO___RelayTrip___INV_S_TS_SEV1 |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Abnormal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SEV1 | Alarme de Estado em Ponto Telessinalizado SEV1
DI_null@null___NORMAL@ATUADO___Custom_S_TS_SEV1 |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Abnormal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SEV1 | Alarme de Estado em Ponto Telessinalizado SEV1
DI_null@null___NORMAL@ATUADO___RelayTrip_S_TS_SEV1 |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Abnormal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SEV1 | Alarme de Estado em Ponto Telessinalizado SEV1
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_DS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
LIGAR@null___DESLIGADO@LIGADO___SwitchStatus_D_TC |  | Error;DESLIGADO;LIGADO;Transit | 0;1;2;3 | 1;0;2;3 | ;LIGAR;null; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Abnormal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_DS_AUTO |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_DS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
ABRIR@null___ABERTO@FECHADO___SwitchStatus_D_TC |  | Error;ABERTO;FECHADO;Transit | 0;1;2;3 | 1;0;2;3 | ;ABRIR;null; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_DS_SGF_DESAB |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
LIGAR@null___DESLIGADO@LIGADO___Custom_S_TC |  | Error;DESLIGADO;LIGADO;Transit | 0;1;2;3 | 1;0;2;3 | ;LIGAR;null; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_DS_SGF_INC |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
null@REARMAR___NORMAL@ATUADO___Custom_S_TC |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;REARMAR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV___admsINV_S_TC_DS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV___admsINV_S_TC_DS_SGF_DESAB |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
DESATIVA@ATIVA___DESATIVADO@ATIVADO___Custom_S_TC |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESATIVA;ATIVA; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DESATIVA@null___DESATIVADO@ATIVADO___Custom_S_TC |  | Error;DESATIVADO;ATIVADO;Transit | 0;1;2;3 | 1;0;2;3 | ;DESATIVA;null; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV___admsINV_S_TC_DS_SGF_INC |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
null@null___NORMAL@ATUADO___Custom_S_TC |  | Error;NORMAL;ATUADO;Transit | 0;1;2;3 | 1;0;2;3 | ;null;null; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
@null___DESATIVADO@ATIVADO___Custom_S_TC |  | Error;DESATIVADO;ATIVADO;Transit | 0;1;2;3 | 1;0;2;3 | ;;null; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
LIGAR@DESLIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;1;2;3 | ;LIGAR;DESLIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 0;1;2;3 | ;ABRIR;FECHAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
LIGAR@DESLIGAR___DESLIGADO@LIGADO___Custom_S_TC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;LIGAR;DESLIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV___admsINV_S_TS_DS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;1;0;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DS | Alarme de Estado em Ponto Telessinalizado DS
DIMINUIR@AUMENTAR___null@null___TapIncrement_S_TC |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;DIMINUIR;AUMENTAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
RELIGADOR@null___NORMAL DESATIVAD@NORMAL ATIVADO___Custom___admsINV_S_TC |  | Error;NORMAL DESATIVAD;NORMAL ATIVADO;Transit | 0;2;1;3 | 2;0;1;3 | ;RELIGADOR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
LIGAR@DESLIGAR___DESLIGADO@LIGADO___SwitchStatus___INV_S_TC |  | Error;DESLIGADO;LIGADO;Transit | 0;1;2;3 | 2;1;0;3 | ;LIGAR;DESLIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
@null___REMOTO@LOCAL___Custom___INV_S_TC |  | Error;REMOTO;LOCAL;Transit | 0;1;2;3 | 1;2;0;3 | ;;null; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
LIGAR@DESLIGAR___DESLIGADO@LIGADO___SwitchStatus_S_TC |  | Error;DESLIGADO;LIGADO;Transit | 0;1;2;3 | 2;0;1;3 | ;LIGAR;DESLIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_S_TC_ELETROSUL |  | Transit;ABERTO;FECHADO;Erro | 0;1;2;3 | 1;0;3;2 | ;ABRIR;FECHAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | TRUE;TRUE;TRUE;TRUE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DESATIVA@ATIVA___DESATIVADO@ATIVADO___Custom___INV_S_TC |  | Error;DESATIVADO;ATIVADO;Transit | 0;1;2;3 | 2;1;0;3 | ;DESATIVA;ATIVA; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
@null___REMOTO@LOCAL___Custom_S_TC |  | Error;REMOTO;LOCAL;Transit | 0;1;2;3 | 1;0;2;3 | ;;null; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
MESTRE@INDIVIDUAL@COMANDO___MESTRE@INDIVIDUAL@COMANDO___Custom___admsINV_D_TC |  | MESTRE;COMANDADO;INDIVIDUAL; | 0;1;2;3 | 0;1;2;3 | MESTRE;;INDIVIDUAL; | #FF00FF00;#FF00FF00;#FF00FF00;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado
null@ATIV_DES___DESATIVADO@ATIVADO___Custom_S_TC |  | Error;DESATIVADO;ATIVADO;Transit | 0;1;2;3 | 1;0;2;3 | ;null;ATIV_DES; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DIMINUIR@AUMENTAR___@___TapIncrement_S_TC |  | Transit;null;null;Error | 0;1;2;3 | 2;0;1;3 | ;DIMINUIR;AUMENTAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
null@MESTRE___DESATIVADO@ATIVADO___CustomCR_S_TC |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;INDIVIDUAL; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado
null@INDIVIDUAL___DESATIVADO@ATIVADO___Custom_S_TC |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;INDIVIDUAL; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
CMD_COS@null___REMOTO@LOCAL___Custom___INV_D_TC_SS |  | Transit;REMOTO;LOCAL;Error | 0;2;1;3 | 0;2;1;3 | ;CMD_COS;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Abnormal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
LIGAR@DESLIGAR___DESLIGADO@LIGADO___Custom___INV_S_TC |  | Error;DESLIGADO;LIGADO;Transit | 0;1;2;3 | 2;1;0;3 | ;LIGAR;DESLIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
RELIGAD@ALTERNATIVO___@___Custom_S_TC |  | Error;null;null;Transit | 0;1;2;3 | 2;0;1;3 | ;RELIGAD;ALTERNATIVO; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
null@null___DESATIVADO@ATIVADO___Custom_S_TC |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
null@null___DESATIVADO@ATIVADO___Custom___INV_S_TC |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
RELIGADOR@null___NORMAL DESATIVAD@NORMAL ATIVADO___Custom___INV___admsINV_S_TC |  | Error;NORMAL DESATIVAD;NORMAL ATIVADO;Transit | 0;2;1;3 | 2;1;0;3 | ;RELIGADOR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
RELIGADOR@ALTERNATIVO___NORMAL@ALTERNATIVO___Custom_S_TC |  | Error;NORMAL;ALTERNATIVO;Transit | 0;1;2;3 | 2;0;1;3 | ;RELIGADOR;ALTERNATIVO; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
CMD_RGE@null___CEEE@RGE___Custom___INV___admsINV_S_TC |  | Error;CEEE;RGE;Transit | 0;2;1;3 | 2;1;0;3 | ;CMD_RGE;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
MESTRE@INDIVIDUAL@COMANDO___MESTRE@INDIVIDUAL@COMANDO___Parallel___admsINV_D_TC |  | MESTRE;INDIVIDUAL;COMANDADO; | 0;1;2;3 | 0;1;2;3 | MESTRE;INDIVIDUAL;COMANDO; | #FF00FF00;#FF00FF00;#FF00FF00;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
null@MESTRE___null@MESTRE___Custom_S_TC_scd |  | Error;;MESTRE;Transit | 0;1;2;3 | 2;0;1;3 | ;;MESTRE; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
null@INDIVIDUAL___null@INDIVIDUAL___Custom_S_TC |  | Error;INATIVO;COMANDADO;Transit | 0;1;2;3 | 2;0;1;3 | ;;INDIVIDUAL; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
null@COMANDADO___MESTRE@COMANDADO___Custom_S_TC |  | Error;MESTRE;COMANDADO;Transit | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
CMD_COS@null___REMOTO@LOCAL___Custom___INV_D_TS_SS |  | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV___admsINV_S_TS_DS_SGF_DESAB |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;1;0;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DS | Alarme de Estado em Ponto Telessinalizado DS
REARMAR@BLOQUEAR___NORMAL@ATUADO___Custom_S_TC |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;REARMAR;BLOQUEAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
RELIGADOR@ALTERNATIVO@CHAVE___RELIGADOR@ALTERNATIVO@CHAVE___Custom_S_TC |  | RELIGADOR;ALTERNATIVO;CHAVE; | 0;1;2;3 | 0;1;2;3 | RELIGADOR;ALTERNATIVO;CHAVE; | #FF00FF00;#FF00FF00;#FF00FF00;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV___admsINV_S_TS_DS_SGF_INC |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;1;0;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DS | Alarme de Estado em Ponto Telessinalizado DS
RELIGAD@ALTERNATIVO___null@null___Custom_D_TC |  | Error;null;null;Transit | 0;1;2;3 | 1;0;2;3 | ;RELIGAD;ALTERNATIVO; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
RELIGAD@ALTERNATIVO___null@null___Custom_S_TC |  | Error;null;null;Transit | 0;1;2;3 | 1;0;2;3 | ;RELIGAD;ALTERNATIVO; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
RELIGAD@ALTERNATIVO___@___Custom_D_TC |  | Error;;;Transit | 0;1;2;3 | 2;0;1;3 | ;RELIGAD;ALTERNATIVO; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
MANUAL@AUTOMATICO___AUTOMATICO@MANUAL___Custom___INV_S_TC |  | Error;AUTOMATICO;MANUAL;Transit | 0;1;2;3 | 2;1;0;3 | ;MANUAL;AUTOMATICO; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
G2@G1___GRUPO 1@GRUPO 2___Custom_S_TC |  | Error;GRUPO 1;GRUPO 2;Transit | 0;1;2;3 | 2;0;1;3 | ;G2;G1; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
MANUAL@AUTOMATICO___AUTOMATICO@MANUAL___Custom_D_TC |  | Error;AUTOMATICO;MANUAL;Transit | 0;1;2;3 | 2;0;1;3 | ;MANUAL;AUTOMATICO; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus___INV_S_TC |  | Error;ABERTO;FECHADO;Transit | 0;1;2;3 | 2;1;0;3 | ;ABRIR;FECHAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DI_DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus___SINV_D_TC_E2 |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;2;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Abnormal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado E2 | Alarme de Estado em Ponto Telecontrolado E2
null@null___DESLIGADO@LIGADO___Custom_S_TS_SE |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SE | Alarme de Estado em Ponto Telessinalizado SE
DI_DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus___INV_D_TC_E2 |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;2;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado E2 | Alarme de Estado em Ponto Telecontrolado E2
ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SE |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 0;1;2;3 | ;ABRIR;FECHAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SE | Alarme de Estado em Ponto Telecontrolado SE
null@INDIVIDUAL___COMANDADO@INDIVIDUAL___Custom_S_TC |  | Error;INATIVO;COMANDADO;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
MESTRE@INDIVIDUAL@COMANDO___MESTRE@INDIVIDUAL@COMANDO___Custom_S_TC |  | MESTRE;INDIVIDUAL;COMANDADO; | 0;1;2;3 | 0;1;2;3 | MESTRE;INDIVIDUAL;COMANDO; | #FF00FF00;#FF00FF00;#FF00FF00;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
MESTRE@INDIVIDUAL@COMANDO___MESTRE@INDIVIDUAL@COMANDO___Parallel___admsINV_D_TC_SS |  | MESTRE;INDIVIDUAL;COMANDADO; | 2;0;1;3 | 0;2;1;3 | MESTRE;INDIVIDUAL;COMANDO; | #FFFF0000;#FF00FF00;#FF00FF00;#FF000000 | Normal;Abnormal;Abnormal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV_S_TC |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
RELIGADOR@null___NORMAL DESATIVAD@NORMAL ATIVADO___Custom_S_TC |  | Error;NORMAL DESATIVAD;NORMAL ATIVADO;Transit | 0;1;2;3 | 2;0;1;3 | ;RELIGADOR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus___INV_S_TC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;1;0;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
RELIGADOR@ALTERNATIVO___@___Custom_S_TC |  | Transit;null;null;Error | 0;1;2;3 | 2;0;1;3 | ;RELIGADOR;ALTERNATIVO; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
CMD_COS@null___REMOTO@LOCAL___Custom___INV_S_TC |  | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;1;0;3 | ;CMD_COS;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus___INV_D_TC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;2;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Abnormal;Abnormal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;1;2;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
CMD_COS@null___REMOTO@LOCAL___Custom___INV_S_TC_SS |  | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;1;0;3 | ;CMD_COS;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
ATIVAR@DESATIVAR___ATIVADO@DESATIVADO___Custom___INV_S_TC_SS |  | Transit;ATIVADO;DESATIVADO;Error | 0;1;2;3 | 2;1;0;3 | ;ATIVAR;DESATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_D_TC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Abnormal;Abnormal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_S_TC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV_S_TC_DS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom___INV_S_TC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;1;0;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
G1@G2___GRUPO 1@GRUPO 2___Custom_S_TC |  | Transit;GRUPO 1;GRUPO 2;Error | 0;1;2;3 | 2;0;1;3 | ;G1;G2; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
null@RELIGADOR___NORMAL DESATIVAD@NORMAL ATIVADO___Custom_S_TC |  | Transit;NORMAL DESATIVAD;NORMAL ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;RELIGADOR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
null@null@null___ALTERNATIVO@NORMAL@CHAVE___Custom_D_TS_SS |  | ALTERNATIVO;NORMAL;CHAVE; | 0;1;2;3 | 0;1;2;3 | ;;; | #FFFF0000;#FF00FF00;#FF00FF00;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado
TROCA@null___NORMAL@ALTERNATIVO___Custom_S_TC |  | Transit;NORMAL;ALTERNATIVO;Error | 0;1;2;3 | 2;0;1;3 | ;TROCA;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
null@RELIGADOR___NORMAL DESATIVAD@NORMAL ATIVADO___Custom___INV_S_TC |  | Transit;NORMAL DESATIVAD;NORMAL ATIVADO;Error | 0;1;2;3 | 2;1;0;3 | ;;RELIGADOR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
RELIGADOR@ALTERNATIVO___null@null___Custom_S_TC |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;RELIGADOR;ALTERNATIVO; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom___INV_S_TC |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;1;0;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
CMD_RGE@null___CEEE@RGE___Custom___INV_S_TC |  | Transit;CEEE;RGE;Error | 0;1;2;3 | 2;1;0;3 | ;CMD_RGE;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV_S_TS_DS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DS | Alarme de Estado em Ponto Telessinalizado DS
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DI_DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_S_TC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DI_DESBLOQUEAR@null___NORMAL@BLOQUEADA___Enabled___INV_S_TC |  | Transit;NORMAL;BLOQUEADA;Error | 0;1;2;3 | 2;1;0;3 | ;DESBLOQUEAR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DI_ATIVAR@null___ATIVADO@DESATIVADO___Custom_S_TC |  | Transit;ATIVADO;DESATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;ATIVAR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DI_DESBLOQUEAR@BLOQUEAR___NORMAL@BLOQUEADA___Enabled___INV_S_TC |  | Transit;NORMAL;BLOQUEADA;Error | 0;1;2;3 | 2;1;0;3 | ;DESBLOQUEAR;BLOQUEAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_DS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_DS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
DI_RESETAR@null___null@null___Custom_S_TC |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;RESETAR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_DS_MANOBRA |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;1;2;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;TRUE | Alarme de Estado em Ponto Telecontrolado SE | Alarme de Estado em Ponto Telecontrolado SE
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_S_TC_SE |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SE | Alarme de Estado em Ponto Telecontrolado SE
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_S_TS_SE |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SE | Alarme de Estado em Ponto Telessinalizado SE
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus___INV_D_TC_SE |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;2;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SE | Alarme de Estado em Ponto Telecontrolado SE
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus___INV_S_TC_SE |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;1;0;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SE | Alarme de Estado em Ponto Telecontrolado SE
DI_DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_E2 |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;1;2;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado E2 | Alarme de Estado em Ponto Telecontrolado E2
DI_DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_D_TC_E2 |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado E2 | Alarme de Estado em Ponto Telecontrolado E2
DI_DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_S_TC_E2 |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado E2 | Alarme de Estado em Ponto Telecontrolado E2
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TS_SE |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;1;2;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SE | Alarme de Estado em Ponto Telessinalizado SE
ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TS_SE |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 0;1;2;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Abnormal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SE | Alarme de Estado em Ponto Telessinalizado SE
null@null___NORMAL@FALTA___Custom___INV_S_TS_SE |  | Transit;NORMAL;FALTA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SE | Alarme de Estado em Ponto Telessinalizado SE
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus___INV_D_TS_SE |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;2;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SE | Alarme de Estado em Ponto Telessinalizado SE
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_S_TS_ST |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado ST | Alarme de Estado em Ponto Telessinalizado ST
DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom___INV_S_TS_SE |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SE | Alarme de Estado em Ponto Telessinalizado SE
null@null___NORMAL@ATUADO___Custom_S_TS_SE |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SE | Alarme de Estado em Ponto Telessinalizado SE
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus___INV_S_TS_SE |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SE | Alarme de Estado em Ponto Telessinalizado SE
null@null___NORMAL@ATUADO___Custom___INV_S_TS_SE |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SE | Alarme de Estado em Ponto Telessinalizado SE
ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_S_TS_SE |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SE | Alarme de Estado em Ponto Telessinalizado SE
null@null___POSICAO 1@POSICAO 2___Custom_S_TS_SE |  | Transit;POSICAO 1;POSICAO 2;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SE | Alarme de Estado em Ponto Telessinalizado SE
null@null___DESLIGADO@LIGADO___SwitchStatus_S_TC_SE |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SE | Alarme de Estado em Ponto Telecontrolado SE
null@LIGAR___null@LIGADO___SwitchStatus_S_TC_SE |  | Transit;LIGAR;; | 0;2;1;3 | 2;1;0;3 | ;LIGAR;; | #FF000000;#FF000000;#00000000;#00000000 | Abnormal;Auto;Normal;Normal | FALSE;TRUE;TRUE;TRUE | Alarme de Estado em Ponto Telecontrolado SE | Alarme de Estado em Ponto Telecontrolado SE
DESLIGAR@null___null@DESLIGADO___SwitchStatus_S_TC_SE |  | Transit;DESLIGAR;; | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;; | #FF000000;#FF000000;#00000000;#00000000 | Abnormal;Auto;Normal;Normal | FALSE;TRUE;TRUE;TRUE | Alarme de Estado em Ponto Telecontrolado SE | Alarme de Estado em Ponto Telecontrolado SE
null@COMANDADO___DESATIVADO@ATIVADO___CustomCR_S_TC |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado
null@INDIVIDUAL___DESATIVADO@ATIVADO___CustomCR_S_TC |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;MESTRE; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE_USO_BC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;1;2;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SE | Alarme de Estado em Ponto Telecontrolado SE
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_S_TS_ST__ICCP_CPFLT |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;1;2;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado ST | Alarme de Estado em Ponto Telessinalizado ST
null@INDIVIDUAL___DESATIVADO@ATIVADO___CustomCR_S_TC_vnb |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;1;0;3 | ;INDIVIDUAL;MESTRE; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado
null@MESTRE___DESATIVADO@ATIVADO___CustomCR_S_TC_VNB |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;PARALELO;INDIVIDUAL; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado
null@REARMAR___NORMAL@ATUADO___Custom_S_TS_SI |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SI | Alarme de Estado em Ponto Telessinalizado SI
null@REARMAR___NORMAL@ATUADO___Custom_S_TC_SI |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;REARMAR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SI | Alarme de Estado em Ponto Telecontrolado SI
null@null___NORMAL@ATUADO___Custom_S_TS_SI |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SI | Alarme de Estado em Ponto Telessinalizado SI
null@null___NORMAL@DEFEITO___Custom___INV_S_TS_SI |  | Transit;NORMAL;DEFEITO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SI | Alarme de Estado em Ponto Telessinalizado SI
null@null___NORMAL@DEFEITO___Custom_S_TS_SI |  | Transit;NORMAL;DEFEITO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SI | Alarme de Estado em Ponto Telessinalizado SI
null@null___NORMAL@ATUADO___Custom___INV_S_TS_SI |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SI | Alarme de Estado em Ponto Telessinalizado SI
DI_null@null___NORMAL@DEFEITO___Malfunctioning___INV_S_TS_SI |  | Transit;NORMAL;DEFEITO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SI | Alarme de Estado em Ponto Telessinalizado SI
null@null___NORMAL@FALHA___Custom_S_TS_SI |  | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SI | Alarme de Estado em Ponto Telessinalizado SI
null@null___LIGADO@DESLIGADO___Custom_S_TS_SI |  | Transit;LIGADO;DESLIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SI | Alarme de Estado em Ponto Telessinalizado SI
null@null___CARGA@DESCARGA___Custom_S_TS_SI |  | Transit;CARGA;DESCARGA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SI | Alarme de Estado em Ponto Telessinalizado SI
null@null___NORMAL@DEFEITO___Custom_D_TS_SI |  | Invalido;NORMAL;DEFEITO;Error | 0;1;2;3 | 0;1;2;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SI | Alarme de Estado em Ponto Telessinalizado SI
null@REARMAR___NORMAL@ATUADO___Custom___INV_S_TS_SI |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SI | Alarme de Estado em Ponto Telessinalizado SI
null@null___ABERTO@FECHADO___SwitchStatus_S_TS |  | Error;ABERTO;FECHADO;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
CMD_COS@null___REMOTO@LOCAL___Custom___INV_S_TS_SS |  | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___NORMAL@ATUADO___RelayTrip_S_TS |  | Error;NORMAL;ATUADO;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@ATUADO___Custom_S_TS |  | Error;NORMAL;ATUADO;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@FALTA___Custom_S_TS |  | Transit;NORMAL;FALTA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@DEFEITO___Custom_S_TS |  | Transit;NORMAL;DEFEITO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@FALHA___Custom_S_TS |  | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___LIGADO@DESLIGADO___Custom_S_TS |  | Transit;LIGADO;DESLIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___CARREGADA@DESCARREGADA___Custom_S_TS |  | Transit;CARREGADA;DESCARREGADA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___ABERTO@FECHADO___SwitchStatus_D_TS |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 0;1;2;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
CMD_COS@null___REMOTO@LOCAL___Custom_S_TC |  | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;0;1;3 | ;CMD_COS;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
null@null___CARGA@DESCARGA___Custom_S_TS |  | Transit;CARGA;DESCARGA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___DESATIVADO@ATIVADO___Custom_S_TS |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_DS_PROT |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
null@null___NORMAL@FALHA___Custom___INV_S_TS |  | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___DESLIGAR@LIGAR___Custom_S_TS |  | Transit;DESLIGAR;LIGAR;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@ATUADO___Custom___INV_S_TS |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___INV___admsINV_S_TC_DS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS |  | Transit;BLOQUEADA;LIBERADA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___ABERTO@FECHADO___Custom___INV_S_TS |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
MESTRE@INDIVIDUAL@COMANDO___MESTRE@INDIVIDUAL@COMANDO___Parallel___admsINV_D_TS |  | MESTRE;INDIVIDUAL;COMANDADO; | 0;1;2;3 | 0;1;2;3 | MESTRE;INDIVIDUAL;COMANDO; | #FF00FF00;#FF00FF00;#FF00FF00;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___@___TapIncrement_S_TS |  | Error;;;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@DEFEITO___Custom___INV_S_TS |  | Error;NORMAL;DEFEITO;Transit | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@FALTA VCC VCA___Custom_S_TS |  | Transit;NORMAL;FALTA VCC VCA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___MANUAL@AUTOMATICO___Custom_S_TS |  | Transit;MANUAL;AUTOMATICO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@FALTA___Custom___INV_S_TS |  | Error;NORMAL;FALTA;Transit | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___LIGADO@DESLIGADO___Custom___INV_S_TS |  | Transit;LIGADO;DESLIGADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___DESLIGADO@LIGADO___Custom_S_TS |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___AUTOMATICO@MANUAL___Custom___INV___admsINV_S_TS |  | Error;AUTOMATICO;MANUAL;Transit | 0;2;1;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
CMD_COS@null___REMOTO@LOCAL___Custom_S_TC_SS |  | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;0;1;3 | ;CMD_COS;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___INV___admsINV_S_TC_DS_MANOBRA |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___INV___admsINV_S_TC_DS_PROT |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
null@null___ABERTO@FECHADO___SwitchStatus___INV_S_TS |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___BLOQUEADA@LIBERADA___Custom_S_TS |  | Transit;BLOQUEADA;LIBERADA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@DISCREPANCIA___Custom_S_TS |  | Transit;NORMAL;DISCREPANCIA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___ABERTO@FECHADO___Custom_S_TS |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@BLOQUEIO___Custom___INV_S_TS |  | Error;NORMAL;BLOQUEIO;Transit | 0;1;2;3 | 1;2;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___AUTOMATICO@MANUAL___Custom___admsINV_S_TS |  | Error;AUTOMATICO;MANUAL;Transit | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@FALHA___Custom_D_TS |  | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@ATUADO___RelayTrip___INV_S_TS |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@FALHA___RelayTrip_S_TS |  | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___DESLIGADO@LIGADO___Custom___INV_S_TS |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@BLOQUEIO___Custom_S_TS |  | Transit;NORMAL;BLOQUEIO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___AUTOM DESATIVOU@AUTOM ATIVOU___Custom___INV_S_TS |  | Transit;AUTOM DESATIVOU;AUTOM ATIVOU;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___MANUAL DESATIVOU@MANUAL ATIVOU___Custom___INV_S_TS |  | Transit;MANUAL DESATIVOU;MANUAL ATIVOU;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
CMD_COS@null___REMOTO@LOCAL___Custom_S_TS_SS |  | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___NORMAL@OLEO FALHA___Custom_S_TS |  | Transit;NORMAL;OLEO FALHA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@BAIXA___Custom_S_TS |  | Transit;NORMAL;BAIXA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_null@null___REMOTO@LOCAL___Local___INV_S_TS |  | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___DESLIGADO@LIGADO___SwitchStatus_S_TS |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_null@null___REMOTO@LOCAL___Local___INV_S_TS_DS |  | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DS | Alarme de Estado em Ponto Telessinalizado DS
null@null___DESATIVADO@ATIVADO___Custom___INV_S_TS |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@BLOQUEADA___Custom___admsINV_S_TS |  | Error;NORMAL;BLOQUEADA;Transit | 0;2;1;3 | 1;0;2;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___DESLIGADO@LIGADO___SwitchStatus___INV_S_TS |  | Error;DESLIGADO;LIGADO;Transit | 0;1;2;3 | 2;1;0;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___CARREGADA@DESCARREGADA___Custom___INV_S_TS |  | Transit;CARREGADA;DESCARREGADA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NÃO PERMITIDO@PERMITIDO___Custom_S_TS |  | Transit;NÃO PERMITIDO;PERMITIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMALIZADO@TENSAO RETORNO___Custom_S_TS |  | Error;NORMALIZADO;TENSAO RETORNO;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___DESATRACADO@ATRACADO___Custom___INV_S_TS |  | Error;DESATRACADO;ATRACADO;Transit | 0;1;2;3 | 1;2;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___DESLIGADO@LIGADO___SwitchStatus_D_TS |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;1;2;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Abnormal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
MESTRE@INDIVIDUAL@COMANDO___MESTRE@INDIVIDUAL@COMANDO___Parallel___admsINV_D_TS_SS |  | MESTRE;INDIVIDUAL;COMANDADO; | 2;0;1;3 | 0;2;1;3 | MESTRE;INDIVIDUAL;COMANDO; | #FFFF0000;#FF00FF00;#FF00FF00;#FF000000 | Normal;Abnormal;Abnormal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___AUTOMATICO@MANUAL___Custom_S_TS |  | Transit;AUTOMATICO;MANUAL;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___MANUAL DESATIVOU@MANUAL ATIVOU___Custom_S_TS |  | Transit;MANUAL DESATIVOU;MANUAL ATIVOU;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___INV_S_TC |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
null@null___NORMAL@TRANSFERIDA___Custom_S_TS |  | Error;NORMAL;TRANSFERIDA;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___COMPLETA@INCOMPLETA___Custom_S_TS |  | Transit;COMPLETA;INCOMPLETA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___FALHA@OPERANDO___Custom_S_TS |  | Transit;FALHA;OPERANDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___@____S_TS |  | Error;;;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_DESABILITAR@HABILITAR___null@null___Custom_S_TC_DVx |  | ;;; | 0;1;2;3 | 2;0;1;3 | ;DESABILITAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DVx | Alarme de Estado em Ponto Telecontrolado DVx
null@null___NORMAL@ALTERNATIVO___Custom_S_TS |  | Error;NORMAL;ALTERNATIVO;Transit | 0;1;2;3 | 1;0;2;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@SEM COMUN___Custom_S_TS |  | Error;NORMAL;SEM COMUN;Transit | 0;1;2;3 | 1;0;2;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_null@null___DESABILITADO@HABILITADO___Custom_S_TS_DS |  | Transit;DESABILITADO;HABILITADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DS | Alarme de Estado em Ponto Telessinalizado DS
null@null___NORMAL@ALTERNATIVO___Custom___INV_S_TS |  | Error;NORMAL;ALTERNATIVO;Transit | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___AUTOM DESATIVOU@AUTOM ATIVOU___Custom_S_TS |  | Transit;AUTOM DESATIVOU;AUTOM ATIVOU;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_null@null___DESABILITADO@HABILITADO___Custom_S_TS_DV |  | Transit;DESABILITADO;HABILITADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DV | Alarme de Estado em Ponto Telessinalizado DV
null@null___AUTOM DESATIVADO@AUTOM ATIVADO___Custom_S_TS |  | Transit;AUTOM DESATIVADO;AUTOM ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@ERRO___Custom_S_TS |  | Transit;NORMAL;ERRO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@BLOQUEADA___Enabled___admsINV_S_TS |  | Error;NORMAL;BLOQUEADA;Transit | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@BLOQUEADA___Enabled___INV___admsINV_S_TS |  | Error;NORMAL;BLOQUEADA;Transit | 0;2;1;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_null@null___DESABILITADO@HABILITADO___HotLineTag_S_TS |  | Transit;DESABILITADO;HABILITADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL DESATIVAD@NORMAL ATIVADO___Custom___admsINV_S_TS |  | Error;NORMAL DESATIVAD;NORMAL ATIVADO;Transit | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___DESLIGADO@LIGADO___Custom_D_TS |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
MESTRE@INDIVIDUAL@COMANDO___MESTRE@INDIVIDUAL@COMANDO___Parallel___INV___admsINV_D_TS_SS |  | MESTRE;INDIVIDUAL;COMANDADO; | 2;0;1;3 | 0;2;1;3 | MESTRE;INDIVIDUAL;COMANDO; | #FFFF0000;#FF00FF00;#FF00FF00;#FF000000 | Normal;Abnormal;Abnormal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___NORMAL@COMPLETA___Custom_S_TS |  | Transit;NORMAL;COMPLETA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NÃO PERMITIDO@PERMITIDO___Custom___INV_S_TS |  | Error;NÃO PERMITIDO;PERMITIDO;Transit | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___@___Custom_S_TS |  | Transit;null;null;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@NORMAL___Custom_S_TS |  | Error;NORMAL;NORMAL;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___INV_S_TC_DS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
null@null___NORMAL@DEFEITO___Custom_D_TS |  | Error;NORMAL;DEFEITO;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___EXTRAIDO@INSERIDO___Custom_S_TS |  | Transit;EXTRAIDO;INSERIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@DISCREPANCIA___Custom___INV_S_TS |  | Transit;NORMAL;DISCREPANCIA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@BLOQUEADO___Custom_S_TS |  | Error;NORMAL;BLOQUEADO;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_null@null___REMOTO@LOCAL___Local_S_TS |  | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@ATUADO___RelayTrip_D_TS |  | Error;NORMAL;ATUADO;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_null@null___DESABILITADO@HABILITADO___HotLineTag_S_TS_DS |  | Transit;DESABILITADO;HABILITADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DS | Alarme de Estado em Ponto Telessinalizado DS
null@null___NORMAL@INTERMITENTE___Custom_S_TS |  | Error;NORMAL;INTERMITENTE;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@FALTA VCA___Custom_S_TS |  | Error;NORMAL;FALTA VCA;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
MESTRE@INDIVIDUAL@COMANDO___MESTRE@INDIVIDUAL@COMANDO___Custom___admsINV_D_TS |  | MESTRE;INDIVIDUAL;; | 0;1;2;3 | 0;1;2;3 | MESTRE;INDIVIDUAL;; | #FF00FF00;#FF00FF00;#FF00FF00;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
MESTRE@INDIVIDUAL@COMANDO___MESTRE@INDIVIDUAL@COMANDO___Parallel___INV_S_TC |  | MESTRE;INDIVIDUAL;COMANDADO; | 0;1;2;3 | 0;1;2;3 | MESTRE;INDIVIDUAL;COMANDO; | #FF00FF00;#FF00FF00;#FF00FF00;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
null@null___NORMAL@FALTA VCA___Custom___INV_S_TS |  | Error;NORMAL;FALTA VCA;Transit | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@FALHA___Custom___INV_D_TS |  | Error;NORMAL;FALHA;Transit | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
TROCA@null___null@null___Custom_S_TC_SA |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;TROCA;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SA | Alarme de Estado em Ponto Telecontrolado SA
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom___INV_S_TC_SA |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;1;0;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SA | Alarme de Estado em Ponto Telecontrolado SA
G1 ATIVAR@G2 ATIVAR___G1 ATIVADO@G2 ATIVADO___Custom_D_TC_SA |  | Transit;G1 ATIVADO;G2 ATIVADO;Error | 0;1;2;3 | 0;1;2;3 | ;G1 ATIVAR;G2 ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SA | Alarme de Estado em Ponto Telecontrolado SA
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom___INV_S_TS_SA |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___DESINIBIDA@INIBIDA___Custom_S_TS |  | Error;DESINIBIDA;INIBIDA;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@FALHA COM___Custom_S_TS |  | Error;NORMAL;FALHA COM;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___LIGADO@DESLIGADO___Custom_D_TS |  | Error;LIGADO;DESLIGADO;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL DESATIVAD@NORMAL ATIVADO___Custom_S_TS |  | Error;NORMAL DESATIVAD;NORMAL ATIVADO;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___LIBERADO@BLOQUEADO___Custom___INV_S_TS |  | Transit;LIBERADO;BLOQUEADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
MESTRE@INDIVIDUAL@COMANDO___MESTRE@INDIVIDUAL@COMANDO___Custom_D_TS |  | MESTRE;INDIVIDUAL;COMANDADO; | 2;0;1;3 | 0;2;1;3 | MESTRE;INDIVIDUAL;COMANDO; | #FFFF0000;#FF00FF00;#FF00FF00;#FF000000 | Normal;Abnormal;Abnormal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
MESTRE@INDIVIDUAL@COMANDO___MESTRE@INDIVIDUAL@COMANDO___Parallel_D_TS |  | MESTRE;INDIVIDUAL;COMANDADO; | 2;0;1;3 | 0;2;1;3 | MESTRE;INDIVIDUAL;COMANDO; | #FFFF0000;#FF00FF00;#FF00FF00;#FF000000 | Normal;Abnormal;Abnormal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@BLOQUEADA___Enabled_S_TS |  | Transit;NORMAL;BLOQUEADA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_null@null___REMOTO@LOCAL___Local_S_TS_DS |  | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DS | Alarme de Estado em Ponto Telessinalizado DS
null@null___NORMAL@BLOQUEADA___Enabled___INV_S_TS |  | Transit;NORMAL;BLOQUEADA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
Habilitar LF |  | LF Desabilitado;Somente LF Habilitado;LF e ES Habilitados | 0;1;2 | 0;1;2 | Desabilitar LF;Habilitar somente LF;Habilitar LF e ES | #00000000;#00F30C0C;#00000000 | Normal;Normal;Normal | TRUE;TRUE;TRUE
null@null___NORMAL@INIBIDO___Custom___INV_S_TS |  | Transit;NORMAL;INIBIDO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___@___TapIncrement_D_TS |  | Transit;null;null;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___MANUAL@AUTOMATICO___Custom___INV_S_TS |  | Transit;MANUAL;AUTOMATICO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
MESTRE@INDIVIDUAL@COMANDO___MESTRE@INDIVIDUAL@COMANDO___Parallel_D_TS_SS |  | MESTRE;INDIVIDUAL;COMANDADO; | 2;0;1;3 | 0;2;1;3 | MESTRE;INDIVIDUAL;COMANDO; | #FFFF0000;#FF00FF00;#FF00FF00;#FF000000 | Normal;Abnormal;Abnormal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___ATIVOU@INIBIU___Custom_S_TS |  | Transit;ATIVOU;INIBIU;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@INCOMPLETA___Custom_S_TS |  | Transit;NORMAL;INCOMPLETA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___FALHA@OPERANDO___Custom___INV_S_TS |  | Transit;FALHA;OPERANDO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___POSICAO 1@POSICAO 2___Custom_S_TS |  | Transit;POSICAO 1;POSICAO 2;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___DESLIGADA@LIGADA___Custom___INV_S_TS |  | Transit;DESLIGADA;LIGADA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@ATUADO___RecloserLockout_S_TS_SA |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled_S_TC |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
null@null___0@EXECUTADO___Custom_S_TS |  | Transit;0;EXECUTADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
HABILITAR@null___HABILITADO@DESABILITADO__Enabled_S_TC_SS |  | Transit;DESABILITADO;HABILITADO;Error | 0;2;1;3 | 2;0;1;3 | ;HABILITAR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@null___NORMAL@ATUADO___Malfunctioning_S_TS |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@DEFEITO___Malfunctioning_S_TS |  | Transit;NORMAL;DEFEITO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@DEFEITO___Malfunctioning___INV_S_TS |  | Transit;NORMAL;DEFEITO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled_S_TC_DS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
null@null___null@null___Custom_S_TS |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_null@null___NORMAL@ATUADO___RecloserLockout_S_TS |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_null@null___NORMAL@ATUADO___Malfunctioning_S_TS |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_null@null___NORMAL@ATUADO___Custom_S_TS |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_null@null___NORMAL@FALHA___Custom_S_TS |  | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DI_null@null___NORMAL@FALTA___Custom_S_TS |  | Transit;NORMAL;FALTA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___DESABILITADO@HABILITADO___Custom___INV_S_TS |  | Error;DESABILITADO;HABILITADO;Transit | 0;1;2;3 | 1;2;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_null@null___NORMAL@ATUADO___RelayTrip_S_TS |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_null@null@null___PROTEÇÃO@CHAVE@SECCIONALIZADOR___Custom_D_TS |  | PROTEÇÃO;CHAVE;SECCIONALIZADOR; | 0;1;2;3 | 0;1;2;3 | ;;; | #FF00FF00;#FF00FF00;#FF00FF00;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_null@null___NORMAL@DEFEITO___Custom_S_TS |  | Transit;NORMAL;DEFEITO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_R90 |  | Error;INCLUIDO;EXCLUIDO;Transit | 0;2;1;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@ATUADO___Custom_S_TS_SA |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@REARMAR___NORMAL@ATUADO___Custom_S_TS_SA |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
REARMAR@null___NORMAL@ATUADO___Custom_S_TC_SA |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;REARMAR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SA | Alarme de Estado em Ponto Telecontrolado SA
null@null___DESLIGAR@LIGAR___Custom_S_TS_SA |  | Transit;DESLIGAR;LIGAR;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@FALHA___Custom_S_TS_SA |  | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@FALTA___Custom_S_TS_SA |  | Transit;NORMAL;FALTA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@FALHA___Custom___INV_S_TS_SA |  | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___DESATIVADO@ATIVADO___Parallel_S_TS |  | Error;DESATIVADO;ATIVADO;Transit | 0;1;2;3 | 2;0;1;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___DESATIVADO@ATIVADO___Custom_S_TS_SA |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@MESTRE___DESATIVADO@ATIVADO___Custom_S_TC_SA |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;MESTRE; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SA | Alarme de Estado em Ponto Telecontrolado SA
null@INDIVIDUAL___DESATIVADO@ATIVADO___Custom_S_TC_SA |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;INDIVIDUAL; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SA | Alarme de Estado em Ponto Telecontrolado SA
null@null___BLOQUEADA@LIBERADA___Custom_S_TS_SA |  | Transit;BLOQUEADA;LIBERADA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SA |  | Transit;BLOQUEADA;LIBERADA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
REARMAR@BLOQUEAR___NORMAL@ATUADO___Custom_S_TS_SA |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@FALHA___RelayTrip_S_TS_SA |  | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@COMPLETA___Custom_S_TS_SA |  | Transit;NORMAL;COMPLETA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___COMPLETA@INCOMPLETA___Custom_S_TS_SA |  | Transit;COMPLETA;INCOMPLETA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@ATUADO___RelayTrip_S_TS_A1 |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado A1 | Alarme de Estado em Ponto Telessinalizado A1
DESBLOQUEAR@BLOQUEAR___NORMAL@BLOQUEADA___Enabled_S_TS_SA |  | Transit;NORMAL;BLOQUEADA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
DI_null@null___NORMAL@ATUADO___RelayTrip___INV_S_TS_DA |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DA | Alarme de Estado em Ponto Telessinalizado DA
DI_null@null___NORMAL@FALTA___Custom___INV_S_TS_A1 |  | Transit;NORMAL;FALTA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado A1 | Alarme de Estado em Ponto Telessinalizado A1
DI_RESET@null___NORMAL@BLOQUEIO___Custom_S_TC_DA |  | Transit;NORMAL;BLOQUEIO;Error | 0;1;2;3 | 2;0;1;3 | ;RESET;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DA | Alarme de Estado em Ponto Telecontrolado DA
DI_null@null___NORMAL@ATUADO___Custom___INV_S_TS_DA |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DA | Alarme de Estado em Ponto Telessinalizado DA
DI_null@null___CARREGADO@DESCARREGADO___Custom___INV_S_TS_DA |  | Transit;CARREGADO;DESCARREGADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DA | Alarme de Estado em Ponto Telessinalizado DA
DI_null@null___NORMAL@ATUADO___RelayTrip_S_TS_DA |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DA | Alarme de Estado em Ponto Telessinalizado DA
DI_null@null___NORMAL@FALTA___Custom_S_TS_A1 |  | Transit;NORMAL;FALTA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado A1 | Alarme de Estado em Ponto Telessinalizado A1
DI_null@null___NORMAL@ATUADO___RecloserLockout_S_TS_A1 |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado A1 | Alarme de Estado em Ponto Telessinalizado A1
DI_null@null___NORMAL@ATUADO___Custom_S_TS_DA |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DA | Alarme de Estado em Ponto Telessinalizado DA
null@null___NORMAL@BLOQUEIO___Custom_S_TS_SA |  | Transit;NORMAL;BLOQUEIO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@DISCREPANCIA___Custom_S_TS_SA |  | Transit;NORMAL;DISCREPANCIA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SA |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SA | Alarme de Estado em Ponto Telecontrolado SA
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TS_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___NORMAL@DEFEITO___Custom_S_TS_SA |  | Transit;NORMAL;DEFEITO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
DI_RESET@null___NORMAL@BLOQUEIO___Custom___admsINV_S_TC_DA |  | Transit;NORMAL;BLOQUEIO;Error | 0;2;1;3 | 2;0;1;3 | ;RESET;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DA | Alarme de Estado em Ponto Telecontrolado DA
null@null___NORMAL@ATUADO___Custom_S_TS_DA |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DA | Alarme de Estado em Ponto Telessinalizado DA
null@null___NORMAL@ATUADO___RelayTrip_S_TS_DA |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DA | Alarme de Estado em Ponto Telessinalizado DA
null@null___NORMAL@ATUADO___Custom_S_TS_A1 |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado A1 | Alarme de Estado em Ponto Telessinalizado A1
null@null___NORMAL@ATUADO___Custom___INV_S_TS_SA |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_D_TC |  | Error;INCLUIDO;EXCLUIDO;Transit | 0;1;2;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_D_TC_SS |  | Invalido;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 0;1;2;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
DESBLOQUEAR@BLOQUEAR___NORMAL@BLOQUEADA___Enabled___admsINV_S_TS_SA |  | Transit;NORMAL;BLOQUEADA;Error | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@TRANSFERIDA___Custom_S_TS_SA |  | Transit;NORMAL;TRANSFERIDA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
DESBLOQUEAR@BLOQUEAR___NORMAL@BLOQUEADA___Enabled___INV___admsINV_S_TS_SA |  | Transit;NORMAL;BLOQUEADA;Error | 0;2;1;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___DESABILITADO@HABILITADO___Custom_S_TS |  | Error;DESABILITADO;HABILITADO;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@ERRO___Custom_S_TS_SA |  | Transit;NORMAL;ERRO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@REARMAR___NORMAL@ATUADO___Custom___INV_S_TS_SA |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@BLOQUEADO___Custom_S_TS_SA |  | Transit;NORMAL;BLOQUEADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@NORMAL___ControlActiveSetting_S_TC_SA |  | Transit;NORMAL;NORMAL;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SA | Alarme de Estado em Ponto Telecontrolado SA
null@null___NORMAL@ATUADO___Custom_S_TC_SA |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SA | Alarme de Estado em Ponto Telecontrolado SA
null@null___DESINIBIDA@INIBIDA___Custom_S_TS_SA |  | Transit;DESINIBIDA;INIBIDA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE |  | Alarme de Estado em Ponto Telessinalizado SA
null@null___LIGADO@DESLIGADO___Custom_S_TS_SA |  | Transit;LIGADO;DESLIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___DESATRACADO@ATRACADO___Custom___INV_S_TS_SA |  | Transit;DESATRACADO;ATRACADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMALIZADO@TENSAO RETORNO___Custom_S_TS_SA |  | Transit;NORMALIZADO;TENSAO RETORNO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@ATUADO___RelayTrip___INV_S_TS_SA |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
RELIGADOR@ALTERNATIVO___null@null___Custom_S_TC_SA |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;RELIGADOR;ALTERNATIVO; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SA | Alarme de Estado em Ponto Telecontrolado SA
null@null___NORMAL@INTERMITENTE___Custom_S_TS_SA |  | Transit;NORMAL;INTERMITENTE;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___DESABILITADO@HABILITADO___Custom6_S_TS |  | Transit;DESABILITADO;HABILITADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SA |  | Transit;CARREGADA;DESCARREGADA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@ATUADO___RelayTrip_D_TS_SA |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@INCOMPLETA___Custom_S_TS_SA |  | Transit;NORMAL;INCOMPLETA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
null@null___CARGA@DESCARGA___Custom_S_TS_SA |  | Transit;CARGA;DESCARGA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@DISCREPANCIA___Custom___INV_S_TS_SA |  | Transit;NORMAL;DISCREPANCIA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
CMD_CEEE@CMD_RGE___CEEE@RGE___Custom___INV___admsINV_S_TC_SA |  | Transit;CEEE;RGE;Error | 0;2;1;3 | 2;1;0;3 | ;CMD_CEEE;CMD_RGE; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SA | Alarme de Estado em Ponto Telecontrolado SA
null@null___OPERANDO@BLOQUEADO___Custom_S_TS_SA |  | Transit;OPERANDO;BLOQUEADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@RECEBIDO___Custom_S_TS_SA |  | Transit;NORMAL;RECEBIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@TRANSMITIDO___Custom_S_TS_SA |  | Transit;NORMAL;TRANSMITIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@ATUADO___Custom___INV_S_TS_DA |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DA | Alarme de Estado em Ponto Telessinalizado DA
DI_null@null___CARREGADO@DESCARREGADO___Custom___INV_S_TS_Dax |  | Transit;CARREGADO;DESCARREGADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DAx | Alarme de Estado em Ponto Telessinalizado DAx
DI_null@null___NORMAL@ATUADO___Custom_S_TS_Dax |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DAx | Alarme de Estado em Ponto Telessinalizado DAx
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom___INV_S_TC_Sax |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;1;0;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SAx | Alarme de Estado em Ponto Telecontrolado SAx
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom___INV_S_TS_Sax |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SAx | Alarme de Estado em Ponto Telessinalizado SAx
null@null___DESLIGADO@LIGADO___SwitchStatus_S_TS_USO_BC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@REVERSO___Custom_S_TS |  | Error;NORMAL;REVERSO;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_null@null___NORMAL@ATUADO___Custom_S_TS_A1 |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado A1 | Alarme de Estado em Ponto Telessinalizado A1
DI_null@null___NORMAL@REVERSO___Custom_S_TS |  | Error;NORMAL;REVERSO;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_null@null___NORMAL@ATUADO___Custom_Sinv_TS_A1 |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado A1 | Alarme de Estado em Ponto Telessinalizado A1
DI_RELIGADOR@CHAVE___RELIGADOR@CHAVE___Custom6_S_TC_DV |  | Transit;RELIGADOR;CHAVE;Error | 0;2;1;3 | 2;0;1;3 | ;RELIGADOR;CHAVE; | #FF000000;#FF00FF00;#FF00FF00;#FF000000 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_null@null___ABERTO@FECHADO___Custom___S_TS_DP |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Abnormal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DP | Alarme de Estado em Ponto Telessinalizado DP
RELIGADOR@ALTERNATIVO___NORMAL@ALTERNATIVO___Custom_S_TS_DV |  | Transit;NORMAL;ALTERNATIVO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DV | Alarme de Estado em Ponto Telessinalizado DV
G1@G2___GRUPO 1@GRUPO 2___Custom_D_TC_SV |  | Transit;GRUPO 1;GRUPO 2;Error | 0;1;2;3 | 0;1;2;3 | ;G1;G2; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SV | Alarme de Estado em Ponto Telecontrolado SV
DI_null@null___ABERTO@FECHADO___Custom_S_TS_DP |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DP | Alarme de Estado em Ponto Telessinalizado DP
TROCA@null___NORMAL@ALTERNATIVO___Custom_S_TC_SV |  | Transit;NORMAL;ALTERNATIVO;Error | 0;1;2;3 | 2;0;1;3 | ;TROCA;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SV | Alarme de Estado em Ponto Telecontrolado SV
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SP |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SP | Alarme de Estado em Ponto Telecontrolado SP
null@null___NORMAL@ATUADO___Custom_S_TS_SP |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SP | Alarme de Estado em Ponto Telessinalizado SP
null@null___NORMAL@DISPARADA___Custom_S_TS |  | Transit;NORMAL;DISPARADA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TC_SV |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SV | Alarme de Estado em Ponto Telecontrolado SV
DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TS_SV |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SV | Alarme de Estado em Ponto Telessinalizado SV
MANUAL@AUTOMATICO___MANUAL@AUTOMATICO___Custom_S_TS_SV |  | Transit;MANUAL;AUTOMATICO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SV | Alarme de Estado em Ponto Telessinalizado SV
null@null___ABERTO@FECHADO___Custom___INV_S_TS_SP |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SP | Alarme de Estado em Ponto Telessinalizado SP
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SV | Alarme de Estado em Ponto Telecontrolado SV
null@ATIV_DES___DESATIVADO@ATIVADO___Custom_S_TS_SV |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SV | Alarme de Estado em Ponto Telessinalizado SV
null@null___DESATIVADO@ATIVADO___Custom_S_TS_SV |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SV | Alarme de Estado em Ponto Telessinalizado SV
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TS_SV |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SV | Alarme de Estado em Ponto Telessinalizado SV
RELIGADOR@ALTERNATIVO___null@null___Custom_S_TC_SV |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;RELIGADOR;ALTERNATIVO; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SV | Alarme de Estado em Ponto Telecontrolado SV
null@null___ABERTO@FECHADO___Custom_S_TS_SP |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SP | Alarme de Estado em Ponto Telessinalizado SP
null@null___NORMAL@DEFEITO___Custom_S_TS_SP |  | Transit;NORMAL;DEFEITO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SP | Alarme de Estado em Ponto Telessinalizado SP
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TS_SP |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SP | Alarme de Estado em Ponto Telessinalizado SP
DI_ALTERNATIVO@RELIGADOR@CHAVE___ALTERNATIVO@RELIGADOR@CHAVE___Custom_D_TC_DV |  | ALTERNATIVO;RELIGADOR;CHAVE; | 0;1;2;3 | 0;1;2;3 | ALTERNATIVO;RELIGADOR;CHAVE; | #FF00FF00;#FF00FF00;#FF00FF00;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
null@null___DESABILITADO@HABILITADO___HotLineTag___INV_S_TS |  | Transit;DESABILITADO;HABILITADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_NORMAL@ALTERNATIVO___NORMAL@ALTERNATIVO___Custom_D_TC_DV |  | Transit;NORMAL;ALTERNATIVO;Error | 0;1;2;3 | 0;1;2;3 | ;NORMAL;ALTERNATIVO; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_null@null___RELIGADOR@CHAVE___Custom6_S_TC_DV |  | Transit;RELIGADOR;CHAVE;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_null@null___0@FALHA___Custom_S_TS_DV |  | Transit;0;FALHA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DV | Alarme de Estado em Ponto Telessinalizado DV
DI_RELIGADOR@CHAVE___RELIGADOR@CHAVE___Custom___INV_S_TC_DV |  | Transit;RELIGADOR;CHAVE;Error | 0;1;2;3 | 2;0;1;3 | ;RELIGADOR;CHAVE; | #FF000000;#FF00FF00;#FF00FF00;#FF000000 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_null@null___0@SUCESSO___Custom_S_TS_DV |  | Transit;0;SUCESSO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DV | Alarme de Estado em Ponto Telessinalizado DV
DI_null@null___ABERTO@FECHADO___Custom___INV_S_TS_DP |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DP | Alarme de Estado em Ponto Telessinalizado DP
DI_null@null___NORMAL@ATUADO___Custom_S_TS_DV |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DV | Alarme de Estado em Ponto Telessinalizado DV
DI_DESBLOQUEAR@BLOQUEAR___NORMAL@BLOQUEADA___Enabled___INV_S_TC_DV |  | Transit;NORMAL;BLOQUEADA;Error | 0;1;2;3 | 2;1;0;3 | ;DESBLOQUEAR;BLOQUEAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_null@null@null___PROTEÇÃO@CHAVE@SECCIONALIZADOR___Custom_D_TS_DV |  | PROTEÇÃO;CHAVE;SECCIONALIZADOR; | 0;1;2;3 | 0;1;2;3 | ;;; | #FF00FF00;#FF00FF00;#FF00FF00;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DV | Alarme de Estado em Ponto Telessinalizado DV
DI_DESBLOQUEAR@null___NORMAL@BLOQUEADA___Enabled_S_TS_DV |  | Transit;NORMAL;BLOQUEADA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DV | Alarme de Estado em Ponto Telessinalizado DV
DI_RESETAR@null___RESET@null___Custom_S_TC_DV |  | Transit;RESET;;Error | 0;1;2;3 | 2;0;1;3 | ;RESETAR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_DESBLOQUEAR@null___NORMAL@BLOQUEADA___Enabled___INV_S_TC_DV |  | Transit;NORMAL;BLOQUEADA;Error | 0;1;2;3 | 2;1;0;3 | ;DESBLOQUEAR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_ATIVAR@null___ATIVADO@DESATIVADO___Custom_S_TC_SV |  | Transit;ATIVADO;DESATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;ATIVAR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SV | Alarme de Estado em Ponto Telecontrolado SV
DI_null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SV | Alarme de Estado em Ponto Telecontrolado SV
null@null___NORMAL@DEFEITO___Custom___INV_S_TS_SP |  | Transit;NORMAL;DEFEITO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SP | Alarme de Estado em Ponto Telessinalizado SP
null@null___NORMAL@FALTA___Custom_S_TS_SP |  | Transit;NORMAL;FALTA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SP | Alarme de Estado em Ponto Telessinalizado SP
DI_DESBLOQUEAR@BLOQUEAR___NORMAL@BLOQUEADA___Enabled___INV___admsINV_S_TC_DV |  | Transit;NORMAL;BLOQUEADA;Error | 0;2;1;3 | 2;1;0;3 | ;DESBLOQUEAR;BLOQUEAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_DESBLOQUEAR@null___NORMAL@BLOQUEADA___Enabled___admsINV_S_TS_DV |  | Transit;NORMAL;BLOQUEADA;Error | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DV | Alarme de Estado em Ponto Telessinalizado DV
DI_DESBLOQUEAR@null___NORMAL@BLOQUEADA___Enabled___INV___admsINV_S_TC_DV |  | Transit;NORMAL;BLOQUEADA;Error | 0;2;1;3 | 2;1;0;3 | ;DESBLOQUEAR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
TROCA@null___NORMAL@ALTERNATIVO___Custom___INV_S_TS_DV |  | Transit;NORMAL;ALTERNATIVO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DV | Alarme de Estado em Ponto Telessinalizado DV
null@null___NORMAL@ATUADO___Custom_S_TS_SV |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SV | Alarme de Estado em Ponto Telessinalizado SV
AUTOMATICO@MANUAL___AUTOMATICO@MANUAL___Custom___admsINV_S_TS_SV |  | Transit;AUTOMATICO;MANUAL;Error | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SV | Alarme de Estado em Ponto Telessinalizado SV
null@null___LIGADO@DESLIGADO___Custom_S_TS_SP |  | Transit;LIGADO;DESLIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SP | Alarme de Estado em Ponto Telessinalizado SP
DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_D_TS_SP |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;1;2;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SP | Alarme de Estado em Ponto Telessinalizado SP
DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom___INV_S_TC_SV |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;1;0;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SV | Alarme de Estado em Ponto Telecontrolado SV
null@null___NORMAL@ATUADO___Custom___INV_S_TS_SP |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SP | Alarme de Estado em Ponto Telessinalizado SP
AUTOMATICO@MANUAL___AUTOMATICO@MANUAL___Custom___admsINV_S_TC_SV |  | Transit;AUTOMATICO;MANUAL;Error | 0;2;1;3 | 2;0;1;3 | ;AUTOMATICO;MANUAL; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SV | Alarme de Estado em Ponto Telecontrolado SV
null@null___DESABILITADO@HABILITADO___HotLineTag___INV_S_TS_SS |  | Transit;DESABILITADO;HABILITADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
G1@G2___GRUPO 1@GRUPO 2___Custom_S_TC_SV |  | Transit;GRUPO 1;GRUPO 2;Error | 0;1;2;3 | 2;0;1;3 | ;G1;G2; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SV | Alarme de Estado em Ponto Telecontrolado SV
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom___INV_S_TS_SV |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SV | Alarme de Estado em Ponto Telessinalizado SV
null@null___NORMAL@DISPARADA___Custom_S_TS_SV |  | Transit;NORMAL;DISPARADA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SP | Alarme de Estado em Ponto Telessinalizado SV
null@null___DEFEITO@NORMAL___Custom_S_TS_SP |  | Transit;DEFEITO;NORMAL;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SP | Alarme de Estado em Ponto Telessinalizado SP
DI_null@CHAVE__INATIVO@CHAVE___Custom_S_TC_DV |  | Transit;INATIVO;CHAVE;Error | 0;1;2;3 | 2;0;1;3 | ;;CHAVE; | #FF000000;#FF00FF00;#FF00FF00;#FF000000 | Abnormal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_ALTERNATIVO@RELIGADOR__ALTERNATIVO@RELIGADOR___Custom_S_TC_DV |  | Transit;ALTERNATIVO;RELIGADOR;Error | 0;1;2;3 | 2;0;1;3 | ;ALTERNATIVO;RELIGADOR; | #FF000000;#FF00FF00;#FF00FF00;#FF000000 | Abnormal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
AUTOMATICO@MANUAL___AUTOMATICO@MANUAL___Custom___INV___admsINV_S_TS_SV |  | Transit;AUTOMATICO;MANUAL;Error | 0;2;1;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SV | Alarme de Estado em Ponto Telessinalizado SV
G1@G2___DESATIVADO@ATIVADO___Custom_S_TS_SV |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SV | Alarme de Estado em Ponto Telessinalizado SV
null@ATIV_DES___DESATIVADO@ATIVADO___Custom_S_TC_SV |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;ATIV_DES; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SV | Alarme de Estado em Ponto Telecontrolado SV
DI_CHAVE@null__CHAVE@null___Custom_S_TC_DV |  | Transit;CHAVE;INATIVO;Error | 0;1;2;3 | 2;0;1;3 | ;CHAVE;; | #FF000000;#FF00FF00;#FF00FF00;#FF000000 | Abnormal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_null@null@null___ALTERNATIVO@RELIGADOR@CHAVE___Custom_D_TS_DV |  | ALTERNATIVO;RELIGADOR;CHAVE;Error | 0;1;2;3 | 0;1;2;3 | ;;; | #FF00FF00;#FF00FF00;#FF00FF00;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_RELIGADOR@null__RELIGADOR@null___Custom_S_TC_DV |  | Transit;RELIGADOR;INATIVO;Error | 0;1;2;3 | 2;0;1;3 | ;RELIGADOR;; | #FF000000;#FF00FF00;#FF00FF00;#FF000000 | Abnormal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_ALTERNATIVO@null__ALTERNATIVO@null___Custom_S_TC_DV |  | Transit;ALTERNATIVO;Inativo;Error | 0;1;2;3 | 2;0;1;3 | ;ALTERNATIVO;; | #FF000000;#FF00FF00;#FF00FF00;#FF000000 | Abnormal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
null@null___DESABILITADO@HABILITADO___HotLineTag_S_TC_SS |  | Transit;DESABILITADO;HABILITADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@null___DEFEITO@NORMAL___Custom___INV_S_TS_SP |  | Transit;DEFEITO;NORMAL;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SP | Alarme de Estado em Ponto Telessinalizado SP
DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TS_SP |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SP | Alarme de Estado em Ponto Telessinalizado SP
DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom___INV_S_TS_SV |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SV | Alarme de Estado em Ponto Telessinalizado SV
null@null___DESLIGADO@LIGADO___Custom_S_TS_SV |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SV | Alarme de Estado em Ponto Telessinalizado SV
DI_RELIGADOR@ALTERNATIVO@CHAVE___RELIGADOR@ALTERNATIVO@CHAVE___Custom_D_TC_DV |  | RELIGADOR;ALTERNATIVO;CHAVE; | 0;1;2;3 | 0;1;2;3 | RELIGADOR;ALTERNATIVO;CHAVE; | #FF00FF00;#FF00FF00;#FF00FF00;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_RESETAR@null___null@null___Custom_S_TC_DV |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;RESETAR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_DESBLOQUEAR@null___NORMAL@BLOQUEADA___Enabled___admsINV_S_TC_DV |  | Transit;NORMAL;BLOQUEADA;Error | 0;2;1;3 | 2;0;1;3 | ;DESBLOQUEAR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
RELIGADOR@ALTERNATIVO___NORMAL@ALTERNATIVO___Custom_S_TC_SV |  | Transit;NORMAL;ALTERNATIVO;Error | 0;1;2;3 | 2;0;1;3 | ;RELIGADOR;ALTERNATIVO; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SV | Alarme de Estado em Ponto Telecontrolado SV
RELIGADOR@ALTERNATIVO___null@null___Custom_S_TS_SV |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SV | Alarme de Estado em Ponto Telessinalizado SV
DI_null@null___DESATIVADO@ATIVADO___Custom_S_TC_DV |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
TROCA@null___null@null___Custom_S_TC_SV |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;TROCA;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SV | Alarme de Estado em Ponto Telecontrolado SV
DI_NORMAL@ALTERNATIVO@CHAVE___Null@Null@Null___Custom_D_TS_DV |  | NORMAL;ALTERNATIVO;CHAVE; | 0;1;2;3 | 1;0;2;3 | ;;; | #FF00FF00;#FF00FF00;#FF00FF00;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_null@ATIVAR___DESATIVADO@ATIVADO___AJPRTN_S_TC_SV |  | Transit;DESATIVADO;ATIVADO;Error | 0;2;1;3 | 2;0;1;3 | ;;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SV | Alarme de Estado em Ponto Telecontrolado SV
DI_null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_DV |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_NORMAL@ALTERNATIVO@CHAVE___NORMAL@ALTERNATIVO@CHAVE___Custom_D_TS_DV |  | NORMAL;ALTERNATIVO;CHAVE; | 0;1;2;3 | 0;1;2;3 | NORMAL;ALTERNATIVO;CHAVE; | #FF00FF00;#FF00FF00;#FF00FF00;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DV | Alarme de Estado em Ponto Telessinalizado DV
DI_CHAVE@NORMAL___CHAVE@NORMAL___Custom___INV_S_TC_DV_F5V |  | Transit;CHAVE;NORMAL;Error | 0;2;1;3 | 2;0;1;3 | ;CHAVE;NORMAL; | #FF000000;#FF00FF00;#FF00FF00;#FF000000 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_null@null@null___ALTERNATIVO@NORMAL@CHAVE___Custom_D_TS_DV_ART1 |  | ALTERNATIVO;NORMAL;CHAVE; | 0;1;2;3 | 0;1;2;3 | ALTERNATIVO;NORMAL;CHAVE; | #FF00FF00;#FF00FF00;#FF00FF00;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DV | Alarme de Estado em Ponto Telessinalizado DV
DI_null@null@null___NORMAL@ALTERNATIVO@CHAVE___Custom_D_TS_DV_SNV3 |  | NORMAL;ALTERNATIVO;CHAVE; | 0;1;2;3 | 1;0;2;3 | NORMAL;ALTERNATIVO;CHAVE; | #FF00FF00;#FF00FF00;#FF00FF00;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DV | Alarme de Estado em Ponto Telessinalizado DV
DI_NORMAL@ALTERNATIVO___NORMAL@ALTERNATIVO___Custom_D_TC_DV_SIV |  | Transit;NORMAL;ALTERNATIVO;Error | 0;1;2;3 | 0;1;2;3 | ;NORMAL;ALTERNATIVO; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_null@ATIVAR___null@null___Custom_S_TC_DV |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_BLOQUEAR@DESBLOQUEAR___BLOQUEADA@NORMAL___Enabled___S_TC_DV_SNV4 |  | Transit;BLOQUEADA;NORMAL;Error | 0;1;2;3 | 2;0;1;3 | ;BLOQUEAR;DESBLOQUEAR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_DESBLOQUEAR@BLOQUEAR___NORMAL@BLOQUEADA___Enabled___admsINV_S_TC_DV |  | Transit;NORMAL;BLOQUEADA;Error | 0;2;1;3 | 2;0;1;3 | ;DESBLOQUEAR;BLOQUEAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_null@ATIVAR___DESATIVADO@ATIVADO___Custom6_S_TC_DV |  | Transit;DESATIVADO;ATIVADO;Error | 0;2;1;3 | 2;0;1;3 | ;;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_null@ATIVAR___DESATIVADO@ATIVADO___Custom6_S_TC_SV |  | Transit;DESATIVADO;ATIVADO;Error | 0;2;1;3 | 2;0;1;3 | ;;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SV | Alarme de Estado em Ponto Telecontrolado SV
DI_null@null@null___ALTERNATIVO@NORMAL@CHAVE___Custom6_D_TS_DV_ART1 |  | ALTERNATIVO;NORMAL;CHAVE; | 0;2;1;3 | 0;1;2;3 | ALTERNATIVO;NORMAL;CHAVE; | #FF00FF00;#FF00FF00;#FF00FF00;#FF000000 | Normal;Normal;Abnormal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DV | Alarme de Estado em Ponto Telessinalizado DV
DI_null@null@null___NORMAL@ALTERNATIVO@CHAVE___Custom6_D_TS_DV_SNV3 |  | NORMAL;ALTERNATIVO;CHAVE; | 2;0;1;3 | 1;0;2;3 | NORMAL;ALTERNATIVO;CHAVE; | #FF00FF00;#FF00FF00;#FF00FF00;#FF000000 | Auto;Auto;Auto;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DV | Alarme de Estado em Ponto Telessinalizado DV
DI_CHAVE@NORMAL___CHAVE@NORMAL___Custom6___INV_S_TC_DV_F5V |  | Transit;CHAVE;NORMAL;Error | 0;1;2;3 | 2;0;1;3 | ;CHAVE;NORMAL; | #FF000000;#FF00FF00;#FF00FF00;#FF000000 | Abnormal;Abnormal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DV | Alarme de Estado em Ponto Telecontrolado DV
DI_RELIGADOR@CHAVE___RELIGADOR@CHAVE___Custom6_S_TC_DVx |  | Transit;RELIGADOR;CHAVE;Error | 0;2;1;3 | 2;0;1;3 | ;RELIGADOR;CHAVE; | #FF000000;#FF00FF00;#FF00FF00;#FF000000 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DVx | Alarme de Estado em Ponto Telecontrolado DVx
null@ATIV_DES___DESATIVADO@ATIVADO___Custom_S_TS_SVx |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SVx | Alarme de Estado em Ponto Telessinalizado SVx
null@null___DESATIVADO@ATIVADO___Custom_S_TS_SVx |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SVx | Alarme de Estado em Ponto Telessinalizado SVx
RELIGADOR@ALTERNATIVO___NORMAL@ALTERNATIVO___Custom_S_TS_DVx |  | Transit;NORMAL;ALTERNATIVO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DVx | Alarme de Estado em Ponto Telessinalizado DVx
DI_null@null___ABERTO@FECHADO___Custom_S_TS_DPx |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DPx | Alarme de Estado em Ponto Telessinalizado DPx
DI_null@null___0@SUCESSO___Custom_S_TS_DVx |  | Transit;0;SUCESSO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DVx | Alarme de Estado em Ponto Telessinalizado DVx
DI_null@ATIVAR___null@null___Custom_S_TC_DVx |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DVx | Alarme de Estado em Ponto Telecontrolado DVx
G1@G2___GRUPO 1@GRUPO 2___Custom_S_TC_SVx |  | Transit;GRUPO 1;GRUPO 2;Error | 0;1;2;3 | 2;0;1;3 | ;G1;G2; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SVx | Alarme de Estado em Ponto Telecontrolado SVx
DI_null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SVx |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SVx | Alarme de Estado em Ponto Telecontrolado SVx
DI_null@ATIVAR___DESATIVADO@ATIVADO___Custom6_S_TC_DVx |  | Transit;DESATIVADO;ATIVADO;Error | 0;2;1;3 | 2;0;1;3 | ;;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DVx | Alarme de Estado em Ponto Telecontrolado DVx
DI_null@null___0@FALHA___Custom_S_TS_DVx |  | Transit;0;FALHA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DVx | Alarme de Estado em Ponto Telessinalizado DVx
DI_null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_DVx |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DVx | Alarme de Estado em Ponto Telecontrolado DVx
DI_null@ATIVAR___DESATIVADO@ATIVADO___Custom6_S_TC_SVx |  | Transit;DESATIVADO;ATIVADO;Error | 0;2;1;3 | 2;0;1;3 | ;;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SVx | Alarme de Estado em Ponto Telecontrolado SVx
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SVx |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SVx | Alarme de Estado em Ponto Telecontrolado SVx
DI_null@null___ABERTO@FECHADO___Custom___INV_S_TS_DPx |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DPx | Alarme de Estado em Ponto Telessinalizado DPx
ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TS_SO |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 0;1;2;3 | ;ABRIR;FECHAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SO | Alarme de Estado em Ponto Telessinalizado SO
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;1;2;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SC | Alarme de Estado em Ponto Telecontrolado SC
ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 0;1;2;3 | ;ABRIR;FECHAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;TRUE | Alarme de Estado em Ponto Telecontrolado SO | Alarme de Estado em Ponto Telecontrolado SO
ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_S_TS_SO |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 2;0;1;3 | ;ABRIR;FECHAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SO | Alarme de Estado em Ponto Telessinalizado SO
ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus___INV_D_TS_SO |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 0;2;1;3 | ;ABRIR;FECHAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SO | Alarme de Estado em Ponto Telessinalizado SO
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus___INV_D_TC_SC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;2;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SC | Alarme de Estado em Ponto Telecontrolado SC
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_S_TC_SC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SC | Alarme de Estado em Ponto Telecontrolado SC
ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_S_TC_SO |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 2;0;1;3 | ;ABRIR;FECHAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SO | Alarme de Estado em Ponto Telecontrolado SO
ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus___INV_S_TS_SO |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 2;1;0;3 | ;ABRIR;FECHAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SO | Alarme de Estado em Ponto Telessinalizado SO
ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus___INV_S_TC_SO |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 2;1;0;3 | ;ABRIR;FECHAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SO | Alarme de Estado em Ponto Telecontrolado SO
ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus___INV_D_TC_SO |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 0;2;1;3 | ;ABRIR;FECHAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SO | Alarme de Estado em Ponto Telecontrolado SO
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus___INV_S_TC_SC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;1;0;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SC | Alarme de Estado em Ponto Telecontrolado SC
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus___INV_D_TS_SC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;2;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SC | Alarme de Estado em Ponto Telessinalizado SC
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_S_TS_SC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SC | Alarme de Estado em Ponto Telessinalizado SC
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus___INV_S_TS_SC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SC | Alarme de Estado em Ponto Telessinalizado SC
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus___INV_D_TC_SC_USO_BC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;2;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SC | Alarme de Estado em Ponto Telecontrolado SC
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus___INV_S_TS_SC_USO_BC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SC | Alarme de Estado em Ponto Telessinalizado SC
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus___INV_S_TC_SC_USO_BC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;1;0;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SC | Alarme de Estado em Ponto Telecontrolado SC
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SC_USO_BC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;1;2;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SC | Alarme de Estado em Ponto Telecontrolado SC
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_S_TC_SC_USO_BC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SC | Alarme de Estado em Ponto Telecontrolado SC
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_S_TS_SC_USO_BC |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SC | Alarme de Estado em Ponto Telessinalizado SC
null@null___NORMAL@INIBIDO___Custom___INV_S_TS_SB |  | Transit;NORMAL;INIBIDO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___DESATIVADO@ATIVADO___Custom_S_TS_SB |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
BLOQUEAR@null___null@null___Custom_S_TC_SB |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;BLOQUEAR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SB | Alarme de Estado em Ponto Telecontrolado SB
null@null___LIGADO@DESLIGADO___Custom___INV_D_TS_SB |  | Transit;LIGADO;DESLIGADO;Error | 0;2;1;3 | 0;2;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NÃO PERMITIDO@PERMITIDO___Custom_S_TS_SB |  | Transit;NÃO PERMITIDO;PERMITIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___DESLIGADO@LIGADO___Custom___INV_D_TS_SB |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;1;2;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@FALTA___Custom___INV_S_TS_SB |  | Transit;NORMAL;FALTA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@FALTA___Custom_S_TS_SB |  | Transit;NORMAL;FALTA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@FALHA___Custom___INV_S_TS_SB |  | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@ATUADO___Custom_S_TS_SB |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB Temporizado | Alarme de Estado em Ponto Telessinalizado SB Temporizado
null@null___NORMAL@FALHA___Custom_S_TS_SB |  | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB |  | Transit;CARREGADA;DESCARREGADA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___LIGADO@DESLIGADO___Custom_S_TS_SB |  | Transit;LIGADO;DESLIGADO;Error | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB Temporizado | Alarme de Estado em Ponto Telessinalizado SB Temporizado
REARMAR@BLOQUEAR___NORMAL@ATUADO___Custom_S_TS_SB |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@ATUADO___Custom___INV_S_TS_SB |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@DEFEITO___Custom_S_TS_SB |  | Transit;NORMAL;DEFEITO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___MANUAL@AUTOMATICO___Custom_S_TS_SB |  | Transit;MANUAL;AUTOMATICO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@REARMAR___NORMAL@ATUADO___Custom_S_TS_SB |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@BLOQUEIO___Custom_S_TS_SB |  | Transit;NORMAL;BLOQUEIO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@OLEO FALHA___Custom_S_TS_SB |  | Transit;NORMAL;OLEO FALHA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@FALTA VCC VCA___Custom_S_TS_SB |  | Transit;NORMAL;FALTA VCC VCA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___LIGADO@DESLIGADO___Custom___INV_S_TS_SB |  | Transit;LIGADO;DESLIGADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___CARREGADA@DESCARREGADA___Custom___INV_S_TS_SB |  | Transit;CARREGADA;DESCARREGADA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TS_SB |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___CARGA@DESCARGA___Custom_S_TS_SB |  | Transit;CARGA;DESCARGA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom___INV_S_TS_SB |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Abnormal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___DESLIGADA@LIGADA___Custom_S_TS_SB |  | Transit;DESLIGADA;LIGADA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@FALHA COM___Custom_S_TS_SB |  | Transit;NORMAL;FALHA COM;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
@___@____S_TS_SB |  | Transit;;;Error | 0;1;2;3 | 0;1;2;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
MANUAL@AUTOMATICO___MANUAL@AUTOMATICO___Custom_S_TS_SB |  | Transit;MANUAL;AUTOMATICO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___AUTOMATICO@MANUAL___Custom_S_TS_SB |  | Transit;AUTOMATICO;MANUAL;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
DI_UNIDIRECIONAL@BIDIRECIONAL___UNIDIRECIONAL@INVERSO___Custom_S_TS_DB |  | Transit;UNIDIRECIONAL;INVERSO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DB | Alarme de Estado em Ponto Telessinalizado DB
DI_null@null___0@EXECUTADO___Custom_S_TS_DB |  | Transit;0;EXECUTADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DB | Alarme de Estado em Ponto Telessinalizado DB
DI_null@null___NORMAL@DEFEITO___Malfunctioning___INV_S_TS_DB |  | Transit;NORMAL;DEFEITO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DB | Alarme de Estado em Ponto Telessinalizado DB
DI_null@null___NORMAL@BLOQUEIO___Custom_S_TS_DB |  | Transit;NORMAL;BLOQUEIO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DB | Alarme de Estado em Ponto Telessinalizado DB
DI_null@null___NORMAL@BAIXA___Custom_S_TS_DB |  | Transit;NORMAL;BAIXA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DB | Alarme de Estado em Ponto Telessinalizado DB
DI_null@null___FALHA@OPERANDO___Custom_S_TS_DB |  | Transit;FALHA;OPERANDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DB | Alarme de Estado em Ponto Telessinalizado DB
DI_null@null___NORMAL@DEFEITO___Custom___INV_S_TS_DB |  | Transit;NORMAL;DEFEITO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DB | Alarme de Estado em Ponto Telessinalizado DB
DI_null@null___NORMAL@ALTA___Custom_S_TS_DB |  | Transit;NORMAL;ALTA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DB | Alarme de Estado em Ponto Telessinalizado DB
DI_null@null___NORMAL@DEFEITO___Custom_S_TS_DB |  | Transit;NORMAL;DEFEITO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DB | Alarme de Estado em Ponto Telessinalizado DB
DI_null@null___NORMAL@ATUADO___Custom_S_TS_DB |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DB | Alarme de Estado em Ponto Telessinalizado DB
DI_null@null___NORMAL@ATUADO___Malfunctioning_S_TS_DB |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DB | Alarme de Estado em Ponto Telessinalizado DB
null@null___NORMAL@ERRO___Custom_S_TS_SB |  | Transit;NORMAL;ERRO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@FALHA___Custom___INV_D_TS_SB |  | Invalido;NORMAL;FALHA;Error | 0;1;2;3 | 0;2;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@FALTA VCA___Custom___INV_S_TS_SB |  | Transit;NORMAL;FALTA VCA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___BLOQUEADA@LIBERADA___Custom_S_TS_SB |  | Transit;BLOQUEADA;LIBERADA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SA |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SA | Alarme de Estado em Ponto Telecontrolado SA
null@null___NORMAL@ATUADO___RelayTrip_S_TS_SB |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@FALHA___RelayTrip_S_TS_SB |  | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
REARMAR@BLOQUEAR___NORMAL@ATUADO___Custom___INV_S_TS_SB |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___FALHA@OPERANDO___Custom_S_TS_DB |  | Transit;FALHA;OPERANDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DB | Alarme de Estado em Ponto Telessinalizado DB
null@null___NORMAL@ATUADO___Custom_S_TS_DB |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DB | Alarme de Estado em Ponto Telessinalizado DB
null@null___NORMAL@NORMAL___Custom_S_TS_SB |  | Transit;NORMAL;NORMAL;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@DEFEITO___Custom___INV_S_TS_SB |  | Transit;NORMAL;DEFEITO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@BAIXA___Custom_S_TS_SB |  | Transit;NORMAL;BAIXA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
REARMAR@BLOQUEAR___NORMAL@ATUADO___Custom_S_TC_SB |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;REARMAR;BLOQUEAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SB | Alarme de Estado em Ponto Telecontrolado SB
DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_D_TC_SB |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;1;2;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Auto | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SB | Alarme de Estado em Ponto Telecontrolado SB
null@null___DEFEITO@NORMAL___Custom_S_TS_SB |  | Transit;DEFEITO;NORMAL;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TS_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SA |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SA | Alarme de Estado em Ponto Telecontrolado SA
null@null___LIGADO@DESLIGADO___Custom_D_TS_SB |  | Transit;LIGADO;DESLIGADO;Error | 0;2;1;3 | 0;1;2;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@BLOQUEIO___Custom___INV_S_TS_SB |  | Transit;NORMAL;BLOQUEIO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@REARMAR___NORMAL@ATUADO___Custom___INV_S_TS_SB |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@DISCREPANCIA___Custom_S_TS_SB |  | Transit;NORMAL;DISCREPANCIA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___ABERTO@FECHADO___Custom___INV_S_TS_SB |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___DESLIGADO@LIGADO___Custom_S_TS_SB |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;DESLIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___DESLIGADO@LIGADO___Custom_S_TS_SB1 |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___FALHA@OPERANDO___Custom_S_TS_SB |  | Transit;FALHA;OPERANDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@FALTA VCA___Custom_S_TS_SB |  | Transit;NORMAL;FALTA VCA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___DESLIGADA@LIGADA___Custom___INV_S_TS_SB |  | Transit;DESLIGADA;LIGADA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___ATIVOU@INIBIU___Custom_S_TS_SB |  | Transit;ATIVOU;INIBIU;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@FALHA___Custom_D_TS_SB |  | Invalido;NORMAL;FALHA;Error | 0;1;2;3 | 0;1;2;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___EXTRAIDO@INSERIDO___Custom_S_TS_SI |  | Transit;EXTRAIDO;INSERIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SI
DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_D_TS_SB |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;1;2;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Abnormal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___EXTRAIDA@INSERIDA___Custom_S_TS_SB |  | Transit;EXTRAIDA;INSERIDA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___DESLIGADO@LIGADO___Custom___INV_S_TS_SB |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;1;0;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___FALHA@OPERANDO___Custom___INV_S_TS_DB |  | Transit;FALHA;OPERANDO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DB | Alarme de Estado em Ponto Telessinalizado DB
null@null___LIBERADO@BLOQUEADO___Custom___INV_S_TS_SB |  | Transit;LIBERADO;BLOQUEADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
EXTRAIR@INSERIR___EXTRAIDO@INSERIDO___Custom___INV_S_TC_SB |  | Transit;EXTRAIDO;INSERIDO;Error | 0;1;2;3 | 2;1;0;3 | ;EXTRAIR;INSERIR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SB | Alarme de Estado em Ponto Telecontrolado SB
null@null___NORMAL@ATUADO___Custom_D_TS_SB |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 0;1;2;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___EXTRAIDO@INSERIDO___Custom___INV_S_TC_SB |  | Transit;EXTRAIDO;INSERIDO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SB | Alarme de Estado em Ponto Telecontrolado SB
DI_UNIDIRECIONAL@BIDIRECIONAL___UNIDIRECIONAL@INVERSO___Custom_S_TS_DBx |  | Transit;FLUXO NORMAL;FLUXO INVERSO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DBx | Alarme de Estado em Ponto Telessinalizado DBx
DI_null@null___NORMAL@DEFEITO___Custom_S_TS_DBx |  | Transit;NORMAL;DEFEITO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DBx | Alarme de Estado em Ponto Telessinalizado DBx
DI_null@null___NORMAL@BLOQUEIO___Custom_S_TS_DBx |  | Transit;NORMAL;BLOQUEIO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DBx | Alarme de Estado em Ponto Telessinalizado DBx
null@null___NORMAL@FALHA___Custom___INV_S_TS_SBx |  | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SBx | Alarme de Estado em Ponto Telessinalizado SBx
DI_null@null___NORMAL@BAIXA___Custom_S_TS_DBx |  | Transit;NORMAL;BAIXA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DBx | Alarme de Estado em Ponto Telessinalizado DBx
DI_null@null___NORMAL@ATUADO___Malfunctioning_S_TS_DBx |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DBx | Alarme de Estado em Ponto Telessinalizado DBx
DI_null@null___NORMAL@ATUADO___Custom_S_TS_DBx |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DBx | Alarme de Estado em Ponto Telessinalizado DBx
null@null___NORMAL@NORMAL___Custom_S_TS_SBx |  | Transit;NORMAL;NORMAL;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SBx | Alarme de Estado em Ponto Telessinalizado SBx
null@null___NORMAL@FALHA___Custom_S_TS_SBx |  | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SBx | Alarme de Estado em Ponto Telessinalizado SBx
DI_null@null___NORMAL@ALTA___Custom_S_TS_DBx |  | Transit;NORMAL;ALTA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DBx | Alarme de Estado em Ponto Telessinalizado DBx
DI_null@null___FALHA@OPERANDO___Custom_S_TS_DBx |  | Transit;FALHA;OPERANDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DBx | Alarme de Estado em Ponto Telessinalizado DBx
DI_null@null___0@EXECUTADO___Custom_S_TS_DBx |  | Transit;0;EXECUTADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DBx | Alarme de Estado em Ponto Telessinalizado DBx
null@null___CARREGADA@DESCARREGADA___Custom__S_TS_SB |  | Transit;CARREGADA;DESCARREGADA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
DI_null@null___FALHA@OK___Custom_S_TS_DBx |  | ;FALHA;OK; | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Abnormal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DBx | Alarme de Estado em Ponto Telessinalizado DBx
ATIVAR@DESATIVAR___null@null___Custom_S_TC_SS |  | Transit;;;Error | 0;1;2;3 | 0;1;2;3 | ;ATIVAR;DESATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
ATIVAR@null___null@null___Custom_S_TC_SS |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;ATIVAR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
AUMENTAR@DIMINUIR___null@null___admsInv__TapIncrement_S_TC_SS |  | Transit;;;Error | 0;2;1;3 | 2;1;0;3 | ;AUMENTAR;DIMINUIR; | #FF000000;#FFFF0000;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@null___DESABILITADO@HABILITADO___HotLineTag_S_TS |  | Error;DESABILITADO;HABILITADO;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
AUMENTAR@DIMINUIR___null@null___INV_TapIncrement_S_TC_SS |  | Transit;;;Error | 0;2;1;3 | 0;1;2;3 | ;AUMENTAR;DIMINUIR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
AUMENTAR@DIMINUIR___null@null___INV_TapIncrement_S_TC_SS_VF |  | Transit;;;Error | 0;1;2;3 | 0;1;2;3 | ;AUMENTAR;DIMINUIR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
AUMENTAR@DIMINUIR___null@null___TapIncrement_S_TC_SS |  | Transit;;;Error | 0;2;1;3 | 2;0;1;3 | ;AUMENTAR;DIMINUIR; | #FF000000;#FFFF0000;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SA |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SB |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV___admsINV_D_TC_SS |  | Invalido;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 0;2;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV___admsINV_S_TC_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@null___LOCAL@REMOTO___Custom___INV_S_TS |  | Transit;LOCAL;REMOTO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom___INV_S_TC_SS |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;1;0;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@null___LOCAL@REMOTO___Custom___INV_S_TS_SS |  | Transit;LOCAL;REMOTO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
DESATIVAR@ATIVAR___NORMAL DESATIVADO@NORMAL ATIVADO___Custom___admsINV_S_TC_SS |  | Transit;NORMAL DESATIVADO;NORMAL ATIVADO;Error | 0;2;1;3 | 2;0;1;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
DESATIVAR@ATIVAR___NORMAL DESATIVADO@NORMAL ATIVADO___Custom___INV___admsINV_S_TC_SS |  | Transit;NORMAL DESATIVADO;NORMAL ATIVADO;Error | 0;2;1;3 | 2;1;0;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV___admsINV_S_TS_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;1;0;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
DESATIVAR@ATIVAR___NORMAL DESATIVADO@NORMAL ATIVADO___Custom___INV_S_TC_SS |  | Transit;NORMAL DESATIVADO;NORMAL ATIVADO;Error | 0;1;2;3 | 2;1;0;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@null___DESABILITADO@HABILITADO___HotLineTag_S_TS_DS |  | Transit;DESABILITADO;HABILITADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DS | Alarme de Estado em Ponto Telessinalizado DS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV_S_TC |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
DESATIVAR@ATIVAR___NORMAL DESATIVADO@NORMAL ATIVADO___Custom_S_TC_SS |  | Transit;NORMAL DESATIVADO;NORMAL ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
DIMINUIR@AUMENTAR___null@null___Custom_S_TC_SS |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;DIMINUIR;AUMENTAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@null___DESABILITADO@HABILITADO___HotLineTag_S_TS_SA |  | Transit;DESABILITADO;HABILITADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___LOCAL@REMOTO___Custom_S_TS |  | Transit;LOCAL;REMOTO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV_S_TC_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV_S_TS_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___NÃO PERMITIDO@PERMITIDO___Custom_S_TS_SS |  | Transit;NÃO PERMITIDO;PERMITIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_D_TC |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
null@null___DESATIVADO@ATIVADO___Custom_S_TS_SS |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___AUTOM DESATIVADO@AUTOM ATIVADO___Custom_S_TS_SS |  | Transit;AUTOM DESATIVADO;AUTOM ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC |  | Error;INCLUIDO;EXCLUIDO;Transit | 0;2;1;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado
null@null___MANUAL DESATIVOU@MANUAL ATIVOU___Custom_S_TS_SS |  | Transit;MANUAL DESATIVOU;MANUAL ATIVOU;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___AUTOM DESATIVOU@AUTOM ATIVOU___Custom_S_TS_SS |  | Transit;AUTOM DESATIVOU;AUTOM ATIVOU;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___BLOQUEADA@LIBERADA___Custom_S_TS_SS |  | Transit;BLOQUEADA;LIBERADA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___LOCAL@REMOTO___Custom_S_TS_SS |  | Transit;LOCAL;REMOTO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_DS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SA |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SA | Alarme de Estado em Ponto Telecontrolado SA
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TS_SA |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TS_SB |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@DISPARADO___Custom_S_TS |  | Transit;NORMAL;DISPARADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
MESTRE@INDIVIDUAL___MESTRE@INDIVIDUAL___Custom_S_TS_SS_SCD |  | ;DESATIVADO;ATIVADO; | 0;1;2;3 | 2;0;1;3 | ;MESTRE;INDIVIDUAL; | #FF00FF00;#FF00FF00;#00FF0000;#00000000 | Normal;Abnormal;Normal;Normal | TRUE;TRUE;TRUE;TRUE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___AUTOMATICO@MANUAL___Custom_S_TS_SS |  | Transit;AUTOMATICO;MANUAL;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___MANUAL DESATIVOU@MANUAL ATIVOU___Custom___INV_S_TS_SS |  | Transit;MANUAL DESATIVOU;MANUAL ATIVOU;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
MANUAL@AUTOMATICO___MANUAL@AUTOMATICO___Custom___INV_D_TC_SS |  | Transit;MANUAL;AUTOMATICO;Error | 0;1;2;3 | 0;2;1;3 | ;MANUAL;AUTOMATICO; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TS_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@MESTRE___DESATIVADO@ATIVADO___Custom_S_TS_SS |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;MESTRE;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___HotLineTag_S_TC_SS |  | Transit;EXCLUIDO;INCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;EXCLUIR;INCLUIR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
DI_BLOQUEAR@MANUAL@AUTOMATICO___BLOQUEADO@MANUAL@AUTOMATICO___Custom_D_TC_DS |  | BLOQUEADO;MANUAL;AUTOMATICO;Erro | 2;0;1;3 | 0;2;1;3 | BLOQUEADO;MANUAL;AUTOMATICO;Erro | #FFFF0000;#FF00FF00;#FF00FF00;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
DI_DIMINUIR@AUMENTAR___null@null___Custom_S_TC_DS |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;DIMINUIR;AUMENTAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
DI_null@ZERAR___NORMAL@ZERADO___Custom_admsINV_S_TC |  | Transit;NORMAL;ZERADO;Error | 0;2;1;3 | 2;0;1;3 | ;;ZERAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
DI_null@null___NORMAL@null___Custom_S_TC_DS |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;RESET ICC;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
DI_null@null___NORMAL@FALTA___Custom_S_TS_DS |  | Transit;NORMAL;FALTA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DS | Alarme de Estado em Ponto Telessinalizado DS
DI_null@null___ABERTO@FECHADO___Custom_S_TS_DS |  | Transit;ABERTO;FECHADO;Error | 0;2;1;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DS | Alarme de Estado em Ponto Telessinalizado DS
DI_UNIDIRECIONAL@BIDIRECIONAL___UNIDIRECIONAL@BIDIRECIONAL___Custom_S_TC_DS |  | Transit;UNIDIRECIONAL;BIDIRECIONAL;Error | 0;1;2;3 | 2;0;1;3 | ;UNIDIRECIONAL;BIDIRECIONAL; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
DI_null@RESET___NORMAL@ATUADO___Custom_S_TC_DS |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;RESET; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
DI_DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_DS |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TS_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___INV___admsINV_S_TC_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___INV___admsINV_S_TS_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;1;0;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___REMOTO@LOCAL___Custom___INV_D_TS_SS |  | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___INV_S_TC |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
null@null___DESABILITADO@HABILITADO___HotLineTag_S_TS_SS |  | Transit;DESABILITADO;HABILITADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
DI_null@null___NORMAL@FALHA___Custom_S_TS_DS |  | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DS | Alarme de Estado em Ponto Telessinalizado DS
DI_null@null___NORMAL@ATUADO___Custom_S_TS_DS |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DS | Alarme de Estado em Ponto Telessinalizado DS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___INV_S_TC_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled_S_TC |  | Error;INCLUIDO;EXCLUIDO;Transit | 0;2;1;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
null@null___REMOTO@LOCAL___Custom___INV_S_TC |  | Error;REMOTO;LOCAL;Transit | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled_S_TC_DS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
null@null___REMOTO@LOCAL___Custom___INV_S_TS |  | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NÃO PERMITIDO@PERMITIDO___Custom___INV_S_TS_SS |  | Transit;NÃO PERMITIDO;PERMITIDO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___NORMAL@ATUADO___Custom_S_TS_SS |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___NORMAL@ATUADO___RelayTrip_S_TS_SS |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___REMOTO@LOCAL___Custom___INV_S_TS_SS |  | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS |  | Transit;BLOQUEADA;LIBERADA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___REMOTO@LOCAL___Custom_D_TS |  | Error;REMOTO;LOCAL;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@BLOQUEIO___Custom_S_TS_SS |  | Transit;NORMAL;BLOQUEIO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
MANUAL@AUTOMATICO___MANUAL@AUTOMATICO___Custom___INV_S_TS_SS |  | Transit;MANUAL;AUTOMATICO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
DI_BLOQUEAR@MANUAL@AUTOMATICO___BLOQUEADO@MANUAL@AUTOMATICO___Custom___admsINV_D_TC_DS |  | BLOQUEADO;MANUAL;AUTOMATICO;Erro | 2;0;1;3 | 0;2;1;3 | BLOQUEADO;MANUAL;AUTOMATICO; | #FFFF0000;#FF00FF00;#FF00FF00;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
null@null___DESABILITOU@HABILITOU___Custom_S_TS |  | Transit;DESABILITOU;HABILITOU;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled_S_TC_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@null___REMOTO@LOCAL___Custom_S_TC |  | Error;REMOTO;LOCAL;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled_S_TS_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
INCLUIR@null___INCLUIDO@EXCLUIDO___Custom_S_TC |  | Error;INCLUIDO;EXCLUIDO;Transit | 0;1;2;3 | 1;0;2;3 | ;INCLUIR;null; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
INCLUIR@null___INCLUIDO@EXCLUIDO___Enabled___INV_S_TC |  | Error;INCLUIDO;EXCLUIDO;Transit | 0;1;2;3 | 1;2;0;3 | ;INCLUIR;null; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
INCLUIR@null___INCLUIDO@EXCLUIDO___Enabled_S_TC |  | Error;INCLUIDO;EXCLUIDO;Transit | 0;1;2;3 | 1;0;2;3 | ;INCLUIR;null; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
INCLUIR@null___null@null___ReclosingEnabled___admsINV_D_TC_SS |  | Transit;;;Error | 0;2;1;3 | 2;0;1;3 | ;INCLUIR;; | #FF000000;#FFA9A9A9;#FFA9A9A9;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@EXCLUIR___null@null___ReclosingEnabled___admsINV_D_TC_SS |  | Transit;;;Error | 0;2;1;3 | 2;0;1;3 | ;;EXCLUIR; | #FF000000;#FFA9A9A9;#FFA9A9A9;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@null___DESABILITOU@HABILITOU___Custom_S_TS_SS |  | Transit;DESABILITOU;HABILITOU;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___INCLUIDO@EXCLUIDO___Custom___INV_S_TC |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
null@null___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@null___LIGADO@DESLIGADO___Custom_S_TS_SS |  | Transit;LIGADO;DESLIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___INCLUIDO@EXCLUIDO___Custom___INV_S_TS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___INCLUIDO@EXCLUIDO___Custom___INV_S_TS_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___INCLUIDO@EXCLUIDO___Custom_S_TC |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado | Alarme de Estado em Ponto Telecontrolado
null@null___NORMAL@DISPARADO___Custom_S_TS_SA |  | Transit;NORMAL;DISPARADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___INCLUIDO@EXCLUIDO___Custom_S_TC_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@null___NORMAL@FALTA___Custom_S_TS_SS |  | Transit;NORMAL;FALTA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@INDIVIDUAL___DESATIVADO@ATIVADO___Custom_S_TS_SS |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
MESTRE@INDIVIDUAL@COMANDO___MESTRE@INDIVIDUAL@COMANDO___Custom___admsINV_D_TS_SS |  | MESTRE;INDIVIDUAL;COMANDADO;ERROR | 2;0;1;3 | 0;2;1;3 | MESTRE;INDIVIDUAL;COMANDO; | #FFFF0000;#FF00FF00;#FF00FF00;#FF000000 | Normal;Abnormal;Abnormal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___INCLUIDO@EXCLUIDO___Custom_S_TS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___NORMAL@DISPARADO___Custom_S_TS_SP |  | Transit;NORMAL;DISPARADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SP | Alarme de Estado em Ponto Telessinalizado SP
MESTRE@INDIVIDUAL@COMANDO___MESTRE@INDIVIDUAL@COMANDO___Custom___admsINV_D_TC_SS |  | MESTRE;INDIVIDUAL;COMANDADO;Error | 0;1;2;3 | 1;2;4;8 | MESTRE;INDIVIDUAL;COMANDADO; | #FFFF0000;#FF00FF00;#FF00FF00;#FF000000 | Normal;Abnormal;Abnormal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
AUMENTAR@DIMINUIR___null@null___TapIncrement_S_TS_SS |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___REMOTO@LOCAL___Custom_S_TS |  | Error;REMOTO;LOCAL;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___INCLUIDO@EXCLUIDO___Custom_S_TS_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SB |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___REMOTO@LOCAL___Custom_S_TS_DS |  | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DS | Alarme de Estado em Ponto Telessinalizado DS
null@null___INCLUIDO@EXCLUIDO___Enabled___INV_S_TS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
MANUAL@AUTOMATICO___MANUAL@AUTOMATICO___Custom___INV_S_TC_SS |  | Transit;MANUAL;AUTOMATICO;Error | 0;1;2;3 | 2;1;0;3 | ;MANUAL;AUTOMATICO; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TS_SS |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
AUTOMATICO@MANUAL___AUTOMATICO@MANUAL___Custom___INV___admsINV_S_TS_SS |  | Transit;AUTOMATICO;MANUAL;Error | 0;2;1;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___MANUAL@AUTOMATICO___Custom_S_TS_SS |  | Transit;MANUAL;AUTOMATICO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___REMOTO@LOCAL___Custom_S_TS_SS |  | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
DESBLOQUEAR@BLOQUEAR___NORMAL@BLOQUEADA___Enabled___admsINV_S_TS_SS |  | Transit;NORMAL;BLOQUEADA;Error | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
MANUAL@AUTOMATICO___MANUAL@AUTOMATICO___Custom_S_TC_SS |  | Transit;MANUAL;AUTOMATICO;Error | 0;1;2;3 | 2;0;1;3 | ;MANUAL;AUTOMATICO; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado
RELIGADOR@ALTERNATIVO___null@null___Custom_S_TS_SS |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___INCLUIDO@EXCLUIDO___Enabled_S_TS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
DI_DESBLOQUEAR@BLOQUEAR___DESBLOQUEADO@BLOQUEADO___Custom___admsINV_D_TC_DS |  | Erro;DESBLOQUEADO;BLOQUEADO;Transit | 0;2;1;3 | 3;0;1;2 | ;;BLOQUEAR; | #FF000000;#FFFF0000;#FF00FF00;#FF00FF00 | Abnormal;Normal;Normal;Normal | FALSE;TRUE;TRUE;TRUE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
DI_MANUAL@AUTOMATICO___MANUAL@AUTOMATICO___Custom___admsINV_D_TC_DS |  | Erro;MANUAL;AUTOMATICO;Transit | 0;1;2;3 | 3;1;2;0 | ;MANUAL;AUTOMATICO; | #FF000000;#FF00FF00;#FF00FF00;#FFFF0000 | Abnormal;Normal;Normal;Normal | FALSE;TRUE;TRUE;TRUE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
null@ATIVAR___DESATIVADO@ATIVADO___Custom___INV_S_TC_SS |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;1;0;3 | ;;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
AUTOMATICO@MANUAL___AUTOMATICO@MANUAL___Custom___admsINV_S_TS_SS |  | Transit;AUTOMATICO;MANUAL;Error | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
RELIGADOR@ALTERNATIVO___null@null___Custom_D_TC_SS |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;RELIGADOR;ALTERNATIVO; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@null___REMOTO@LOCAL___Local___INV_S_TS |  | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___INCLUIDO@EXCLUIDO___Enabled_S_TS_SB |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB | Alarme de Estado em Ponto Telessinalizado SB
null@null___LIGADO@DESLIGADO___Custom___INV_S_TS_SS |  | Transit;LIGADO;DESLIGADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom___INV_S_TS_SS |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
DESATIVAR@ATIVAR___NORMAL DESATIVADO@NORMAL ATIVADO___Custom___admsINV_S_TS_SS |  | Transit;NORMAL DESATIVADO;NORMAL ATIVADO;Error | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___PARALELO@INDIVIDUAL___Custom_S_TS |  | Transit;PARALELO;INDIVIDUAL;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@ATIVAR___DESATIVADO@ATIVADO___Custom___INV_S_TC_SSx |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;1;0;3 | ;;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SSx | Alarme de Estado em Ponto Telecontrolado SSx
RELIGADOR@CHAVE___RELIGADOR@CHAVE___Custom_D_TC_SS |  | Transit;RELIGADOR;CHAVE;Error | 0;1;2;3 | 0;1;2;3 | ;RELIGADOR;CHAVE; | #FF000000;#FF00FF00;#FF00FF00;#FF000000 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@null___AUTOM DESATIVADO@AUTOM ATIVOU___Custom___INV_S_TS_SS |  | Transit;AUTOM DESATIVADO;AUTOM ATIVOU;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
@___@____S_TS_SS |  | Transit;;;Error | 0;1;2;3 | 0;1;2;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___AUTOM DESATIVADO@AUTOM ATIVOU___Custom_S_TS_SS |  | Transit;AUTOM DESATIVADO;AUTOM ATIVOU;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___DESABILITOU@HABILITOU___Custom_S_TS_SV |  | Transit;DESABILITOU;HABILITOU;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SV | Alarme de Estado em Ponto Telessinalizado SV
MESTRE@INDIVIDUAL@COMANDADO___MESTRE@INDIVIDUAL@COMANDADO___Custom___D_TS_SS |  | MESTRE;INDIVIDUAL;COMANDADO;Error | 0;1;2;3 | 0;2;1;3 | ;MESTRE;INDIVIDUAL; | #FFFF0000;#FFFF0000;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___INCLUIDO@EXCLUIDO___Enabled_S_TS_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
PARALELO@INDIVID___PARALELO@INDIVIDUAL___Custom_S_TS_SS |  | Transit;PARALELO;INDIVIDUAL;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
MESTRE@INDIVIDUAL@COMANDO___MESTRE@INDIVIDUAL@COMANDO___Custom___INV___admsINV_D_TS_SS |  | MESTRE;INDIVIDUAL;COMANDADO; | 2;0;1;3 | 0;2;1;3 | MESTRE;INDIVIDUAL;COMANDO; | #FFFF0000;#FF00FF00;#FF00FF00;#FF000000 | Normal;Abnormal;Abnormal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
MESTRE@INDIVIDUAL@COMANDADO___MESTRE@INDIVIDUAL@COMANDADO___Custom___INV___D_TS_SS |  | INDIVIDUAL;MESTRE;COMANDADO;Error | 0;1;2;3 | 0;1;2;3 | ;MESTRE;INDIVIDUAL; | #FFFF0000;#FFFF0000;#FFFF0000;#FFA9A9A9 | Normal;Normal;Abnormal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@null___HABILITADO@DESABILITADO___Custom_S_TS |  | Error;HABILITADO;DESABILITADO;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@ATIVAR___NORMAL DESATIVADO@NORMAL ATIVADO___Custom___admsINV_S_TC_SS |  | Transit;NORMAL DESATIVADO;NORMAL ATIVADO;Error | 0;2;1;3 | 2;0;1;3 | ;;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@DESABILITAR___null@null__Enabled_S_TC_SS |  | ;;;Error | 0;1;2;3 | 2;0;1;3 | ;;DESABILITAR; | #00000000;#00000000;#00000000;#FFA9A9A9 | Normal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@INDIVIDUAL___DESATIVADO@ATIVADO___Custom_S_TC_SS |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;INDIVIDUAL; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@MESTRE___DESATIVADO@ATIVADO___Custom_S_TC_SS |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;MESTRE; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@null___AUTOMATICO@MANUAL___Custom___INV_S_TS_SS |  | Transit;AUTOMATICO;MANUAL;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null@null___MESTRE@INDIVIDUAL@COMANDO___Custom___admsINV_D_TS_SS |  | MESTRE;COMANDADO;INDIVIDUAL;Error | 0;1;2;3 | 0;1;2;3 | MESTRE;;; | #FFFF0000;#FFFF0000;#FFFF0000;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
MESTRE@INDIVIDUAL@COMANDO___null@null@null___Custom___admsINV_D_TC_SS |  | ;;; | 0;1;2;3 | 1;2;4;8 | MESTRE;INDIVIDUAL;COMANDADO; | #FFFF0000;#FFFF0000;#FFFF0000;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@null___LIBERADO@BLOQUEADO___Custom___INV_S_TS_SS |  | Transit;LIBERADO;BLOQUEADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___OPERANDO@BLOQUEADO___Custom_S_TS_SS |  | Transit;OPERANDO;BLOQUEADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___HABILITADO@DESABILITADO___Custom_S_TS_SA |  | Transit;HABILITADO;DESABILITADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA | Alarme de Estado em Ponto Telessinalizado SA
null@null___EXTRAIDA@INSERIDA___Custom_S_TS_SS |  | Transit;EXTRAIDA;INSERIDA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
G1@G2___DESATIVADO@ATIVADO___Custom_S_TS_SS |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___INCLUIDO@EXCLUIDO___INV___Local_S_TS_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___DESATIVADA@ATIVADA___Custom_S_TS_SS |  | Transit;DESATIVADA;ATIVADA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___INCLUIDO@EXCLUIDO___Local___INV_S_TS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___REMOTO@LOCAL___Local_S_TS |  | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null@null___INDIVIDUAL@MESTRE@COMANDADO___Custom___admsINV__CDCO_D_TC_SS |  | INDIVIDUAL;MESTRE;COMANDADO;Error | 0;1;2;3 | 0;1;2;3 | ;;; | #FFFF0000;#FFFF0000;#FFFF0000;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;TRUE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
INDIVIDUAL@MESTRE___null@null___Custom___admsINV__CDCO_D_TC_SS_CTRL |  | ;;; | 0;1;2;3 | 1;2;4;8 | INDIVIDUAL;MESTRE;; | #FF000000;#FF000000;#FF000000;#FF000000 | Normal;Normal;Normal;Normal | TRUE;TRUE;TRUE;TRUE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
RELIGADOR@ALTERNATIVO___null@null___Custom_S_TC_SS |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;RELIGADOR;ALTERNATIVO; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
DI_UNIDIRECIONAL@BIDIRECIONAL___UNIDIRECIONAL@BIDIRECIONAL___Custom_S_TC_DSx |  | Transit;UNIDIRECIONAL;BIDIRECIONAL;Error | 0;1;2;3 | 2;0;1;3 | ;UNIDIRECIONAL;BIDIRECIONAL; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DSx | Alarme de Estado em Ponto Telecontrolado DSx
DI_null@RESET___NORMAL@ATUADO___Custom_S_TC_DSx |  | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;RESET; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DSx | Alarme de Estado em Ponto Telecontrolado DSx
DI_null@null___NORMAL@FALTA___Custom_S_TS_DSx |  | Transit;NORMAL;FALTA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DSx | Alarme de Estado em Ponto Telessinalizado DSx
G1@G2___DESATIVADO@ATIVADO___Custom_S_TS_SSx |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SSx | Alarme de Estado em Ponto Telessinalizado SSx
DI_MANUAL@AUTOMATICO___MANUAL@AUTOMATICO___Custom___admsINV_D_TC_DSx |  | Erro;MANUAL;AUTOMATICO;Transit | 0;1;2;3 | 3;1;2;0 | ;MANUAL;AUTOMATICO; | #FF000000;#FF00FF00;#FF00FF00;#FFFF0000 | Abnormal;Normal;Normal;Normal | FALSE;TRUE;TRUE;TRUE | Alarme de Estado em Ponto Telecontrolado DSx | Alarme de Estado em Ponto Telecontrolado DSx
DI_DIMINUIR@AUMENTAR___null@null___Custom_S_TC_DSx |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;DIMINUIR;AUMENTAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DSx | Alarme de Estado em Ponto Telecontrolado DSx
DI_DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_DSx |  | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DSx | Alarme de Estado em Ponto Telecontrolado DSx
DI_null@null___ABERTO@FECHADO___Custom_S_TS_DSx |  | Transit;ABERTO;FECHADO;Error | 0;2;1;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DSx | Alarme de Estado em Ponto Telessinalizado DSx
AUMENTAR@DIMINUIR___null@null___TapIncrement_Sinv_TC_SS |  | Transit;;;Error | 0;2;1;3 | 0;2;1;3 | ;AUMENTAR;DIMINUIR; | #FF000000;#FFFF0000;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
MESTRE@INDIVIDUAL@COMANDADO___MESTRE@INDIVIDUAL@COMANDADO___Custom___INV___2414_TS_SS |  | INDIVIDUAL;MESTRE;COMANDADO;Error | 0;1;2;3 | 0;2;4;8 | MESTRE;INDIVIDUAL;; | #FFFF0000;#FFFF0000;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
INDIVIDUAL@MESTRE___null@null___Custom___admsINV__CDCO_D_TC_SS_CTRL_vnb |  | INDIVIDUAL; | 0;1 | 0;1 | MESTRE;INDIVIDUAL | #FF000000;#FF000000 | Normal;Normal | TRUE;TRUE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
RELIGADOR@CHAVE___RELIGADOR@CHAVE___Custom___S_TC_SS |  | Transit;RELIGADOR;CHAVE;Error | 0;1;2;3 | 2;0;1;3 | ;RELIGADOR;CHAVE; | #FF000000;#FF00FF00;#FF00FF00;#FF000000 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
DI_null@null___NORMAL@FALHA___Custom_Sinv_TS_DS |  | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado DS | Alarme de Estado em Ponto Telessinalizado DS
PARALELO@INDIVIDUAL___PARALELO@INDIVIDUAL___Custom_S_TS_SS |  | Transit;INDIVIDUAL;PARALELO;Error | 0;1;2;3 | 2;0;1;3 | ;INDIVIDUAL;PARALELO; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
RESET@null___null@null___Custom_S_TC_SS |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;RESET;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
TROCA@null___null@null___Custom_S_TC_SS |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;TROCA;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
DI_null@null___UNIDIRECIONAL@BIDIRECIONAL___Custom_S_TC_DS | CMD - UNIDIRECIONAL/BIDIRECIONAL | ;;; | 0;1;2;3 | 2;0;1;3 | ;UNIDIRECIONAL;BIDIRECIONAL; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
DI_null@null___UNIDIRECIONAL@BIDIRECIONALBLOQ___Custom_S_TC_DS | CMD - BIDIRECIONAL BLOQ. I=0 | ;;;Error | 0;1;2;3 | 2;0;1;3 | ;UNIDIRECIONAL;BIDIRECIONAL BLOQ. I=0; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
DI_null@null___UNIDIRECIONAL@COGERACAO___Custom_S_TC_DS | CMD - COGERAÇÃO | ;;;Error | 0;1;2;3 | 2;0;1;3 | ;UNIDIRECIONAL;COGERAÇÃO; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
DI_null@null___UNIDIRECIONAL@BIDIRECIONALI=0___Custom_S_TC_DS | CMD - BIDIRECIONAL I=0 | ;;;Error | 0;1;2;3 | 2;0;1;3 | ;UNIDIRECIONAL;BIDIRECIONAL I=0; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DS | Alarme de Estado em Ponto Telecontrolado DS
DI_null@RESETRUA___null@null___Custom_S_TC_DSx | RESET RUA | ;;; | 0;1;2;3 | 2;0;1;3 | ;;RESET RUA; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado DSx | Alarme de Estado em Ponto Telecontrolado DSx
ZERAR@null___null@null___Custom_S_TC_SS |  | Transit;;;Error | 0;1;2;3 | 2;0;1;3 | ;ZERAR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS | Alarme de Estado em Ponto Telecontrolado SS
null@null___INCLUIDO@EXCLUIDO___Local___INV_S_TS_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___INCLUIDO@EXCLUIDO___Local_D_TS |  | Error;INCLUIDO;EXCLUIDO;Transit | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___INCLUIDO@EXCLUIDO___Local_D_TS_SS |  | Invalido;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 0;1;2;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___INCLUIDO@EXCLUIDO___Local_S_TS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TS_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___INCLUIDO@EXCLUIDO___ReclosingEnabled___INV___admsINV_S_TS_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;1;0;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___INCLUIDO@EXCLUIDO___ReclosingEnabled___INV_S_TS |  | Error;INCLUIDO;EXCLUIDO;Transit | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___INCLUIDO@EXCLUIDO___ReclosingEnabled___INV_S_TS_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___INCLUIDO@EXCLUIDO___ReclosingEnabled_S_TS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado | Alarme de Estado em Ponto Telessinalizado
null@null___INCLUIDO@EXCLUIDO___ReclosingEnabled_S_TS_SS |  | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_S_TC_ST |  | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado ST | Alarme de Estado em Ponto Telecontrolado ST
ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_S_TC_ST |  | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 2;0;1;3 | ;ABRIR;FECHAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado ST | Alarme de Estado em Ponto Telecontrolado ST
Switch.SwitchStatus |  | Error;ABERTO;FECHADO;Transit | 0;1;2;3 | 0;1;2;3 | ;ABRIR;FECHAR; | #00000000;#FF00FF00;#FFFF0000;#00000000 | Abnormal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;TRUE
RegulatingControl.Enabled |  | Error;DISABLED;ENABLED;Transit | 0;1;2;3 | 0;1;2;3 | ;DISABLE;ENABLE; | #00000000;#00FF0000;#0000FF00;#00000000 | Normal;Normal;Normal;Normal | TRUE;TRUE;TRUE;TRUE
Fuse.SwitchStatus |  | Error;ABERTO;FECHADO;Transit | 0;1;2;3 | 0;1;2;3 | ;ABRIR;FECHAR; | #00000000;#0000FF00;#00FF0000;#00000000 | Abnormal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;TRUE
ProtectionEquipment.Enabled |  | Error;DISABLED;ENABLED;Transit | 0;1;2;3 | 0;1;2;3 | ;DISABLE;ENABLE; | #00000000;#00FF0000;#0000FF00;#00000000 | Normal;Normal;Normal;Normal | TRUE;TRUE;TRUE;TRUE
ProtectionEquipment.ReclosingEnabled |  | Error;DISABLED;ENABLED;Transit | 0;1;2;3 | 0;1;2;3 | ;DISABLE;ENABLE; | #00000000;#00FF0000;#0000FF00;#00000000 | Normal;Normal;Normal;Normal | TRUE;TRUE;TRUE;TRUE
Reclosing.Enabled |  | Error;DESABILITADO;HABILITADO;Transit | 0;1;2;3 | 0;1;2;3 | ;DESABILITAR;HABILITAR; | #00000000;#00FF0000;#0000FF00;#00000000 | Normal;Normal;Normal;Normal | TRUE;TRUE;TRUE;TRUE
TapIncrement |  | Error;;;Transit | 0;1;2;3 | 0;1;2;3 | ;DIMINUIR;AUMENTAR; | #00000000;#00FF0000;#0000FF00;#00000000 | Normal;Normal;Normal;Normal | TRUE;TRUE;TRUE;TRUE
RegulatingControl.Refresh |  | Error;Refresh;HeartBeat;Transit | 0;1;2;3 | 0;1;2;3 | ;Refresh;HeartBeat; | #00000000;#00FF0000;#0000FF00;#00000000 | Normal;Normal;Normal;Normal | TRUE;TRUE;TRUE;TRUE
FaultIndicator.FaultStatus |  | Error;Open;Closed;Transit | 0;1;2;3 | 0;1;2;3 | ;Open;Close; | #00000000;#0000FF00;#00FF0000;#00000000 | Abnormal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;TRUE
DI_ANTENA |  | OMNI;OMNI AMP;DIRECIONAL;DIREC AMP;RESERVADO;INDEFINIDO | 0;1;2;3;4;5 | 0;1;2;3;4;5 | OMNI;OMNI AMP;DIRECIONAL;DIREC AMP;RESERVADO;INDEFINIDO | #00A9A9A9;#00A9A9A9;#00A9A9A9;#00A9A9A9;#00A9A9A9;#00A9A9A9 | Normal;Normal;Normal;Normal;Normal;Normal | FALSE;FALSE;FALSE;FALSE;FALSE;FALSE
DI_MODEM |  | ATIVA HORIZON;UTW;V2COM;ROBUSTEL;SILVER SPRING;ATIVA;VELP;DWF;INDEFINIDO | 0;1;2;3;4;5;6;7;8 | 0;1;2;3;4;5;6;7;8 | ATIVA HORIZON;UTW;V2COM;ROBUSTEL;SILVER SPRING;ATIVA;VELP;DWF;INDEFINIDO | #00A9A9A9;#00A9A9A9;#00A9A9A9;#00A9A9A9;#00A9A9A9;#00A9A9A9;#00A9A9A9;#00A9A9A9;#00000000 | Normal;Normal;Normal;Normal;Normal;Normal;Normal;Normal;Normal | FALSE;FALSE;FALSE;FALSE;FALSE;FALSE;FALSE;FALSE;TRUE
null@null___HABILITADO@DESABILITADO___Custom_S_TS_SS |  | Transit;HABILITADO;DESABILITADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
Reclosing.Enabled.Manual |  | Error;INCLUIDO;EXCLUIDO;Transit | 0;2;1;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #00000000;#00FF0000;#0000FF00;#00000000 | Normal;Normal;Normal;Normal | TRUE;TRUE;TRUE;TRUE
DI_RT_OPER_FLUXO |  | BIDIRECIONAL;UNIDIRECIONAL;BIDIRECIONAL BLOQ. (I=0);;COGERAÇÃO;;;;BIDIRECIONAL;;;;;;; | 0;1;2;3;4;5;6;7;8;9;10;11;12;13;14;15 | 0;1;2;3;4;5;6;7;8;9;10;11;12;13;14;15 | ;;;;;;;;;;;;;;; | #00A9A9A9;#00A9A9A9;#00A9A9A9;#00A9A9A9;#00A9A9A9;#00A9A9A9;#00A9A9A9;#00A9A9A9;#00000000;#00000000;#00000000;#00000000;#00000000;#00000000;#00000000;#00000000 | Normal;Normal;Normal;Normal;Normal;Abnormal;Abnormal;Abnormal;Normal;Abnormal;Abnormal;Abnormal;Abnormal;Abnormal;Abnormal;Abnormal | TRUE;TRUE;TRUE;FALSE;TRUE;FALSE;FALSE;FALSE;TRUE;TRUE;TRUE;TRUE;TRUE;TRUE;TRUE;TRUE
null@null___23kV@13,8kV___Custom_S_TS |  | Error;23kV;13,8kV;Transit | 0;1;2;3 | 2;1;0;3 | ;;; | #00000000;#FF00FF00;#FFFF0000;#00000000 | Abnormal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;TRUE
null@null___138kV@69kV___Custom_S_TS |  | Error;138kV;69kV;Transit | 0;1;2;3 | 2;1;0;3 | ;;; | #00000000;#FF00FF00;#FFFF0000;#00000000 | Abnormal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;TRUE
null@null___REMOTO@LOCAL__Local_S_TS_SS |  | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS | Alarme de Estado em Ponto Telessinalizado SS
null@null___DESABILITADO@HABILITADO___Custom_S_TS_SV |  | Transit;DESABILITADO;HABILITADO;Error | 0;1;2;3 | 2;0;1;3 | Alarme de Estado em Ponto Telessinalizado DV | Severidade 5 |  |  |  | Alarme de Estado em Ponto Telessinalizado SV
null@COMANDADO___DESATIVADO@ATIVADO___Custom_S_TC_SS |  | Transit;DESABILITADO;HABILITADO;Error | 0;1;2;3 | 2;0;1;3 | [5 empty] | Alarme de Estado em Ponto Telecontrolado SS
Note on A1: User definable name of the message mapping.
Note on B1: Optional string describing an alternate name of the message mapping.
Note on C1: List of strings associated with possible values, in the same order as Values. An empty string denotes that the corresponding value cannot occur as read from the field (i.e. may be used only for commanding). Elements in list are separated using ";" character, e.g. Transit; Open; Close; Error
Note on D1: List of possible values that the signal can obtain. Elements in list are separated using ";" character, e.g. 0; 1; 2; 3.
Note on E1: Integer values in SCADA which correspond to DMS values in values attribute. SCADA plugin does the translation in both directions. If empty, no translation is perfomed, and SCADA values are translated as-is. Elements in list are separated using ";" character, e.g. 0; 1; 2; 3.
Note on F1: List of strings associated with possible values, used for commanding, in the same order as Values. If the value is not commandable, an empty string is used. Elements in list are separated using ";" character, e.g. ;ON;OFF;
Note on G1: Color associated with the state. Color is represented as six digits hexadecimal RGB value, where the first two hexa numbers represent Red color, following Green and Blue. Additionally, FF or 00 value added prior to RGB format determines whether color is used by default or not, respectively. Examples: #00FF0000 - represents Red color; color is NOT used by default #FF00FF00 - represents Green color; color IS used by default #FF0000FF - represents Blue color; color IS used by default
Note on H1: For each value in the list, specifies if it is treated as abnormal. Abnormal values are listed in the Abnormal Summary, and an alarm might be rised, depending on Severity attribute. Supported values are: Normal Abnormal Auto
Note on I1: Specifies whether every possible value can be entered as manual override.
Note on J1: List of references to an alarm/event catalogs assigned to this message mapping setting. Elements in list are seperated using ";" character.

## MANUT_DiscreteSignals
SINAL | DESCRIÇÃO NOVA | SIGNAL TYPE | TYPE SEVERIDADE | FUNÇÃO | EA | PE | Sinal | Coordenada
79_L | 79 - RELIGAMENTO LOCAL | Custom | PROT | Transit;NORMAL;ATUADO;Error | CAX; PMI |  | CLA_AL11_52-3_79_L; BGA_AL11_52-9_79_L | 34502; 34672
J124 | AJUSTE PARA AL1 OU AL2 OU AL4 | Custom | ALARMES PREDIAIS/VF/GRUPO | Transit;DESABILITADO;HABILITADO;Error | VAI | Confirmar o funcionamento. | ENA_TRF2_24-2_J124 | 632
SF6I | INIBIR TRIP POR BAIXA PRESSAO SF6 | Custom | FUNCÕES/43/PARALELISMO | Transit;NORMAL;INIBIDO;Error | VAI | Confirmar o funcionamento. Função inibe o trip por SF6? | ETB_AL11_52-13_SF6I; ETB_AL21_52-12_SF6I | 508; 547
PARALELO | PARALELO | Parallel | FUNCÕES/43/PARALELISMO | Transit;DESATIVADO;ATIVADO;Error | VAI | Confirmar o funcionamento; ponto diferente do padrão. | VNB_TR1_TR1_PARALELO | 266
R90E | RELE 90 EMERGENCIAL | Custom | FUNCÕES/43/PARALELISMO | Transit;INCLUIDO;EXCLUIDO;Error | SMA; ALE | Confirmar o funcionamento. | SSP_TR1_TR1_R90E; SNA_TR2AT_TR2AT_R90E; SGB_TR1AT_52-2_R90E; SFA_TR2AT_TR2AT_R90E; IQB_TR1_TR1_R90E | 170; 847; 664; 152; 652
90PI | RELE PARALELISMO | Custom | FUNCÕES/43/PARALELISMO | Transit;PARALELO;INDIVIDUAL;Error | SLE | Confirmar o funcionamento. | GTA_TR3_TR3_90PI | 9320
FCMC | FALHA COMUNICACAO MULTIMEDIDOR | Custom | FALHAS FCOM/VCA/VCC | Transit;NORMAL;FALHA;Error | VAI | Confirmar o funcionamento. | ENA_TR1_TR1_FCMC; VNB_TR2_TR2_FCMC | 103; 270
M69C | DJAUX 69 PAINEL | Custom | FALHAS FCOM/VCA/VCC | Transit;LIGADO;DESLIGADO;Error | Automação | Alterar o nome do sinal |  | OK
MDP1 | DJAUX TP BARRA P1 PAINEL | Custom | FALHAS FCOM/VCA/VCC | Transit;LIGADO;DESLIGADO;Error | Automação | Alterar o nome do sinal |  | OK
MDP2 | DJAUX TP BARRA P2 PAINEL | Custom | FALHAS FCOM/VCA/VCC | Transit;LIGADO;DESLIGADO;Error | Automação | Alterar o nome do sinal |  | OK
MDTP1 | DJAUX TP PATIO BARRAP1 | Custom | FALHAS FCOM/VCA/VCC | Transit;LIGADO;DESLIGADO;Error | Automação | Alterar o nome do sinal |  | OK
MDTP2 | DJAUX TP PATIO BARRAP2 | Custom | FALHAS FCOM/VCA/VCC | Transit;LIGADO;DESLIGADO;Error | Automação | Alterar o nome do sinal |  | OK
MINC | MINC | Custom | FUNCÕES/43/PARALELISMO | Transit;NORMAL;ATUADO;Error | PFU | Confirmar o funcionamento. | LT800_KECENG_89-2_MINC | 26
VF1I | CHAVE VF1 PRIORITARIO | Custom | FUNCÕES/43/PARALELISMO | Transit;INCLUIDO;EXCLUIDO;Error | CAX | Confirmar o funcionamento. | CXC_TR1_TR1_VF2I; FEL_TR1_TR1_VF2I | 22225; 573
VF1L | CHAVE VF1 POSICAO LOCAL | Custom | FUNCÕES/43/PARALELISMO | Transit;REMOTO;LOCAL;Error | CAX | Confirmar o funcionamento. | VAC_TR1_TR1_VF1L | 16080
VF2I | CHAVE VF2 PRIORITARIO | Custom | FUNCÕES/43/PARALELISMO | Transit;INCLUIDO;EXCLUIDO;Error | CAX | Confirmar o funcionamento. | CXC_TR1_TR1_VF1I; FEL_TR1_TR1_VF1I | 22224; 572
VF2L | CHAVE VF2 POSICAO LOCAL | Custom | FUNCÕES/43/PARALELISMO | Transit;REMOTO;LOCAL;Error | CAX | Confirmar o funcionamento. | TCO_TR2_TR2_VF2L | 16081
50CD | 50 - SOBRECORRENTE CDC | RelayTrip | PROT | Transit;NORMAL;ATUADO;Error | CAX; ALE | Confirmar o funcionamento. | GMB_TR1_TR1_A_50CD; URI_TR1_TR1_50CD | 471; 227
MTRF | MODULO TRANSFERIDO | Custom | FUNCÕES/43/PARALELISMO | Transit;NORMAL;ATUADO;Error | SMA; PFU | Confirmar o funcionamento. | SMB_LTFXA_LTFXA_MTRF; THA_LTKSM_LTKSM_MTRF | 443; 316
CMDE | PROPRIEDADE DO COMANDO | Custom | ALARMES PREDIAIS/VF/GRUPO | Transit;CEEE;RGE;Error | Automação | Alterar o MM | ERN

## Manut_AnalogSignals
SINAL | DESCRIÇÃO NOVA | Pendência
BIHI | TENSAO DE REFERENCIA ALTA AUXILIAR | Confirmar o funcionamento.
BILO | TENSAO DE REFERENCIA BAIXA AUXILIAR | Confirmar o funcionamento.
I2 |  | Confirmar o funcionamento.
PCVA |  | Confirmar o funcionamento.
RTC |  | Confirmar o funcionamento.
VABL |  | trocar pra v
VAUX |  | trocar pra vca
VCA | TENSAO CORRENTE ALTERNADA | trocar para V, nos TSA
VCC1 | TENSAO CORRENTE CONTINUA 1 | ver na UTR
VCC2 | TENSAO CORRENTE CONTINUA 2
FUGA | FUGA A TERRA | Confirmar o funcionamento.