## Info
File name: | Telemetry Data Template File
File created: | 06/26/2026 10:15:57
User: | rgeprod\rafael.weber
Location(s): | FREDERICO WESTPHALEN 2 (Subestação)
Document Number:
Revision:
Legend
DMSMatchingTemplateInfo | Sheet containing supported ADMS types and attributes
RTUs | Configuration of Remote Terminal Units, Terminal Servers and Modem Banks
CommLInks | Configuration of TCP/IP based communication links
Modem | Modem configuration
ModemLinks | Configuration of Modem Links
DiscreteSignals | Configuration of discrete signals attached to a discrete type of remote points
AnalolgSignals | Configuration of analog signals attached to analog or rate (accumulator) type of remote points
Discrete-AnalogSignalTypes | Configuration of discrete signals attached to a analog or rate (accumulator) point type of remote poins (e.g. tap position signal types)
ScanGroups | Scan group configuration typical for serial based protocols (DNP3, VanComm, Series5...)
ICCP_RemoteControlCenters | Configuration of ICCP Remote Control Centers
ICCP_DataSetTransferSet | Configuration of ICCP Data Sets Transfer Sets
ICCP_NetworkConfigurationInfo | Configuration of network and security parameters for communication with the RCC
ServerDiscreteSignals | List of discrete signals served to the remote control center or SCADA master
ServerAnalogSignals | List of analog signals served to the remote control center or SCADA master
Note Catalog | Configuration of applicable types of note cataogs
Alarm Catalog | Configuration of Alarm catalog e.g. alarm text, alarm cause, priority (severity)
Event Catalog | Configuration of Event catalog e.g. event text, priority (severity)
Alarm Limits | Configuration of Alarm Limits for a specific measurement type, including reasonability checks and references to return-to-normal and high/low alarm limit catalogs
Limit Sets | Configuration of applicable limit sets and deadbands associated with an Alarm Limit
Tag Catalog | Configuration of applicable types of tags within the utility
Message Mappings | Message Mapping configuration - mapping of each possible discrete signal value (state) to a text message and alarm catalog associated with the state
DOM Catalog | Device operation monitoring - specifies criteria for alarm generation based on monitoring of cumulative switchgear operations

## DMSMatchingTemplateInfo (hidden)
YesNo | TrueFalse | AlarmEventCause | AlarmSeverity | MeasurementType | TagSemantics | DMSType | DiscreteSignalType | AbnormalState | PhaseCode | WindingType | SignalDirection | AnalogSignalType | UnitSymbol | FlowDirection | RemoteUnitType | TimeZone | RedundancyBehaviorType | SOEGroup | ProtocolTypeConitel | ScanTypeConitel | RemotePointType | OperateType | DiscreteInputTypeConitel | SectionConitel | DiscreteOutputDataTypeConitel | CommandTypeConitel | FunctionCodeConitel | AnalogInputTypeConitel | DeadbandDataType | DNP3Scan | TimeSyncMode |  | DNP3ConfirmMode | DNP3ObjectGroup | DNP3InputType | DNP3OutputType | ControlCode | DNP3Variation | DNP3SlaveEvent | DNP3SlaveDiscreteInputDataType | DNP3SlaveClassData | DNP3SlaveAnalogInputDataType | DNP3SlaveCounterDataType | IccpVersion | IccpBlocks | ConnectionRole | ServiceRole | AuthenticationMode | DstsType | IccpScope | IccpDataValueType | IECCounterInterrogationType | IECClockSyncMode | OctetSize | IEC101LinkMode | IEC101ConfirmMode | ModemCallType | ModemCommandType | BaudRate | IECDiscreteType | IECCommandQualifier | CommandState | IECAnalogType | IECRateType | ScanTypeMD3 | DiscreteInputModuleTypeMD3 | DiscreteInputDataTypeMD3 | DiscreteOutputTypeMD3 | DiscreteOutputDataTypeMD3 | CmdTypeMD3 | AnalogInputModuleTypeMD3 | AnalogInputDataTypeMD3 | AnalogOutputTypeMD3 | ModbusByteOrder | ModbusTransmissionMode | ModbusRegisterType | ModbusDiscreteOutputType | ModbusAnalogType | SecurityCodeSeries5 | ScanTypeSeries5 | DiscreteTypeSeries5 | ScanTypeVanComm | DiscreteInputTypeVanComm | DiscreteOutputTypeVanComm | AnalogTypeVanComm | CalculationParamType | InputTriggerType | RemoteUnitType | OperateType | RemotePointType | RemotePointType | RemotePointType | SignalDirection | MeasurementType | RemotePointType | OperateType | DNP3InputType | RemotePointType | OperateType | RemotePointType | SignalDirection | OperateType | MeasurementType | RemotePointType | OperateType | RemotePointType | OperateType | RemoteUnitType | RemoteUnitType | RemotePointType | IccpDataValueType | RemotePointType | IccpDataValueType | RemotePointType | SignalDirection | IccpDataValueType | MeasurementType | IccpDataValueType | IccpDataValueType | RemoteUnitType | OctetSize | OctetSize | OctetSize | OctetSize | BaudRate | OctetSize | RemotePointType | IECDiscreteType | IECDiscreteType | RemotePointType | IECAnalogType | RemotePointType | SignalDirection | MeasurementType | IECAnalogType | RemotePointType | IECDiscreteType | IECDiscreteType | RemotePointType | IECAnalogType | RemoteUnitType | OctetSize | RemoteUnitType | RemotePointType | IECDiscreteType | IECDiscreteType | RemotePointType | IECAnalogType | IECAnalogType | RemotePointType | SignalDirection | IECAnalogType | IECAnalogType | MeasurementType | RemotePointType | RemotePointType | RemotePointType | SignalDirection | MeasurementType | RemotePointType | RemotePointType | ModbusRegisterType | RemotePointType | SignalDirection | ModbusRegisterType | MeasurementType | RemotePointType | RemotePointType | RemotePointType | SignalDirection | MeasurementType | RemotePointType | RemotePointType | RemotePointType | SignalDirection | MeasurementType | CalculationParamType
No | TRUE | ApplicationAlarm | Severidade 16 | Unitless | DoNotOperatorClose | SUBSTATION | Custom | Normal | Unknown | None | Read | Custom | Default | Undirected | RTU | (UTC-12:00) International Date Line West | PrioritizeCostFactor | Group07 | Conitel2025 | Scan | Analog | DirectOperate | SingleBit | SectionA | SingleCoord | TripClose | Trip | TwelveBitSignedMagnitude | Int32 | Class0 | LAN | None | Never | BinaryInput | SingleBit | SingleCoord | Nul | Empty | WithoutTime | BinaryInputPackedFormat | Class1 | Int32WithFlag | Int32WithFlag | Version1996 | Block1 | Outgoing | Client | None | ManualRBE | Vcc | Unknown | CounterRead | SyncOnly | OneOctet | Unbalanced | Sometimes | DialOut | BaudRate | B100 | IECNone | UseDefault | On | IECShortNormalized | IECRateTimestamp | AnalogUnconditional | DigitalInputModuleDCM | SingleBit | RaiseLower | SingleCoord | Trip | AnalogInputModule | TwelveBitSignedMagnitude | AOMType | LittleEndian | TCP | Coil | SingleCoord | Short | LRC8bit | ExceptionScan | SingleCoord | AnalogScan | MomentaryStatus | SingleCoord | Signed | Bool | None | RTU | DirectOperate | Status | Analog | Analog | Read | Discrete | Status | DirectOperate | SingleBit | Analog | DirectOperate | Analog | Read | DirectOperate | Discrete | Status | DirectOperate | Analog | DirectOperate | ControlCenter | ControlCenter | Status | State | Analog | Real | Analog | Read | Real | Discrete | State | Real | RTU | OneOctet | OneOctet | OneOctet | OneOctet | B9600 | OneOctet | Status | IECSingleBit | IECSingleBit | Analog | IECShortNormalized | Analog | Read | Discrete | IECShortNormalized | Status | IECSingleBit | IECSingleBit | Analog | IECShortNormalized | RTU | OneOctet | RTU | Status | IECSingleBit | IECSingleBit | Analog | IECShortNormalized | IECShortNormalized | Analog | Read | IECShortNormalized | IECShortNormalized | Discrete | Status | Analog | Analog | Read | Discrete | Status | Analog | Coil | Analog | Read | Coil | Discrete | Status | Analog | Analog | Read | Discrete | Status | Analog | Analog | Read | Discrete | Bool
Yes | FALSE | DiscreteState | Severidade 15 | Voltage | DoNotOperatorOpen | BAY | SwitchStatus | Abnormal | N | Primary | Write | MeasuredValue | kV | Forward | SubstationControlSystem | (UTC-11:00) Coordinated Universal Time-11 | SwitchOnFirstRTUFailure | Group8F | Baker | SOEScan | Status | SelectWithValue | SingleBitMCDA | SectionB | TwoCoord | RaiseLower | Close | TwelveBitSignedTwoComplement | Int16 | Class0123 | Serial | Diagnostic | Sometimes | BinaryInputEvent | DoubleBit | MultiCoord | PulseOn | Int32 | WithAbsoluteTime | BinaryInputWithFlags | Class2 | Int16WithFlag | Int16WithFlag | Version2000 | Block2 | Incoming | Server | Mace | ManualInterval | Icc | Real | CounterFreezeWithReset | LoadDelay | TwoOctets | Balanced | Always | DialIn | TelephoneNumber | B200 | IECSingleBit | ShortPulse | Off | IECShortScaled | IECRateShortTimestamp | AnalogDeltaScan | DigitalInputModule | MultiBit | POMType | TwoCoord | Close | FloatingPointModule | TwelveBitSignedTwoComplement | InputPointControl | BigEndian | ASCII | DiscreteInput | TwoCoords | UShort | CRC16bit | StatusScan | DoubleCoord | AllStatusScan | MemoryStatus | DoubleCoord | Unsigned | Int | Value | TerminalServer | AutoSelectWithValue |  | Counter | Counter |  |  |  | AutoSelectWithValue | DoubleBit | Counter | AutoSelectWithValue | Counter |  | AutoSelectWithValue |  |  | AutoSelectWithValue | Counter | AutoSelectWithValue | DSTS | DSTS |  | Discrete | Counter | RealQuality | Counter |  | RealQuality |  | Discrete | RealQuality | ModemBank | TwoOctets | TwoOctets | TwoOctets | TwoOctets |  | TwoOctets |  | IECDoubleBit | IECDoubleBit | Counter | IECShortScaled | Counter |  |  | IECShortScaled |  | IECDoubleBit | IECDoubleBit | Counter | IECShortScaled |  | TwoOctets |  |  | IECDoubleBit | IECDoubleBit | Counter | IECShortScaled | IECShortScaled | Counter |  | IECShortScaled | IECShortScaled |  |  | Counter | Counter |  |  |  | Counter | HoldingRegister | Counter |  | HoldingRegister |  |  | Counter | Counter |  |  |  | Counter | Counter |  |  | Int
|  | AnalogHigh | Severidade 14 | Current | DoNotAutoClose | BASEVOLTAGE | Local | Auto | C | Secondary | ReadWrite | ControlSetValue | V | Reverse | ControlCenter | (UTC-10:00) Aleutian Islands | SwitchOnAllRTUFailure |  |  |  | Counter | SelectWithoutValue | MultiBit |  | MultiCoord |  | Raise | SixBitUnsigned | Float | ScanTable |  | Type2 | Always | DoubleBinaryInput | MultiCoord |  | PulseOff | Int16 | WithRelativeTime | DoubleBitBinaryInputPackedFormat | Class3 | Int32WithoutFlag | Int32WithoutFlag |  | Block3 |  | Peer | SSL | AutoAll |  | State | CounterFreezeWithoutReset | DelayAcq | ThreeOctets |  | Never |  | Command | B300 | IECDoubleBit | LongPulse |  | IECFloat | IECRate | DigitalCOSTimeTagged |  | MultiBitBCD | DOMType | MultiCoord | Raise | AnalogInputModuleDCM | TwelveBitUnsigned | FloatingPointOP |  | RTU | InputRegister | MultiCoord | Int32 |  | AnalogScan | MultiCoord | MomentaryStatusScan | LatchingStatus | MultiCoord |  | Double | Flags | [8 empty] | DirectNoAck | MultiCoord |  | DirectNoAck |  |  | DirectNoAck |  |  | DirectNoAck |  | DirectNoAck |  |  |  | StateSupp |  | RealQualityTimeTag |  |  | RealQualityTimeTag |  | StateSupp | RealQualityTimeTag | TerminalServer |  |  |  | Undefined |  | Undefined |  | IECStepPosition | IECStepPosition |  | IECFloat |  |  |  | IECFloat |  | IECStepPosition | IECStepPosition |  | IECFloat |  |  |  |  | IECStepPosition | IECStepPosition |  | IECFloat | IECFloat |  |  | IECFloat | IECFloat | [23 empty] | Double
|  | AnalogLow | Severidade 13 | ActivePower | DoNotAutoOpen | NETWORKINFO | OperationCount |  | CN | Tertiary |  | ControlBandwidth | mV |  | IED | (UTC-10:00) Hawaii | CostFactorWithAvailabilityCheck |  |  |  | SmartMeter | AutoSelectWithValue | MultiBitBCD |  |  |  | Lower | TwelveBitUnsigned |  |  |  | Type1 |  | DoubleBinaryInputEvent | MultiCoordBCD |  | LatchOn | Float |  | DoubleBitBinaryInputWithFlags | None | Int16WithoutFlag | Int16WithoutFlag |  | Block4 |  |  |  | AutoReal |  | Discrete | CounterReset |  | Undefined |  |  |  | Delay | B600 | IECStepPosition | Persistent |  | IECShortNormalizedTimestamp |  | DigitalUnconditional |  |  | InputPointControl |  | Lower |  | FloatingPoint |  |  |  | HoldingRegister |  | UInt32 |  | SetpointScan |  | MemoryStatusScan | Multibit | RaiseLower |  | String | Timestamp | [23 empty] | StateQuality |  | RealExtended |  |  | RealExtended |  | StateQuality | RealExtended | [8 empty] | IECBitstring | IECBitstring | [7 empty] | IECBitstring | IECBitstring | [6 empty] | IECBitstring | IECBitstring |  | IECShortNormalizedTimestamp | IECShortNormalizedTimestamp |  |  | IECShortNormalizedTimestamp | IECShortNormalizedTimestamp | [23 empty] | String
|  | AnalogCreep | Severidade 12 | ReactivePower | WarnOnOpen | FAULTINDICATORC | TapPosition |  | B |  |  | ControlDelay | A |  | SmartMeter | (UTC-09:30) Marquesas Islands | [5 empty] | AutoSelectWithoutValue | SingleBitMCDB |  |  |  |  | RemoteStatusByte | [5 empty] | BinaryOutput |  |  | LatchOff | Double |  |  |  | FloatWithFlag |  |  | Block5 |  |  |  | AutoDiscrete |  | StateSupp | [7 empty] | B1200 | IECBitstring |  |  | IECShortScaledTimestamp |  | FloatingPointUnconditional |  |  |  |  | PointOff |  | FifteenBitSignedMagnitude | [5 empty] | Float |  |  |  | LatchingStatusScan |  |  |  | ASignal | AlarmLimit | [23 empty] | DiscreteQuality |  | RealQualityTimeTagExtended |  |  | RealQualityTimeTagExtended |  | DiscreteQuality | RealQualityTimeTagExtended | [8 empty] | IECMultiBit | IECMultiBit | [7 empty] | IECMultiBit | IECMultiBit | [6 empty] | IECMultiBit | IECMultiBit |  | IECShortScaledTimestamp | IECShortScaledTimestamp |  |  | IECShortScaledTimestamp | IECShortScaledTimestamp | [23 empty] | ASignal
|  | AnalogGrowth | Severidade 11 | CosPhi | WarnOnClose | POWERTRC2W | TapIncrement |  | BN |  |  | ControlSubDelay | kA |  | ModemBank | (UTC-09:00) Alaska | [5 empty] | DirectNoAck | SingleBitMCDC | [10 empty] | BinaryOutputEvent |  |  | ClosePulseOn |  |  |  |  | DoubleWithFlag | [6 empty] | AutoState |  | RealQuality | [7 empty] | B2400 | IECMultiBit |  |  | IECFloatTimestamp |  | FloatingPointDelta |  |  |  |  | PointOn |  | FifteenBitSignedTwoComplement | [9 empty] | StatusExceptionScan |  |  |  | DSignal | [24 empty] | StateSuppQuality | [6 empty] | StateSuppQuality | [10 empty] | IECSingleBitTimestamp | [7 empty] | IECSingleBitTimestamp | [7 empty] | IECSingleBitTimestamp | IECSingleBitTimestamp |  | IECFloatTimestamp | IECFloatTimestamp |  |  | IECFloatTimestamp | IECFloatTimestamp | [23 empty] | DSignal
|  | AnalogFlatline | Severidade 10 | Frequency | Predicted | POWERTRC3W | Enabled |  | BC |  |  | ControlLimitHigh | mA |  | DSTS | (UTC-09:00) Coordinated Universal Time-09 | [6 empty] | DoubleBitMCDA | [10 empty] | BinaryCounter |  |  | TripPulseOn | [13 empty] | StateQuality | [7 empty] | B4800 | IECSingleBitTimestamp |  |  | IECShortNormalizedNoQuality |  | FloatingPointCOSTimeTagged |  |  |  |  | SinglePoleOperate |  | FifteenBitUnsigned | [9 empty] | ReadInternalStatus |  |  |  | BoolArray | [24 empty] | StateQualityTimeTag | [6 empty] | StateQualityTimeTag | [10 empty] | IECDoubleBitTimestamp | [7 empty] | IECDoubleBitTimestamp | [7 empty] | IECDoubleBitTimestamp | IECDoubleBitTimestamp |  | IECShortNormalizedNoQuality | IECShortNormalizedNoQuality |  |  | IECShortNormalizedNoQuality | IECShortNormalizedNoQuality | [23 empty] | ASignalArray
|  | AnalogDrop | Severidade 9 | Temperature | Confirmed | SYNCMACHINEC | LoadBonus |  | BCN |  |  | ControlLimitLow | kW |  | TerminalServer | (UTC-08:00) Baja California | [6 empty] | DoubleBitMCDB | [10 empty] | FrozenCounter |  |  | ClosePulseOff | [13 empty] | DiscreteQuality | [7 empty] | B9600 | IECDoubleBitTimestamp |  |  | IECShortNormalizedShortTimestamp | [6 empty] | CustomPayload0 | [11 empty] | ClearInternalStatus |  |  |  | IntArray | [24 empty] | DiscreteQualityTimeTag | [6 empty] | DiscreteQualityTimeTag | [10 empty] | IECStepPositionTimestamp | [7 empty] | IECStepPositionTimestamp | [7 empty] | IECStepPositionTimestamp | IECStepPositionTimestamp | [30 empty] | DSignalArray
|  | AnalogRTN | Severidade 8 | ActiveEnergy | OutOfOrder | CAPACITORC | ReclosingEnabled |  | A |  |  | ControlSlopeReal | MW |  |  | (UTC-08:00) Coordinated Universal Time-08 | [6 empty] | DoubleBitMCDC | [10 empty] | CounterEvent |  |  | TripPulseOff | [13 empty] | StateSuppQuality | [7 empty] | B19200 | IECStepPositionTimestamp |  |  | IECShortScaledShortTimestamp | [6 empty] | CustomPayload1 | [11 empty] | StatusAcknowledge |  |  |  | DoubleArray | [24 empty] | StateSuppQualityTimeTag | [6 empty] | StateSuppQualityTimeTag | [10 empty] | IECBitstringTimestamp | [7 empty] | IECBitstringTimestamp | [7 empty] | IECBitstringTimestamp | IECBitstringTimestamp
|  | TransformerOverload | Severidade 7 | ReactiveEnergy | Malfunctioning | PETERSENCOILC | ControlActiveSetting |  | AN |  |  | ControlSlopeImag | W |  |  | (UTC-08:00) Pacific Time (US & Canada) | [17 empty] | FrozenCounterEvent |  |  | CloseLatchOn | [13 empty] | RealQualityTimeTag | [7 empty] | B38400 | IECBitstringTimestamp |  |  | IECFloatShortTimestamp | [6 empty] | CustomPayload32 | [15 empty] | StringArray | [24 empty] | StateExtended | [6 empty] | StateExtended | [10 empty] | IECMultiBitTimestamp | [7 empty] | IECMultiBitTimestamp | [7 empty] | IECMultiBitTimestamp | IECMultiBitTimestamp
|  | LineOverload | Severidade 6 | ApparentPower | AlarmInhibit | JUMPERC | Refresh |  | AC |  |  | FaultRecorder | kVAr |  |  | (UTC-07:00) Arizona | [17 empty] | AnalogInput |  |  | TripLatchOn | [13 empty] | StateQualityTimeTag | [7 empty] | B56000 | IECMultiBitTimestamp | [25 empty] | ASignalArray | [24 empty] | DiscreteExtended | [6 empty] | DiscreteExtended | [10 empty] | IECSingleBitShortTimestamp | [7 empty] | IECSingleBitShortTimestamp
|  | AnalogReasonability | Severidade 5 | VoltageAngle | AlarmAudioInhibit | DISCONNECTORC | VoltageIndex1 |  | ACN |  |  | WeatherData | MVAr |  |  | (UTC-07:00) La Paz, Mazatlan | [17 empty] | FrozenAnalogInput |  |  | CloseLatchOff | [13 empty] | DiscreteQualityTimeTag | [7 empty] | B64000 | IECSingleBitShortTimestamp | [25 empty] | DSignalArray | [24 empty] | StateSuppExtended | [6 empty] | StateSuppExtended | [10 empty] | IECDoubleBitShortTimestamp | [7 empty] | IECDoubleBitShortTimestamp
|  | SystemAlarm | Severidade 4 | Status | StopProcessing | SECTIONALIZERC | VoltageIndex2 |  | AB |  |  | BellwetherMeter | VAr |  |  | (UTC-07:00) Mountain Time (US & Canada) | [17 empty] | AnalogInputEvent |  |  | TripLatchOff | [13 empty] | StateSuppQualityTimeTag | [8 empty] | IECDoubleBitShortTimestamp | [50 empty] | StateQualityTimeTagExtended | [6 empty] | StateQualityTimeTagExtended | [10 empty] | IECStepPositionShortTimestamp | [7 empty] | IECStepPositionShortTimestamp
|  | DOMAlarm | Severidade 3 | Discrete | PointTest | LOADBREAKERC | LoadFlowEnabled |  | ABN |  |  | RecloseDelay | Hz |  |  | (UTC-07:00) Yukon | [17 empty] | FrozenAnalogInputEvent | [16 empty] | RealExtended | [8 empty] | IECStepPositionShortTimestamp | [50 empty] | DiscreteQualityTimeTagExtended | [6 empty] | DiscreteQualityTimeTagExtended | [10 empty] | IECBitstringShortTimestamp | [7 empty] | IECBitstringShortTimestamp
|  |  | Severidade 2 | SwitchStatus | DOMInhibit | FUSEC | FaultStatus |  | ABC |  |  | FaultCurrentSub | Hz_s |  |  | (UTC-06:00) Central America | [17 empty] | AnalogOutputStatus | [16 empty] | StateExtended | [8 empty] | IECBitstringShortTimestamp | [50 empty] | StateSuppQualityTimeTagExtended | [6 empty] | StateSuppQualityTimeTagExtended | [10 empty] | IECMultiBitShortTimestamp | [7 empty] | IECMultiBitShortTimestamp
|  |  | Severidade 1 | Time |  | BREAKERC | RecloserLockout |  | ABCN |  |  | FaultAngleSub | C |  |  | (UTC-06:00) Central Time (US & Canada) | [17 empty] | AnalogOutputEvent | [16 empty] | DiscreteExtended | [8 empty] | IECMultiBitShortTimestamp
|  |  |  | Humidity |  | CONNODE | FanStatus |  |  |  |  | FaultCurrentTrans | F |  |  | (UTC-06:00) Easter Island | [17 empty] | ClassObjects | [16 empty] | StateSuppExtended
|  |  |  | WindSpeed |  | BUSNODE | OilPumpStatus |  |  |  |  | FaultAngleTrans | kWh |  |  | (UTC-06:00) Guadalajara, Mexico City, Monterrey | [17 empty] | Authentication | [16 empty] | RealQualityTimeTagExtended
|  |  |  | FeelsLike |  | POTENTIALTR | HotLineTag |  |  |  |  | DeltaVoltage | MWh |  |  | (UTC-06:00) Saskatchewan | [17 empty] | SecureDNP3Statistics | [16 empty] | StateQualityTimeTagExtended
|  |  |  | SunshineMinutes |  | SURGEPROTECTOR | MaxOpCount |  |  |  |  | MaxRampUp | kVArh |  |  | (UTC-05:00) Bogota, Lima, Quito, Rio Branco | [17 empty] | SecureDNP3StatisticsEvent | [16 empty] | DiscreteQualityTimeTagExtended
|  |  |  | SkyCover |  | GNDIMPEDANCE | HourlyOpCount |  |  |  |  | MaxRampDown | MVArh |  |  | (UTC-05:00) Chetumal | [34 empty] | StateSuppQualityTimeTagExtended
|  |  |  | Length |  | CONSUMER | DailyOpCount |  |  |  |  | Charged | kVA |  |  | (UTC-05:00) Eastern Time (US & Canada)
|  |  |  | CrossSection |  | SOURCE | MonthlyOpCount |  |  |  |  | EnergyPrice | MVA |  |  | (UTC-05:00) Haiti
|  |  |  | Impedance |  | CAPACITOR | UnderFrequencyAlarm |  |  |  |  | GenerationPrice | VA |  |  | (UTC-05:00) Havana
|  |  |  | Admittance |  | SYNCMACHINE | Forward |  |  |  |  | PInjectedReal | deg |  |  | (UTC-05:00) Indiana (East)
|  |  |  | ImpedancePerLength |  | CURRENTTR | RelayTrip |  |  |  |  | QInjectedReal | dms |  |  | (UTC-05:00) Turks and Caicos
|  |  |  | AdmittancePerLength |  | INDUCTOR | ReverseMode |  |  |  |  | PInjectedEq | sec |  |  | (UTC-04:00) Atlantic Time (Canada)
|  |  |  | Percent |  | FAULTINDICATOR | SourceStatus |  |  |  |  | QInjectedEq | min |  |  | (UTC-04:00) Caracas
|  |  |  | Money |  | SECTION | Parallel |  |  |  |  | CalculatedVoltage | hour |  |  | (UTC-04:00) Cuiaba
|  |  |  | RelativeVoltage |  | TAPCHANGER | PowerOn |  |  |  |  | PMin | km_h |  |  | (UTC-04:00) Georgetown, La Paz, Manaus, San Juan
|  |  |  | Insolation |  | POWERTR2W | Manageable |  |  |  |  | PMax | mph |  |  | (UTC-04:00) Santiago
|  |  |  | CurrentAngle |  | POWERTR3W | Malfunctioning |  |  |  |  | QMin | m_s |  |  | (UTC-03:30) Newfoundland
|  |  |  | RotationSpeed |  | ASIGNAL | WeightingFactor |  |  |  |  | QMax | m |  |  | (UTC-03:00) Araguaina
|  |  |  | Mass |  | DSIGNAL | TemporaryFault |  |  |  |  | SShortCircuit | km |  |  | (UTC-03:00) Asuncion
|  |  |  | FailureRate |  | GROUNDNODE | GroupStatus |  |  |  |  | X1R1Ratio | ft |  |  | (UTC-03:00) Brasilia
|  |  |  | SoilTemperature |  | REMOTEPOINT | Custom1 |  |  |  |  | RWard | yd |  |  | (UTC-03:00) Cayenne, Fortaleza
|  |  |  | OilTemperature |  | CURVE | Custom2 |  |  |  |  | XWard | mi |  |  | (UTC-03:00) City of Buenos Aires
|  |  |  | HotSpotTemperature |  | PETERSENCOIL | Custom3 |  |  |  |  | R1ShortCircuit | mm2 |  |  | (UTC-03:00) Montevideo
|  |  |  | AbsoluteDateTime |  | COMPSWITCH | Custom4 |  |  |  |  | X1ShortCircuit | kcmil |  |  | (UTC-03:00) Punta Arenas
|  |  |  | LatLong |  | PCELL | Custom5 |  |  |  |  | R2ShortCircuit | AWG |  |  | (UTC-03:00) Saint Pierre and Miquelon
|  |  |  | Date |  | REGCTRL | Custom6 |  |  |  |  | X2ShortCircuit | Ohm |  |  | (UTC-03:00) Salvador
|  |  |  | LongDistanceLength |  | CTRLLIMIT | Custom7 |  |  |  |  | R0ShortCircuit | S |  |  | (UTC-02:00) Coordinated Universal Time-02
|  |  |  | Precipitation |  | DAYTYPE | Custom8 |  |  |  |  | X0ShortCircuit | mS |  |  | (UTC-02:00) Greenland
|  |  |  | WindDirection |  | SEASON | Custom9 |  |  |  |  | Custom1 | uS |  |  | (UTC-02:00) Mid-Atlantic - Old
|  |  |  | ThermalPower |  | LOADRSPCHAR | Custom10 |  |  |  |  | Custom2 | Ohm_km |  |  | (UTC-01:00) Azores
|  |  |  | Emission |  | LOADPICKUPCHAR | [5 empty] | Custom3 | Ohm_m |  |  | (UTC-01:00) Cabo Verde Is.
[6 empty] | LOADGROUP | [5 empty] | Custom4 | Ohm_kft |  |  | (UTC) Coordinated Universal Time
[6 empty] | SECTIONALIZER | [5 empty] | Custom5 | Ohm_mi |  |  | (UTC+00:00) Dublin, Edinburgh, Lisbon, London
[6 empty] | RECLSTAGE | [6 empty] | S_km |  |  | (UTC+00:00) Monrovia, Reykjavik
[6 empty] | PROTECTEQP | [6 empty] | S_m |  |  | (UTC+00:00) Sao Tome
[6 empty] | RELSTAGE | [6 empty] | S_kft |  |  | (UTC+01:00) Casablanca
[6 empty] | RTUC | [6 empty] | S_mi |  |  | (UTC+01:00) Amsterdam, Berlin, Bern, Rome, Stockholm, Vienna
[6 empty] | REGION | [6 empty] | uS_km |  |  | (UTC+01:00) Belgrade, Bratislava, Budapest, Ljubljana, Prague
[6 empty] | SUBREGION | [6 empty] | uS_m |  |  | (UTC+01:00) Brussels, Copenhagen, Madrid, Paris
[6 empty] | FEEDER | [6 empty] | uS_kft |  |  | (UTC+01:00) Sarajevo, Skopje, Warsaw, Zagreb
[6 empty] | FEEDEROBJECT | [6 empty] | uS_mi |  |  | (UTC+01:00) West Central Africa
[6 empty] | ASYNCMACHINE | [6 empty] | Percent |  |  | (UTC+02:00) Athens, Bucharest
[6 empty] | ASYNCMACHINEC | [6 empty] | pu |  |  | (UTC+02:00) Beirut
[6 empty] | WIREC | [6 empty] | base120 |  |  | (UTC+02:00) Cairo
[6 empty] | CABLEC | [6 empty] | currency |  |  | (UTC+02:00) Chisinau
[6 empty] | LINEGEOMETRYC | [6 empty] | W_m2 |  |  | (UTC+02:00) Gaza, Hebron
[6 empty] | WEATHERREGION | [6 empty] | rpm |  |  | (UTC+02:00) Harare, Pretoria
[6 empty] | TRANSFORMERAREA | [6 empty] | kg |  |  | (UTC+02:00) Helsinki, Kyiv, Riga, Sofia, Tallinn, Vilnius
[6 empty] | CONSUMERCONTRACT | [6 empty] | ton |  |  | (UTC+02:00) Jerusalem
[6 empty] | JUMPER | [6 empty] | lb |  |  | (UTC+02:00) Juba
[6 empty] | LOADBREAKSWITCH | [6 empty] | perYear |  |  | (UTC+02:00) Kaliningrad
[6 empty] | BREAKER | [6 empty] | mm_h |  |  | (UTC+02:00) Khartoum
[6 empty] | CBLTHERMMODEL | [6 empty] | in_h |  |  | (UTC+02:00) Tripoli
[6 empty] | ARRAYSIGNAL | [6 empty] | MBTU_h |  |  | (UTC+02:00) Windhoek
[6 empty] | INTERLOCKINGITEM | [6 empty] | kcal_h |  |  | (UTC+03:00) Amman
[6 empty] | INTERLOCKINGSCHEME | [6 empty] | kJ_h |  |  | (UTC+03:00) Baghdad
[6 empty] | CTRLSETT | [6 empty] | MJ_h |  |  | (UTC+03:00) Damascus
[6 empty] | FEEDERSEGMENT | [6 empty] | khour |  |  | (UTC+03:00) Istanbul
[6 empty] | FUSE | [6 empty] | kg_h |  |  | (UTC+03:00) Kuwait, Riyadh
[6 empty] | DISCONNECTOR | [6 empty] | g_h |  |  | (UTC+03:00) Minsk
[6 empty] | TAGC | [9 empty] | (UTC+03:00) Moscow, St. Petersburg
[6 empty] | MOBILEOBJECT | [9 empty] | (UTC+03:00) Nairobi
[6 empty] | AORGROUP | [9 empty] | (UTC+03:00) Volgograd
[6 empty] | CUSTOMGROUP | [9 empty] | (UTC+03:30) Tehran
[6 empty] | INTSCHEDULE | [9 empty] | (UTC+04:00) Abu Dhabi, Muscat
[6 empty] | ANNUALSCHEDULE | [9 empty] | (UTC+04:00) Astrakhan, Ulyanovsk
[6 empty] | LVNETWORK | [9 empty] | (UTC+04:00) Baku
[6 empty] | LVFEEDER | [9 empty] | (UTC+04:00) Izhevsk, Samara
[6 empty] | TEMPSCHEDULE | [9 empty] | (UTC+04:00) Port Louis
[6 empty] | CURRENTTRC | [9 empty] | (UTC+04:00) Saratov
[6 empty] | POTENTIALTRC | [9 empty] | (UTC+04:00) Tbilisi
[6 empty] | MESSAGEMAPPING | [9 empty] | (UTC+04:00) Yerevan
[6 empty] | SEASONDAYSCH | [9 empty] | (UTC+04:30) Kabul
[6 empty] | CUSTOMTYPE | [9 empty] | (UTC+05:00) Ashgabat, Tashkent
[6 empty] | GENCONTRACT | [9 empty] | (UTC+05:00) Astana
[6 empty] | DISTGEN | [9 empty] | (UTC+05:00) Ekaterinburg
[6 empty] | PWRPLANT | [9 empty] | (UTC+05:00) Islamabad, Karachi
[6 empty] | SRVDELIVERYPOINT | [9 empty] | (UTC+05:30) Chennai, Kolkata, Mumbai, New Delhi
[6 empty] | SRVLOCATION | [9 empty] | (UTC+05:30) Sri Jayawardenepura
[6 empty] | BUSBAR | [9 empty] | (UTC+05:45) Kathmandu
[6 empty] | NOTEC | [9 empty] | (UTC+06:00) Bishkek
[6 empty] | DYNAMICLINERATING | [9 empty] | (UTC+06:00) Dhaka
[6 empty] | DYNAMICPWTRATING | [9 empty] | (UTC+06:00) Omsk
[6 empty] | RELSETTS | [9 empty] | (UTC+06:30) Yangon (Rangoon)
[6 empty] | DISTRELSETTS | [9 empty] | (UTC+07:00) Bangkok, Hanoi, Jakarta
[6 empty] | DISTRELSTAGE | [9 empty] | (UTC+07:00) Barnaul, Gorno-Altaysk
[6 empty] | RELCONDITION | [9 empty] | (UTC+07:00) Hovd
[6 empty] | REGCTRLGROUP | [9 empty] | (UTC+07:00) Krasnoyarsk
[6 empty] | TRBANK | [9 empty] | (UTC+07:00) Novosibirsk
[6 empty] | CAPBANK | [9 empty] | (UTC+07:00) Tomsk
[6 empty] | PROTGROUP | [9 empty] | (UTC+08:00) Beijing, Chongqing, Hong Kong, Urumqi
[6 empty] | TRANSMISSION | [9 empty] | (UTC+08:00) Irkutsk
[6 empty] | METERC | [9 empty] | (UTC+08:00) Kuala Lumpur, Singapore
[6 empty] | LOGICALNODE | [9 empty] | (UTC+08:00) Perth
[6 empty] | CUSTOMEQP | [9 empty] | (UTC+08:00) Taipei
[6 empty] | CUSTOMBRANCH | [9 empty] | (UTC+08:00) Ulaanbaatar
[6 empty] | CUSTOMSHUNT | [9 empty] | (UTC+08:45) Eucla
[6 empty] | CUSTOMSWITCH | [9 empty] | (UTC+09:00) Chita
[6 empty] | FLEXIBLELOAD | [9 empty] | (UTC+09:00) Osaka, Sapporo, Tokyo
[6 empty] | LIMITSET | [9 empty] | (UTC+09:00) Pyongyang
[6 empty] | ALARMEVENTC | [9 empty] | (UTC+09:00) Seoul
[6 empty] | SIGNALVALUEALARM | [9 empty] | (UTC+09:00) Yakutsk
[6 empty] | ANALOGALARMLIMITS | [9 empty] | (UTC+09:30) Adelaide
[6 empty] | ADVALMLIMITS | [9 empty] | (UTC+09:30) Darwin
[6 empty] | STORAGE | [9 empty] | (UTC+10:00) Brisbane
[6 empty] | METERCMEAS | [9 empty] | (UTC+10:00) Canberra, Melbourne, Sydney
[6 empty] | PHASETAPCHANGER | [9 empty] | (UTC+10:00) Guam, Port Moresby
[6 empty] | SVC | [9 empty] | (UTC+10:00) Hobart
[6 empty] | COUNTERIEC | [9 empty] | (UTC+10:00) Vladivostok
[6 empty] | AINPUTIEC | [9 empty] | (UTC+10:30) Lord Howe Island
[6 empty] | DINPUTIEC | [9 empty] | (UTC+11:00) Bougainville Island
[6 empty] | AOUTPUTIEC | [9 empty] | (UTC+11:00) Chokurdakh
[6 empty] | DOUTPUTIEC | [9 empty] | (UTC+11:00) Magadan
[6 empty] | SUBRTUIEC104 | [9 empty] | (UTC+11:00) Norfolk Island
[6 empty] | RTUIEC104 | [9 empty] | (UTC+11:00) Sakhalin
[6 empty] | COMMLINKIEC104 | [9 empty] | (UTC+11:00) Solomon Is., New Caledonia
[6 empty] | COMMCHANNELIEC104 | [9 empty] | (UTC+12:00) Anadyr, Petropavlovsk-Kamchatsky
[6 empty] | AINPUTDNP3 | [9 empty] | (UTC+12:00) Auckland, Wellington
[6 empty] | DINPUTDNP3 | [9 empty] | (UTC+12:00) Coordinated Universal Time+12
[6 empty] | AOUTPUTDNP3 | [9 empty] | (UTC+12:00) Fiji
[6 empty] | DOUTPUTDNP3 | [9 empty] | (UTC+12:00) Petropavlovsk-Kamchatsky - Old
[6 empty] | RTUDNP3 | [9 empty] | (UTC+12:45) Chatham Islands
[6 empty] | COMMLINKDNP3 | [9 empty] | (UTC+13:00) Coordinated Universal Time+13
[6 empty] | COMMCHANNELDNP3 | [9 empty] | (UTC+13:00) Nuku'alofa
[6 empty] | COUNTERDNP3 | [9 empty] | (UTC+13:00) Samoa
[6 empty] | REMOTEINPUTICCP | [9 empty] | (UTC+14:00) Kiritimati Island
REMOTEOUTPUTICCP
DSTSICCP
RCCICCP
APPREFICCP
ASSOCIATIONICCP
APROCESSING
DERGROUP
TERMINALSERVER
RTUIEC101
COMMLINKIEC101
COMMCHANNELIEC101
SERIALLINK
TCPIPLINK
CALCCONSTARG
CALCSIGNALARG
CALCPARAM
CALCULATION
CALCCODE
AINPUTADMS
DINPUTADMS
AINPUTMODBUS
DINPUTMODBUS
AOUTPUTMODBUS
DOUTPUTMODBUS
RTUMODBUS
COMMLINKMODBUS
COMMCHANNELMODBUS
MODEM
MODEMBANK
MODEMLINK
SCANGROUPDNP3
NETCONFIGICCP
AINPUT2179
DINPUT2179
RPOINT2179
AOUTPUT2179
DOUTPUT2179
RTU2179
COMMLINK2179
COMMCHANNEL2179
SCANGROUP2179
SUBRTU2179
AINPUTCUSTOM1
DINPUTCUSTOM1
AOUTPUTCUSTOM1
DOUTPUTCUSTOM1
COMMCHANNELCUSTOM1
RTUCUSTOM1
COMMLINKCUSTOM1
AINPUTCUSTOM2
DINPUTCUSTOM2
AOUTPUTCUSTOM2
DOUTPUTCUSTOM2
COMMCHANNELCUSTOM2
RTUCUSTOM2
COMMLINKCUSTOM2
AINPUTCUSTOM3
DINPUTCUSTOM3
AOUTPUTCUSTOM3
DOUTPUTCUSTOM3
COMMCHANNELCUSTOM3
RTUCUSTOM3
COMMLINKCUSTOM3
AINPUT61850
DINPUT61850
AOUTPUT61850
DOUTPUT61850
COMMCHANNEL61850
RTU61850
COMMLINK61850
AINPUTDNP3SLAVE
DINPUTDNP3SLAVE
AOUTPUTDNP3SLAVE
DOUTPUTDNP3SLAVE
COMMCHANNELDNP3SLAVE
RTUDNP3SLAVE
COMMLINKDNP3SLAVE
COUNTERDNP3SLAVE
AINPUTS5
DINPUTS5
AOUTPUTS5
DOUTPUTS5
RTUS5
COMMLINKS5
COMMCHANNELS5
SCANGROUPS5
CONDITIONALSCHM
DOMCATALOG
TEMPLATE
AINPUTMETER
DINPUTMETER
RTUVCOM
COMMLINKVCOM
COMMCHANNELVCOM
SCANGROUPVCOM
AINPUTVCOM
AOUTPUTVCOM
DINPUTVCOM
DOUTPUTVCOM
RTUMD3
COMMLINKMD3
COMMCHANNELMD3
SCANGROUPMD3
AINPUTMD3
AOUTPUTMD3
DINPUTMD3
DOUTPUTMD3
RTUCONITEL
COMMLINKCONITEL
COMMCHANNELCONITEL
SCANGROUPCONITEL
AINPUTCONITEL
AOUTPUTCONITEL
DINPUTCONITEL
DOUTPUTCONITEL
SECUREDNP3
TEMPLATEINSTANCE
TMPMOBILEOBJECT
TMPCUT
TMPGENERATOR
TMPGROUNDING
TMPJUMPER
TMPSWITCH
FAULT
TMPLOAD
CHATTERPROCESSING
EVENTSCHEDULE
AINPUTIECSLAVE
DINPUTIECSLAVE
COUNTERIECSLAVE
AOUTPUTIECSLAVE
DOUTPUTIECSLAVE
RTUIECSLAVE
COMMCHANNELIEC101SLAVE
COMMLINKIEC101SLAVE
UDPLINK
TLS

## AlarmCatalog
Alarm Catalog
ALARMEVENTC
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | ALARMEVENTC_DOALARM | ALARMEVENTC_TEXT | ALARMEVENTC_INFO | ALARMEVENTC_DELAY | ALARMEVENTC_ESCALATION | ALARMEVENTC_CAUSE | ALARMEVENTC_SEVERITY | ALARMEVENTC_ESCALATEDSEVERITY | ALARMEVENTC_AUTOACKRTN
Name | Delete | Alias | Custom ID | Do alarm | Text | Alarm Information | Delay [s] | Escalation Timeout [s] | Cause | Severity | Escalated Severity | Auto Acknowledge RTN
Retorno do Dado do Limite sem Alarme |  | LIRLIM | bfa467a2-0504-4148-93cd-22ceb2c7b90b | FALSE | LIRLIM - Retorno de limite {0:G} {1} {2} [] | Retorno do Dado do Limite Superior / Inferior | 0 | 0 | AnalogRTN | Severidade 12 | Severidade 16 | FALSE
Alarme de Dado em Limite Inferior 1 |  | ALIINF OPER | c7ece8f5-c6e7-487b-b037-1203bc485f3a | TRUE | ALIINF OPER - Valor {0:G} {1} (limite = {3:0.00}) {4} [] | Alarme de Dado em Limite Inferior - Nivel 1 | 0 | 0 | AnalogLow | Severidade 11 | Severidade 16 | FALSE
Alarme de Dado em Limite Inferior 2 |  | ALIINF EMERG | be48ca90-c6b7-41ba-8ee9-c8e438a1d7b9 | TRUE | ALIINF EMERG - Valor {0:G} {1} (limite = {3:0.00}) {4} [] | Alarme de Dado em Limite Inferior - Nivel 2 | 0 | 0 | AnalogLow | Severidade 10 | Severidade 16 | FALSE
Alarme de Dado em Limite Superior 1 |  | ALISUP OPER | ff1d090d-cb13-4917-9eb3-e0fa2d86d7c6 | TRUE | ALISUP OPER - Valor {0:G} {1} (limite = {3:0.00}) {4} [] | Alarme de Dado em Limite Superior - Nivel 1 | 0 | 0 | AnalogHigh | Severidade 11 | Severidade 16 | FALSE
Alarme de Dado em Limite Superior 2 |  | ALISUP EMERG | 7f78107b-a539-488b-947c-5208b1b636a7 | TRUE | ALISUP EMERG - Valor {0:G} {1} (limite = {3:0.00}) {4} [] | Alarme de Dado em Limite Superior - Nivel 2 | 0 | 0 | AnalogHigh | Severidade 10 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telessinalizado SB |  | ALESTS SB | 1f59c83d-ed50-4c30-b78c-f6a7bf4fc419 | TRUE | ALESTS - {1} [] | Alarme de Estado em Ponto Telessinalizado SB | 0 | 0 | DiscreteState | Severidade 7 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telessinalizado SA |  | ALESTS SA | ea37e1f4-2f6f-4890-bff5-f26ef60861bc | TRUE | ALESTS - {1} [] | Alarme de Estado em Ponto Telessinalizado SA | 0 | 0 | DiscreteState | Severidade 4 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telessinalizado SO |  | ALESTS SO | 824112f7-80f9-44d3-b23f-a5dd759a8089 | TRUE | ALESTS - {1} [] | Alarme de Estado em Ponto Telessinalizado SO | 0 | 0 | DiscreteState | Severidade 6 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telessinalizado SBx |  | ALESTS SB | 74952f44-9ac5-43e3-8c99-462f63f1dfb8 | FALSE | ALESTS - {1} [] | Alarme de Estado em Ponto Telessinalizado SB | 0 | 0 | DiscreteState | Severidade 7 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telessinalizado SI |  | ALESTS SI | 8f25ca55-4b1e-4922-9939-22adf675a896 | TRUE | ALESTS - {1} [] | Alarme de Estado em Ponto Telessinalizado SI | 0 | 0 | DiscreteState | Severidade 3 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telessinalizado SB sem temporizacao |  | ALESTS SB sem temporizado | 25f438c3-fe49-4b9e-a52f-39ee48ce83cf | TRUE | ALESTS - {1} [] | Alarme de Estado em Ponto Telessinalizado SB nao Temporizado | 0 | 0 | DiscreteState | Severidade 7 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telessinalizado SS |  | ALESTS SS | 67432746-cf34-4050-b437-ce71f5c97687 | TRUE | ALESTS - {1} [] | Alarme de Estado em Ponto Telessinalizado SS | 0 | 0 | DiscreteState | Severidade 8 | Severidade 16 | FALSE
Alarme Prioritario de Dado a 90% do Limite Superior com Temporização |  | ALI90 | 4bfc2d6b-ef89-419d-a340-43a7e4fae649 | TRUE | ALI90 - Valor {0:G} {1} (limite = {3:0.00}) {4} [] | Alarme Prioritario de Dado a 90% do Limite Superior com Temporização | 180 | 0 | AnalogHigh | Severidade 12 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telecontrolado SS |  | ALESTC SS | 86dfd195-09a3-4de8-8a16-4e75477b0a6d | TRUE | ALESTC - {1} [] | Alarme de Estado em Ponto Telecontrolado SS | 0 | 0 | DiscreteState | Severidade 8 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telecontrolado SV |  | ALESTC SV | a0074a11-62cf-49d4-bf2d-845b23e10823 | TRUE | ALESTC - {1} [] | Alarme de Estado em Ponto Telecontrolado SV | 0 | 0 | DiscreteState | Severidade 5 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telecontrolado SE |  | ALESTC SE | 79db9ae6-f5fa-48d7-a106-e844ad4cffd1 | TRUE | ALESTC - {1} [] | Alarme de Estado em Ponto Telecontrolado SE | 0 | 0 | DiscreteState | Severidade 2 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telecontrolado SO |  | ALESTC SO | f61778cb-e93a-4585-a157-96927f8984dd | TRUE | ALESTC - {1} [] | Alarme de Estado em Ponto Telecontrolado SO | 0 | 0 | DiscreteState | Severidade 6 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telecontrolado SA |  | ALESTC SA | ca6bf4fd-884a-4c87-a290-9f6e0c688ba8 | TRUE | ALESTC - {1} [] | Alarme de Estado em Ponto Telecontrolado SA | 0 | 0 | DiscreteState | Severidade 4 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telessinalizado SP |  | ALESTS SP | 9081b1ae-4a23-44c1-9bbf-ede74195045f | TRUE | ALESTS - {1} [] | Alarme de Estado em Ponto Telessinalizado SP | 0 | 0 | DiscreteState | Severidade 5 | Severidade 16 | FALSE

## AlarmLimits
Alarm Limits
ANALOGALARMLIMITS | [6 empty] | SIGNALVALUEALARM
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | ANALOGALMLIMITS_MEASTYPE | ANALOGALMLIMITS_MINEGU | ANALOGALMLIMITS_MAXEGU | SIGNALVALUEALARM_USEDINCREEP | SIGNALVALUEALARM_USEDINFLATLINE | SIGNALVALUEALARM_USEDIN2 | SIGNALVALUEALARM_USEDIN1
Name | Delete | Alias | Custom ID | Measurement Type | Min. Reasonable Value | Max. Reasonable Value | Reasonability Check Alarm Catalog | Return-To-Normal Alarm Catalog | Low Limit Catalog | High Limit Catalog
VBC_14.49@14.35_13.52@13.39_Trans |  |  | a9b50990-538e-4440-93ba-03ac42c1ac6f | Voltage | -3.4028e+38 | 3.4028e+38 |  | Retorno do Dado do Limite sem Alarme | Alarme de Dado em Limite Inferior 1;Alarme de Dado em Limite Inferior 2 | Alarme de Dado em Limite Superior 1;Alarme de Dado em Limite Superior 2
VBC_144.9@143.52_131.1@124.2_Trans |  |  | 52c8833e-40da-45a1-b805-c0b427dd8ec3 | Voltage | -3.4028e+38 | 3.4028e+38 |  | Retorno do Dado do Limite sem Alarme | Alarme de Dado em Limite Inferior 1;Alarme de Dado em Limite Inferior 2 | Alarme de Dado em Limite Superior 1;Alarme de Dado em Limite Superior 2
V_24.2@23.9_21.9@21.6_Trans |  |  | 8b30a88d-9f7e-4eb0-bc1a-dd6c8f1dadb3 | Voltage | -3.4028e+38 | 3.4028e+38 |  | Retorno do Dado do Limite sem Alarme | Alarme de Dado em Limite Inferior 1;Alarme de Dado em Limite Inferior 2 | Alarme de Dado em Limite Superior 1;Alarme de Dado em Limite Superior 2
TOLE_95@85_0@0_Trans |  |  | cb6dae5a-aac1-4f05-af90-c9e27fa5c830 | Temperature | -3.4028e+38 | 3.4028e+38 |  | Retorno do Dado do Limite sem Alarme | Alarme de Dado em Limite Inferior 1;Alarme de Dado em Limite Inferior 2 | Alarme de Dado em Limite Superior 1;Alarme de Dado em Limite Superior 2
TENR_105@95_0@0_Trans |  |  | b3ec273e-e399-4b6f-a12b-94cc6dd8eb02 | Temperature | -3.4028e+38 | 3.4028e+38 |  | Retorno do Dado do Limite sem Alarme | Alarme de Dado em Limite Inferior 1;Alarme de Dado em Limite Inferior 2 | Alarme de Dado em Limite Superior 1;Alarme de Dado em Limite Superior 2
I_403.2@null_null@null_Distr |  |  | 002d0a43-c094-4cc4-a82c-defc8f98a753 | Current | -3.4028e+38 | 3.4028e+38 |  | Retorno do Dado do Limite sem Alarme |  | Alarme Prioritario de Dado a 90% do Limite Superior com Temporização
VCC_142@138_115@110_Trans |  |  | 7f4f2fe9-c8ea-4f09-a58e-70e560ec4ab1 | Unitless | -3.4028e+38 | 3.4028e+38 |  | Retorno do Dado do Limite sem Alarme | Alarme de Dado em Limite Inferior 1;Alarme de Dado em Limite Inferior 2 | Alarme de Dado em Limite Superior 1;Alarme de Dado em Limite Superior 2

## LimitSets
Limit Set
LIMITSET
LIMITSET_DYNAMICRATING | IDOBJ_NAME | LIMITSET_LOWLIMITVALUES | LIMITSET_LOWDEADBAND | LIMITSET_LIMITVALUES | LIMITSET_HIGHDEADBAND
Alarm Limit | Name | Low Limits | Low Limit Deadbands | High Limits | High Limit Deadbands
VBC_14.49@14.35_13.52@13.39_Trans | Default | 13.52;13.39 | 0.12;0.12 | 14.35;14.49 | 0.13;0.13
VBC_144.9@143.52_131.1@124.2_Trans | Default | 131.1;124.2 | 2.484;4.14 | 143.52;144.9 | 1.37;1.37
V_24.2@23.9_21.9@21.6_Trans | Default | 21.9;21.6 | 0.12;0.12 | 23.9;24.2 | 0.09;0.09
TOLE_95@85_0@0_Trans | Default | 1;0 | 0.5;0.5 | 85;95 | 4.25;4.75
TENR_105@95_0@0_Trans | Default | 1;0 | 0.5;0.5 | 95;105 | 4.75;5.25
I_403.2@null_null@null_Distr | Default |  |  | 403.2 | 0.2016
VCC_142@138_115@110_Trans | Default | 115;110 | 4.6;4.99 | 138;142 | 3.99;3.99

## MessageMappings
Message Mapping
MESSAGEMAPPING | [10 empty] | SIGNALVALUEALARM
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | MESSAGEMAPPING_MESSAGES | MESSAGEMAPPING_VALUES | MESSAGEMAPPING_SCADAVALUES | MESSAGEMAPPING_CMDMESSAGES | MESSAGEMAPPING_COLORS | MESSAGEMAPPING_ABNORMAL | MESSAGEMAPPING_OVERRIDABLE | SIGNALVALUEALARM_USEDIN1
Name | Delete | Alias | Custom ID | Messages | Values | SCADA Values | Commanding Messages | Colors | Abnormal Status | Overridable | Alarm Catalog
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___LAR |  | LAR | 541568dc-14b9-4301-bd17-a8db8f632f42 | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 0;1;2;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | TRUE;TRUE;TRUE;TRUE
Switch.SwitchStatus |  |  | Switch.SwitchStatus | Error;ABERTO;FECHADO;Transit | 0;1;2;3 | 0;1;2;3 | ;ABRIR;FECHAR; | #00000000;#FF00FF00;#FFFF0000;#00000000 | Abnormal;Auto;Auto;Abnormal | TRUE;TRUE;TRUE;TRUE
null@null___CARGA@DESCARGA___Custom_S_TS_SB |  |  | 734ab987-9820-4cb6-8e25-2a16529bdf82 | Transit;CARGA;DESCARGA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@ATUADO___Custom_S_TS_SA |  |  | aba5eec1-6268-464b-a141-f943b4fed6b7 | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@FALTA___Custom_S_TS_SB |  |  | b3a0f05e-a43e-4987-9664-6b2ab339c7d7 | Transit;NORMAL;FALTA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB
Fuse.SwitchStatus |  |  | Fuse.SwitchStatus | Error;ABERTO;FECHADO;Transit | 0;1;2;3 | 0;1;2;3 | ;ABRIR;FECHAR; | #00000000;#0000FF00;#00FF0000;#00000000 | Abnormal;Auto;Auto;Abnormal | TRUE;TRUE;TRUE;TRUE
ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TS_SO |  |  | a7f4838c-d4e0-4669-85e4-6eb1f1251ec9 | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 0;1;2;3 | ;ABRIR;FECHAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SO;Alarme de Estado em Ponto Telessinalizado SO;Alarme de Estado em Ponto Telessinalizado SO;Alarme de Estado em Ponto Telessinalizado SO
DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom___INV_S_TS_SB |  |  | 513294cb-0204-4535-9d23-6044069e61aa | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Abnormal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@FALHA___Custom___INV_S_TS_SB |  |  | 59dce93e-75d8-4fad-a224-f156dca33b3c | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB
ProtectionEquipment.Enabled |  |  | ProtectionEquipment.Enabled | Error;DISABLED;ENABLED;Transit | 0;1;2;3 | 0;1;2;3 | ;DISABLE;ENABLE; | #00000000;#00FF0000;#0000FF00;#00000000 | Normal;Normal;Normal;Normal | TRUE;TRUE;TRUE;TRUE
null@null___NORMAL@FALHA___Custom_S_TS_SBx |  |  | 2d048be4-e0f6-4ae7-92f2-cfb9a1c38a0e | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SBx;Alarme de Estado em Ponto Telessinalizado SBx;Alarme de Estado em Ponto Telessinalizado SBx;Alarme de Estado em Ponto Telessinalizado SBx
null@null___NORMAL@FALHA___Custom_S_TS_SB |  |  | 30c921f9-7b77-4cc5-893d-5c91765e61bd | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  | 3318464c-b4db-4052-8f62-984a82bed1b1 | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@ATUADO___Custom_S_TS_SI |  |  | 9dc12e55-d022-469e-8177-3a9739f98546 | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SI;Alarme de Estado em Ponto Telessinalizado SI;Alarme de Estado em Ponto Telessinalizado SI;Alarme de Estado em Ponto Telessinalizado SI
null@null___NORMAL@ATUADO___Custom_S_TS_SB |  |  | df150184-40aa-49e4-8676-b36b56adfffc | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB sem temporizacao;Alarme de Estado em Ponto Telessinalizado SB sem temporizacao;Alarme de Estado em Ponto Telessinalizado SB sem temporizacao;Alarme de Estado em Ponto Telessinalizado SB sem temporizacao
null@null___NÃO PERMITIDO@PERMITIDO___Custom_S_TS_SS |  |  | fcbd0f6e-5b23-4bc5-a6e5-965c166384a6 | Transit;NÃO PERMITIDO;PERMITIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS
null@null___REMOTO@LOCAL___Custom_S_TS_SS |  |  | 1dac907a-d6e3-42f8-ba71-4d801f99a716 | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS
null@null___REMOTO@LOCAL___Custom___INV_S_TS_SS |  |  | 808fdfbe-d938-4095-a956-c49d044b683e | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS
null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS |  |  | f86c33b8-6d2d-42db-a138-83e9df4dd790 | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS
null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB |  |  | 5079bf20-9a7c-4632-a068-75e30dcfb560 | Transit;CARREGADA;DESCARREGADA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB
null@null___MANUAL DESATIVOU@MANUAL ATIVOU___Custom_S_TS_SS |  |  | e3d08b30-aba3-4242-a9dc-5e69d58f5c6b | Transit;MANUAL DESATIVOU;MANUAL ATIVOU;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS
null@null___AUTOM DESATIVADO@AUTOM ATIVOU___Custom_S_TS_SS |  |  | 47cb64f2-8605-4375-a4e3-2175dbe3d1fb | Transit;AUTOM DESATIVADO;AUTOM ATIVOU;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS
null@null___NORMAL@DEFEITO___Custom_S_TS_SI |  |  | a9894d24-135c-4e7b-b8be-9bc122849a5c | Transit;NORMAL;DEFEITO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SI;Alarme de Estado em Ponto Telessinalizado SI;Alarme de Estado em Ponto Telessinalizado SI;Alarme de Estado em Ponto Telessinalizado SI
null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS |  |  | 3406f2cb-403f-49a7-bf04-cadb523c6223 | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS
null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS |  |  | ac10e5d2-e465-4a89-86e0-679309bdb0a9 | Transit;BLOQUEADA;LIBERADA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS
null@null@null___MESTRE@INDIVIDUAL@COMANDO___Custom___admsINV_D_TS_SS |  |  | 02c55c6e-913d-48ce-83ab-ffc8acbd9e45 | MESTRE;COMANDADO;INDIVIDUAL;Error | 0;1;2;3 | 0;1;2;3 | MESTRE;;; | #FFFF0000;#FFFF0000;#FFFF0000;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS
null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS |  |  | 327d67af-b2c3-4d6f-b850-08371eaef8e3 | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS |  |  | 89142b13-37f0-4791-9940-db88dfa90839 | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV |  |  | b3fa1bf2-fc9d-481b-be2d-0b7eaa29c641 | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SV;Alarme de Estado em Ponto Telecontrolado SV;Alarme de Estado em Ponto Telecontrolado SV;Alarme de Estado em Ponto Telecontrolado SV
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV___admsINV_S_TC_SS |  |  | 439c8e84-f1c8-4e53-bf66-725a2bd1315a | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS
DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TC_SV |  |  | e3c9e933-d75d-4dd9-814b-a37ba1c61422 | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SV;Alarme de Estado em Ponto Telecontrolado SV;Alarme de Estado em Ponto Telecontrolado SV;Alarme de Estado em Ponto Telecontrolado SV
AUMENTAR@DIMINUIR___null@null___TapIncrement_S_TC_SS |  |  | 3ed40982-078f-4656-b5db-7a1d89a8fbd4 | Transit;;;Error | 0;2;1;3 | 2;0;1;3 | ;AUMENTAR;DIMINUIR; | #FF000000;#FFFF0000;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE |  |  | 7bf0bf18-4079-44b8-809f-5e74dbacc82e | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;1;2;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;TRUE | Alarme de Estado em Ponto Telecontrolado SE;Alarme de Estado em Ponto Telecontrolado SE;Alarme de Estado em Ponto Telecontrolado SE;Alarme de Estado em Ponto Telecontrolado SE
ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO |  |  | f0107821-8e5f-485b-bf9a-6d42132eb32e | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 0;1;2;3 | ;ABRIR;FECHAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;TRUE | Alarme de Estado em Ponto Telecontrolado SO;Alarme de Estado em Ponto Telecontrolado SO;Alarme de Estado em Ponto Telecontrolado SO;Alarme de Estado em Ponto Telecontrolado SO
null@null___AUTOMATICO@MANUAL___Custom___INV_S_TS_SS |  |  | a2ba1b5d-d6ce-4a64-b586-326376123d1e | Transit;AUTOMATICO;MANUAL;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS
REARMAR@null___NORMAL@ATUADO___Custom_S_TC_SA |  |  | b928b78f-9d6b-498f-aad0-7226d65b8d1a | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;REARMAR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SA;Alarme de Estado em Ponto Telecontrolado SA;Alarme de Estado em Ponto Telecontrolado SA;Alarme de Estado em Ponto Telecontrolado SA
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS |  |  | 7138c8f2-60bb-40a4-849d-2528a3386832 | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS
MESTRE@INDIVIDUAL@COMANDO___null@null@null___Custom___admsINV_D_TC_SS |  |  | ab593396-4eef-45fa-b47e-d7300efe3766 | ;;; | 0;1;2;3 | 1;2;4;8 | MESTRE;INDIVIDUAL;COMANDADO; | #FFFF0000;#FFFF0000;#FFFF0000;#FF000000 | Normal;Normal;Normal;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS
null@null___NORMAL@FALHA___RelayTrip_S_TS_SA |  |  | d893e257-9ac6-4791-8959-a08365901b8b | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS |  |  | 00d7c00c-471c-4cf6-b9f7-94ca1909009e | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS |  |  | 1a02e12d-4aa3-419e-a0e6-775cdc28239b | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS
null@null___NORMAL@ATUADO___Custom_S_TS_SP |  |  | c4385961-b437-4afd-83d8-85b9745cfe29 | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SP;Alarme de Estado em Ponto Telessinalizado SP;Alarme de Estado em Ponto Telessinalizado SP;Alarme de Estado em Ponto Telessinalizado SP
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS |  |  | 4aa35948-de64-4637-a941-9a68d35431ae | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS

## ManualDiscreteSignals
Signal Details
DSIGNAL
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | MEASUREMENT_PSR |  | IDOBJ_AORGROUP | SIGNAL_DEVICEMAPPING | [7 empty] | DSIGNAL_TYPE | MEASUREMENT_TYPE | MEASUREMENT_PHASE | MEASUREMENT_SIDE | SIGNAL_DIRECTION | SIGNAL_ANNUALSCH | DSIGNAL_MAPPING | DSIGNAL_NORMALVALUE | DSIGNAL_DOMCATALOG
Signal Name | Delete | Signal Alias | Signal Custom ID | Device Name | Device Custom ID | Signal AOR Group | Substation | Feeder | Feeder Object | Bank | Bay | Device | Device Mapping | Description | Signal Type | Measurement Type | Phases | Side | Direction | Annual Schedule | Message Mapping | Normal Value | DOM Catalog
ESTADO_LAR |  | LAR | ea7dc560-f433-411e-bbfb-253f404767d2 | FREDERICO WESTPHALEN 2 | 7605493c-d9f8-4bfd-9b6e-f9256e5f881b | FWB Trans | [6 empty] | FWB |  | Custom | Discrete | Unknown | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___LAR | 1
FWB_TRF2_29-118_SECF |  | SEC FONT | 09a1767c-31e2-4110-8bad-f2696e7a8199 | 29-118_FWB | 2eb9e4b7-7e38-430a-806d-16351b786455 | FWB Distr | [6 empty] | FWB_TRF2_29-118_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_TR1BT_29-38_SECC |  | SEC CARG | bff20e2a-6e6e-402a-ad01-3f79c7063a0c | 29-38_FWB | 4f05c1da-dc0e-42fe-9850-d4c21bcef95b | FWB Trans | [6 empty] | FWB_TR1BT_29-38_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_BC1_29-52_SECF |  | SEC FONT | a56e02b4-6614-44f7-9c1a-e3ec83157e53 | 29-52_FWB | 182c6f8f-6d7e-4ffd-8cd3-50cf16f21d90 | FWB Trans | [6 empty] | FWB_BC1_29-52_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_TRF1_29-76_SECF |  | SEC FONT | 276f48b9-ab00-4e10-9e87-85891e16ac46 | 29-76_FWB | b5f7252d-fffe-4148-a084-b71faddb6b54 | FWB Distr | [6 empty] | FWB_TRF1_29-76_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
SCD_IB_29-98_SECI |  | SEC BARR | c9b8ea8c-3135-4803-ba27-23578aa9a3c4 | 29-98_FWB | 8fa2b839-6b60-4a9c-aad9-6c01526d59f0 | FWB Trans | [6 empty] | SCD_IB_29-98_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_BP1_29-48_SECF |  | SEC FONT | 5ae9a708-52bd-48cc-96af-e07c457d06ec | 29-48_FWB | d5fbd38a-28f5-4c35-b180-7c86927c02f8 | FWB Trans | [6 empty] | FWB_MOV_29-48_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_AL21_29-108_SECC |  | SEC CARG | 61bb5181-fb97-48f9-91d5-d9b27acc32ad | 29-108_FWB | 54803fec-abb8-46e5-97c3-aa6d4266ceda | FWB Distr | [6 empty] | FWB_AL21_29-108_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_SE_RET1_BADC |  | BATERIA EM DESCARGA | e3bbdc82-19a4-47de-85a9-ccbf54cc3012 | FWB_SE_RET1_RET | 66cb5094-f5aa-4c22-97cc-2cc9ef7b9857 | FWB Trans | [6 empty] | SCD_SE_RET1_RET |  | Custom | Status | ABC | None | Read |  | null@null___CARGA@DESCARGA___Custom_S_TS_SB | 1
FWB_AL12_29-64_SECF |  | SEC FONT | 16c482e5-fdf9-441e-9851-7e216d1a09e4 | 29-64_FWB | 0cc7c8cb-4270-4fe5-9a94-082b46252c0c | FWB Distr | [6 empty] | FWB_AL12_29-64_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_SE_RET1_CAAL |  | VCA ALARME | 4215dab9-f125-4ad2-b275-7a7366b45efa | FWB_SE_RET1_RET | 66cb5094-f5aa-4c22-97cc-2cc9ef7b9857 | FWB Trans | [6 empty] | SCD_SE_RET1_RET |  | Custom | Status | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1
FWB_SE_RET1_CCAL |  | VCC ALARME | 63bde1a1-61f7-4b0d-a618-aff2a3ea4395 | FWB_SE_RET1_RET | 66cb5094-f5aa-4c22-97cc-2cc9ef7b9857 | FWB Trans | [6 empty] | SCD_SE_RET1_RET |  | Custom | Status | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1
FWB_AL22_29-114_SECC |  | SEC CARG | 428cc7f7-d8c5-4b5a-937e-32013d002d21 | 29-114_FWB | db3d4c88-ecf9-445b-9e4f-e3a2fa481c1f | FWB Distr | [6 empty] | FWB_AL22_29-114_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_AL12_29-66_SECC |  | SEC CARG | 99eab070-a294-4638-a756-2f15ab07fc24 | 29-66_FWB | eb36250f-46b5-4431-9cb8-b8a5eb114eb5 | FWB Distr | [6 empty] | FWB_AL12_29-66_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FU-4 |  | FU-4 | b30bc70c-e74a-4cb0-914e-609ef4d8daa9 | FU-4_FWB | 76faa883-32d2-4c7a-853b-b826160be65f | FWB Trans | [8 empty] | SwitchStatus | SwitchStatus | ABC | None | ReadWrite |  | Fuse.SwitchStatus | 2
FWB_BC1_29-56_SECT |  | SEC TRAN | fd2d7f16-4070-417c-924e-93800f44cfde | 29-56_FWB | 67c62521-07ce-4b0d-855b-7e7d7d8c8305 | FWB Trans | [6 empty] | FWB_BC1_29-56_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TS_SO | 1
FU-2 |  | FU-2 | 5601b00b-80ed-400a-9572-559b84903503 | FU-2_FWB | 3e3d73e2-685a-4563-b150-913f963d1105 | FWB Trans | [8 empty] | SwitchStatus | SwitchStatus | ABC | None | ReadWrite |  | Fuse.SwitchStatus | 2
FWB_SE_RET1_EST |  | ESTADO EQUIPAMENTO | 329c3568-9571-4462-bc45-0e19120dceed | FWB_SE_RET1_RET | 66cb5094-f5aa-4c22-97cc-2cc9ef7b9857 | FWB Trans | [6 empty] | SCD_SE_RET1_RET |  | Custom | Status | ABC | None | Read |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom___INV_S_TS_SB | 2
FWB_TRF2_29-120_SECC |  | SEC CARG | 5800d33e-bc8f-41ac-84ca-770e7e733a9c | 29-120_FWB | d6e0a055-c7aa-49d4-8ce7-ced6bf2900ed | FWB Distr | [6 empty] | FWB_TRF2_29-120_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_TRF2_29-122_SECT |  | SEC TRAN | bea6f98a-3b8b-4669-af47-d4ac61bd7cee | 29-122_FWB | 24754edd-ce2a-4524-a95f-9177b2a992ba | FWB Distr | [6 empty] | FWB_TRF2_29-122_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 1
FWB_AL13_29-70_SECF |  | SEC FONT | b56ed877-77c4-4b5c-9a59-9346a6f52ad7 | 29-70_FWB | 8990a145-ba46-463b-b717-c066c6a22e3d | FWB Distr | [6 empty] | FWB_AL13_29-70_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FU-3 |  | FU-3 | 92321860-6347-40c5-ab37-6e3d6b067b46 | FU-3_FWB | 9b1424b2-ec62-498b-98c1-74521a44ce84 | FWB Trans | [8 empty] | SwitchStatus | SwitchStatus | ABC | None | ReadWrite |  | Fuse.SwitchStatus | 2
FWB_SE_RET1_FCOM |  | FALHA COMUNICACAO | 77d73ad7-55d1-497e-ac88-9fc75bf1f6cb | FWB_SE_RET1_RET | 66cb5094-f5aa-4c22-97cc-2cc9ef7b9857 | FWB Trans | [6 empty] | SCD_SE_RET1_RET |  | Custom | Status | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom___INV_S_TS_SB | 1
FWB_AL14_29-84_SECC |  | SEC CARG | c3f6b104-6f3f-413a-8bc7-40c7b5be96c5 | 29-84_FWB | 0034f771-8dfc-4ae3-8962-f546c97ef43b | FWB Distr | [6 empty] | FWB_AL14_29-84_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_AL24_29-134_SECT |  | SEC TRAN | daf3a989-84d0-4f26-8c4e-cd71240be7e4 | 29-134_FWB | 1c66da50-1c3e-487d-921d-9fe1002837a7 | FWB Distr | [6 empty] | FWB_AL24_29-134_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 1
FWB_AL13_29-72_SECC |  | SEC CARG | a1db62c2-244f-4fdd-ae10-5055d644baf6 | 29-72_FWB | ec62a664-5bbb-4a86-967b-d8d11d60a61b | FWB Distr | [6 empty] | FWB_AL13_29-72_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FU-1 |  | FU-1 | 06b61781-34ea-49ab-808f-6fc0708e7219 | FU-1_FWB | 7f517dfb-9db7-4518-bc7c-9766a3efd4a0 | FWB Trans | [8 empty] | SwitchStatus | SwitchStatus | ABC | None | ReadWrite |  | Fuse.SwitchStatus | 2
FWB_AL24_29-130_SECF |  | SEC FONT | efaf5a77-d3d6-42d2-a902-02c6cbbb8cc2 | 29-130_FWB | 7ea996e0-8190-4f18-bc3b-7bd75742cbc3 | FWB Distr | [6 empty] | FWB_AL24_29-130_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
Novo Sinal Discreto |  |  | 4dd324a9-9113-4ad3-9e65-c3f5991317a4 | Novo Regulador | 434ab3ea-baa0-4975-9256-7d7ecea61d3b | FWB Trans | [8 empty] | Enabled | Status | ABC | None | ReadWrite |  | ProtectionEquipment.Enabled | 2
FWB_TR1BT_29-36_SECF |  | SEC FONT | a79a8c3a-cd12-480e-842b-7d1f9fa3f8d6 | 29-36_FWB | ba83b985-ab7e-4a86-88b3-5d1271c199b9 | FWB Trans | [6 empty] | FWB_TR1BT_29-36_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_TR2BT_29-42_SECF |  | SEC FONT | 2754ee02-ae1f-455d-a32d-8e6e801699c8 | 29-42_FWB | 346cbd12-0a9c-4d00-972e-5a324efea71a | FWB Trans | [6 empty] | FWB_TR2BT_29-42_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
Novo Sinal Discreto |  |  | 7054b95c-c901-4fa8-9628-e7528c3a2341 | Novo Regulador | 9bd3a849-9992-4fc7-9b0e-a355b8c371bf | FWB Trans | [8 empty] | Enabled | Status | ABC | None | ReadWrite |  | ProtectionEquipment.Enabled | 2
FWB_AL24_29-132_SECC |  | SEC CARG | 3f54f120-fb64-4ae0-8cd9-ba93ee41b706 | 29-132_FWB | 7a5d202b-4cf0-4d71-b728-b442a7352279 | FWB Distr | [6 empty] | FWB_AL24_29-132_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_AL12_29-68_SECT |  | SEC TRAN | 75458a8b-5646-4898-9e77-9aa0dd180793 | 29-68_FWB | 87acb120-bff6-44db-a74b-0c0dd8fd349f | FWB Distr | [6 empty] | FWB_AL12_29-68_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 1
FWB_IB_29-96_SECI |  | SEC BARR | 0fa06733-0197-4389-88f9-b74637be8e54 | 29-96_FWB | bacb978d-6768-4322-badf-01a12967792a | FWB Trans | [6 empty] | FWB_IB_29-96_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_AL14_29-82_SECF |  | SEC FONT | bef2d6ed-7c96-47db-8807-e1d369d390fe | 29-82_FWB | 864d3db9-f9b0-4f99-9a97-cc8f2a7abd7f | FWB Distr | [6 empty] | FWB_AL14_29-82_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_TR4_TR4_FCOM |  | FALHA COMUNICACAO | 2290d6f2-c937-403f-acb7-3cb05a7e0f5b | FWB_SE_RET1_RET | 66cb5094-f5aa-4c22-97cc-2cc9ef7b9857 | FWB Trans | [6 empty] | SCD_SE_RET1_RET |  | Custom | Status | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SBx | 1
FWB_TRF1_29-78_SECC |  | SEC CARG | 722bb9be-111b-4f33-96e7-8829517226ab | 29-78_FWB | 13c07018-3a42-423c-bab3-a7371b470cae | FWB Distr | [6 empty] | FWB_TRF1_29-78_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_IB_29-94_SECI |  | SEC BARR | d4467e90-3c5f-4b30-8c67-d597cfa7542a | 29-94_FWB | 36beea19-509e-4271-bd2c-c944236d9c50 | FWB Trans | [6 empty] | FWB_IB_29-94_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_TR5_TR5_FCOM |  | FALHA COMUNICACAO | 02f0b343-3532-47b7-aa75-7b786172787b | FWB_SE_RET2_RET | df7f17ff-87bf-4643-9238-679774d799d0 | FWB Trans | [6 empty] | FWB_SE_RET2_RET |  | Custom | Status | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SBx | 1
FWB_AL22_29-116_SECT |  | SEC TRAN | 69c27f60-f408-425c-b333-3945f458a408 | 29-116_FWB | 6fb4db49-4432-4304-927d-c4c11048403c | FWB Distr | [6 empty] | FWB_AL22_29-116_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 1
FWB_TR2BT_29-44_SECC |  | SEC CARG | 6fd0f9ed-4cab-46a7-b72a-44dceb70435e | 29-44_FWB | 441b9501-e486-4561-a6df-186eacd772b4 | FWB Trans | [6 empty] | FWB_TR2BT_29-44_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_AL22_29-112_SECF |  | SEC FONT | eaeeb824-efbd-4cd1-b039-b0d87ff3e8e0 | 29-112_FWB | 73c07864-5061-47e4-b8ad-dbae78923ade | FWB Distr | [6 empty] | FWB_AL22_29-112_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_AL21_29-106_SECF |  | SEC FONT | ef63104a-cc30-48ad-8f96-c1cd74b22433 | 29-106_FWB | 9df032c0-750e-40c9-98f1-dbf25bfcf7f3 | FWB Distr | [6 empty] | FWB_AL21_29-106_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_AL13_29-74_SECT |  | SEC TRAN | 84434fcf-d274-481b-83b5-ee2f8dbd1f8a | 29-74_FWB | f1c7362e-e8d6-4965-a626-4869a2d598fa | FWB Distr | [6 empty] | FWB_AL13_29-74_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 1
FWB_AL14_29-86_SECT |  | SEC TRAN | 5c1c4505-4876-4165-b4f5-6f3fd303daed | 29-86_FWB | 770e3c2f-ec83-4aab-a1e7-7f68e4c822bc | FWB Distr | [6 empty] | FWB_AL14_29-86_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 1
FWB_TRF1_29-80_SECT |  | SEC TRAN | c18bb3bf-e819-4ac3-8d8e-c314f508df58 | 29-80_FWB | 22a51599-0020-415c-8f73-db9ab106c137 | FWB Distr | [6 empty] | FWB_TRF1_29-80_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 1
FWB_AL21_29-110_SECT |  | SEC TRAN | e671d9ce-6c2f-4341-8b97-d11ef554ce02 | 29-110_FWB | 6d2e53da-4aba-4072-b2a9-5d3957983f26 | FWB Distr | [6 empty] | FWB_AL21_29-110_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 1
FWB_AL15_29-90_SECC |  | SEC CARG | 3b190fca-9a44-4471-8da5-861cf92c465b | 29-90_FWB | 60c8e211-cbd2-45b6-97d9-b57d04ac5b7b | FWB Distr | [6 empty] | FWB_AL15_29-90_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_AL15_29-92_SECT |  | SEC TRAN | 74c499b3-4ff2-4d57-93a9-f9b8665278c0 | 29-92_FWB | 8014f60b-dcee-42d1-9051-3a356d853d9d | FWB Distr | [6 empty] | FWB_AL15_29-92_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 1
FWB_AL15_29-88_SECF |  | SEC FONT | 46cdb815-15d3-41cd-97dd-690bd61a2807 | 29-88_FWB | 5678b5a4-0f29-44a4-92a7-48d697892617 | FWB Distr | [6 empty] | FWB_AL15_29-88_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_AL25_29-136_SECF |  | SEC FONT | 93da727a-0670-4432-8db4-e09fde38621f | 29-136_FWB | a3f5fba4-8966-47da-8b7e-4fc01e42a707 | FWB Distr | [6 empty] | FWB_AL25_29-136_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_AL25_29-140_SECT |  | SEC TRAN | 0364eaac-b8f5-4abc-8009-d9413f90bac2 | 29-140_FWB | 3c33fe21-cca3-4a29-985b-9b2ac5a4380e | FWB Distr | [6 empty] | FWB_AL25_29-140_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 1
FWB_AL25_29-138_SECC |  | SEC CARG | 28a4a893-6dec-4ff5-aaf8-eb6eadd55b78 | 29-138_FWB | 44f3f711-5892-4545-aec1-c86a4315266d | FWB Distr | [6 empty] | FWB_AL25_29-138_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_BP1_29-50_SECF |  | SEC FONT | 0aba6b91-4b82-49f9-bee9-39e5ca42d130 | 29-50_FWB | 6054ab33-3501-44f4-afa1-07f244e21909 | FWB Trans | [6 empty] | FWB_BP1_29-50_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_BC1_29-54_SECF |  | SEC FONT | 076912bd-5784-4147-9f97-bbb6f64b7af6 | 29-54_FWB | 636f178c-31a1-4bc7-92e4-e7492e5bdfc2 | FWB Trans | [6 empty] | FWB_BC1_29-54_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_BP2_29-142_SECF |  | SEC FONT | 096ee0c5-b1af-4888-a7ae-d2cfe494cd0f | 29-142_FWB | 2eaf3781-eadf-4cb0-b8ee-425f9fea3cfa | FWB Trans | [6 empty] | FWB_BP2_29-142_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2
FWB_BP1_29-50_SECF |  | SEC FONT | e3ba7cc0-6e59-46c6-9b82-ecad9cffea28 | 29-144_FWB | dd56b5c8-5389-4bea-a22c-2c3b90693245 | FWB Trans | [6 empty] | FWB_BP1_29-144_SEC |  | SwitchStatus | SwitchStatus | ABC | None | Read |  | Switch.SwitchStatus | 2

## ManualAnalogSignals
Signal Details
ASIGNAL | [27 empty] | ADVALMLIMITS
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | MEASUREMENT_PSR |  | IDOBJ_AORGROUP | SIGNAL_DEVICEMAPPING | [7 empty] | ASIGNAL_TYPE | MEASUREMENT_TYPE | MEASUREMENT_UNIT | MEASUREMENT_PHASE | MEASUREMENT_SIDE | SIGNAL_DIRECTION | SIGNAL_ANNUALSCH | ASIGNAL_FLOWDIRECTION | ASIGNAL_RATEDVALUE | ASIGNAL_MINSETPOINT | ASIGNAL_MAXSETPOINT | ASIGNAL_TRUST | ASIGNAL_ALARMLIMITS | IDOBJ_NAME | ADVALMLIMITS_ROCALARMGROWTH | ADVALMLIMITS_ROCLIMITGROWTH | ADVALMLIMITS_ROCALARMDROP | ADVALMLIMITS_ROCLIMITDROP | ADVALMLIMITS_FLATLINEALARM | ADVALMLIMITS_FLATLINETIMEOUT | ADVALMLIMITS_CREEPALARM | ADVALMLIMITS_CREEPDEADBAND
Signal Name | Delete | Signal Alias | Signal Custom ID | Device Name | Device Custom ID | Signal AOR Group | Substation | Feeder | Feeder Object | Bank | Bay | Device | Device Mapping | Description | Signal Type | Measurement Type | Display Unit | Phases | Side | Direction | Annual Schedule | Flow Direction | Rated Value | Min. Setpoint | Max. Setpoint | Trust Factor | Alarm Limits | Advanced Alarms - Name | Advanced Alarms - Rate-Of-Growth Alarm | Advanced Alarms - Rate-Of-Growth Limit | Advanced Alarms - Rate-Of-Drop Alarm | Advanced Alarms - Rate-Of-Drop Limit | Advanced Alarm - Flatline Alarm | Advanced Alarm - Flatline Timeout [s] | Advanced Alarm - Creep Alarm | Advanced Alarm - Creep Deadband
FWB_TR2BT_TR2BT_VBC |  | VBC | a443227e-1584-40e2-b4b1-65d158b08c26 | FWB_BP2_BP2_TP | 14c85bc5-b156-4eef-b153-052a625035f9 | FWB Trans | [6 empty] | FWB_BP2_BP2_TP |  | MeasuredValue | Voltage | kV | BC | None | Read |  | Undirected | 0 | 0 | 100 | -1 | VBC_14.49@14.35_13.52@13.39_Trans
FWB_SE_SE_VBAT |  | VBAT | db62b077-1484-4c1e-8cac-ab2508e5f71a | FWB_SE_RET1_RET | 66cb5094-f5aa-4c22-97cc-2cc9ef7b9857 | FWB Trans | [6 empty] | SCD_SE_RET1_RET |  | Custom | Unitless | Default | ABC | None | Read |  | Undirected | 0 | 0 | 100 | -1

## DNP3_RTUs
DNP3 Remote Unit
RTUDNP3 | [55 empty] | COMMCHANNELDNP3
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | IDOBJ_AORGROUP | PSR_LOCATION | EQUIPMENT_CONT |  | RTU_TYPE | REMOTETERMINALUNIT_LISTENONLYMODE¦TERMINALSERVER_LISTENONLYMODE | TERMINALSERVER_DELAYBETWEENCOMMANDS | RTU_TIMEZONE | RTU_USEDST | RTU_ENABLETIMEOFFSET | RTU_TIMEOFFSETPAST | RTU_TIMEOFFSETFUTURE | RTU_PARENTREMOTE | RTU_INITIALPOLL | RTU_INITSEQUENCERETRYPERIOD | REMOTETERMINALUNIT_FASTPOLLING | REMOTETERMINALUNIT_FASTTIMEOUT | REMOTETERMINALUNIT_REQTIMEOUT | RTU_WATCHDOGTIMEOUT | RTU_REDUNDANCYBEHAVIOR | REMOTETERMINALUNIT_COMMRETRIES | REMOTETERMINALUNIT_SCANAFTERCMD | REMOTETERMINALUNIT_CMDSCANDELAY | REMOTETERMINALUNIT_SCANAFTERUCOS | RTUDNP3_SRCADDRESS | RTUDNP3_DESTADDRESS | RTUDNP3_C1UNSOLICITED | RTUDNP3_C2UNSOLICITED | RTUDNP3_C3UNSOLICITED | RTUDNP3_INTEGRITYSCOPE | RTUDNP3_KEEPALIVEPERIOD | RTUDNP3_COLDRESTART | RTUDNP3_ENABLEFREEZE | RTUDNP3_PROTTYPE | RTUDNP3_CLEAR | RTUDNP3_NOACK | RTUDNP3_FREEZECYCLE | RTUDNP3_USERNUMBER | RTUDNP3_ENABLESECURE | RTUDNP3_SECURE | REMOTETERMINALUNIT_PERIODICPOLL | REMOTETERMINALUNIT_POLLCYCLE | RTUDNP3_C1POLL | RTUDNP3_C1POLLCYCLE | RTUDNP3_C2POLL | RTUDNP3_C2POLLCYCLE | RTUDNP3_C3POLL | RTUDNP3_C3POLLCYCLE | RTUDNP3_TIMESYNC | RTUDNP3_TIMESYNCCYCLE | RTUDNP3_TIMESYNCMODE | RTUDNP3_INITIALRESETLINKSTATES | COMMCHANNEL_FRONTEND
Remote Unit (Terminal Server) Name | Delete | Remote Unit Alias | Remote Unit Custom ID | Remote Unit AOR Group | Remote Unit Description | Container Name | Container Custom ID | Remote Unit Type | Listen-Only Mode | Delay Between RTUs [s] | Time Zone | DST-Aware | Enable Time Offset | Time Offset Past [s] | Time Offset Future [s] | Parent Remote | Enable Initial Integrity Scan | Initial Sequence Retry Period | Fast-Scan Period [s] | Fast-Scan Timeout [s] | Request Timeout [s] | Watchdog Timeout [s] | Redundancy Behavior | Command Attempts | Scan After Command | Scan Delay [s] | Scan After Uncommanded Change | Source Address | Destination Address | Class 1 Unsolicited Messages | Class 2 Unsolicited Messages | Class 3 Unsolicited Messages | Scan Scope | Keep Alive Period | RTU Cold Restart | Enable Freeze and Read | Protection Type | Clear | No Acknowledgement | Freeze and Read Periodic Cycle [s] | User Number | Enable Secure | Secure DNP3 Settings | Enable Class 0 Periodic Scan | Class 0 Scan Cycle [s] | Enable Class 1 Periodic Scan | Class 1 Scan Cycle [s] | Enable Class 2 Periodic Scan | Class 2 Scan Cycle [s] | Enable Class 3 Periodic Scan | Class 3 Scan Cycle [s] | Enable Time Synchronization | Synchronization Cycle [s] | Time Sync Mode | Initial Reset Link States | Front-End Name
UTR_FWB_1 |  | UTR_FWB_1__SEL_SEL-2241 | 323d9b8e-b83e-4913-b478-ed6f448e4bd1 | FWB Trans | SEL_SEL-2241 | FREDERICO WESTPHALEN 2 | 7605493c-d9f8-4bfd-9b6e-f9256e5f881b | RTU | FALSE |  | (UTC-03:00) Brasilia | FALSE | TRUE | 20 | 1 |  | TRUE | 100 | 120 | 240 | 120 | 0 | PrioritizeCostFactor | 2 | FALSE | 0 | FALSE | 1 | 2 | FALSE | FALSE | FALSE | Class0123 | 0 | TRUE | FALSE | None | FALSE | FALSE | 3600 | 1 | FALSE |  | TRUE | 3600 | TRUE | 6 | TRUE | 6 | FALSE | 15 | TRUE | 28800 | Serial | TRUE | prod-FrontEndProcessor-Default

## DNP3_UDPLinks
DNP3 Communication Link
COMMLINKDNP3 | [13 empty] | UDPLINK
IDOBJ_NAME | DELETE | COMMLINK_RTU | IDOBJ_ALIAS | COMMLINK_COMMCOST | IDOBJ_AORGROUP | COMMLINK_CONNRETRIES | COMMLINK_LATENCYTIMEOUT | COMMLINKDNP3_PERIODICLINKSTATUSCHECK | COMMLINKDNP3_CONFIRMMODE | COMMLINKDNP3_CONFIRMTIMEOUT | COMMLINK_MEDIUM | COMMLINKDNP3_LINKSTATUSCHECKCYCLE | IDOBJ_CUSTOMID | UDPLINK_IPADDRESS | UDPLINK_DESTPORT | UDPLINK_USESOURCEPORT | UDPLINK_SOURCEPORT | UDPLINK_UDPCONNTIMEOUT
Communication Link Name | Delete | Remote Unit | Communication Link Alias | Cost Factor | Communication Link AOR Group | Connection Attempts | Link Latency [s] | Periodic link status check | Confirm Mode | Confirm Timeout [s] | Communication Medium | Link status check cycle [s] | Communication Link Custom ID | IP Address | Destination Port | Use Source Port | Source Port | Connect Timeout [s]

## DNP3_TCPLinks
DNP3 Communication Link
COMMLINKDNP3 | [13 empty] | TCPIPLINK
IDOBJ_NAME | DELETE | COMMLINK_RTU | IDOBJ_ALIAS | COMMLINK_COMMCOST | IDOBJ_AORGROUP | COMMLINK_CONNRETRIES | COMMLINK_LATENCYTIMEOUT | COMMLINKDNP3_PERIODICLINKSTATUSCHECK | COMMLINKDNP3_CONFIRMMODE | COMMLINKDNP3_CONFIRMTIMEOUT | COMMLINK_MEDIUM | COMMLINKDNP3_LINKSTATUSCHECKCYCLE | IDOBJ_CUSTOMID | TCPIPLINK_IPADDRESS | TCPIPLINK_PORT | TCPIPLINK_TCPCONNTIMEOUT
Communication Link Name | Delete | Remote Unit | Communication Link Alias | Cost Factor | Communication Link AOR Group | Connection Attempts | Link Latency [s] | Periodic link status check | Confirm Mode | Confirm Timeout [s] | Communication Medium | Link status check cycle [s] | Communication Link Custom ID | IP Address | Port | TCP Connection Timeout [s]
UTR_FWB_1_Link1__SAT Hughes |  | UTR_FWB_1 | UTR_FWB_1_Link1 | 0 | FWB Trans | 3 | 2 | FALSE | Never | 10 | SAT Hughes | 3600 | fa3e9d7f-d3e8-4d75-af54-46ff71b25251 | 10.68.29.225 | 20000 | 60
UTR_FWB_1_Link8__SAT Starlink |  | UTR_FWB_1 | UTR_FWB_1_Link8 | 8 | FWB Trans | 3 | 2 | FALSE | Never | 10 | SAT Starlink | 3600 | b5b7b48a-e097-4fe6-be7f-dd18b155df34 | 10.27.0.82 | 29000 | 60
UTR_FWB_1_Link9__SAT Starlink |  | UTR_FWB_1 | UTR_FWB_1_Link9 | 9 | FWB Trans | 3 | 2 | FALSE | Never | 10 | SAT Starlink | 3600 | 2751ae2c-4fe4-41f6-8145-6b3be19a621d | 10.27.0.66 | 29000 | 60
UTR_FWB_1_Link2__M2M Vivo |  | UTR_FWB_1 | UTR_FWB_1_Link2 | 0 | FWB Trans | 3 | 2 | FALSE | Never | 10 | M2M Vivo | 3600 | 0dd65cde-451e-4262-ac70-7c7aaa6630d4 | 99.99.99.51 | 99 | 60

## DNP3_ScanGroups
DNP3 Scan Group
SCANGROUPDNP3
SCANGROUP_RTU | SCANGROUP_SCANCYCLE | SCANGROUPDNP3_OBJGROUP | SCANGROUPDNP3_OBJVARIATION | SCANGROUPDNP3_ALLPOINTS | SCANGROUP_STARTCOORD | SCANGROUP_ENDCOORD
Remote Unit | Scan Cycle [s] | Group | Object Variation | All Points | Start Coordinate | End Coordinate

## DNP3_DiscreteSignals
Signal Details | [22 empty] | Remote Points
DSIGNAL | [22 empty] | REMOTEPOINT | [15 empty] | CHATTERPROCESSING
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | MEASUREMENT_TYPE | IDOBJ_AORGROUP | SIGNAL_DEVICEMAPPING | [7 empty] | DSIGNAL_TYPE | MEASUREMENT_PHASE | MEASUREMENT_SIDE | SIGNAL_DIRECTION | SIGNAL_ANNUALSCH | DSIGNAL_MAPPING | DSIGNAL_NORMALVALUE | DSIGNAL_DOMCATALOG | MEASUREMENT_PSR | IDOBJ_NAME | DELETE | IDOBJ_CUSTOMID | IDOBJ_ALIAS | REMOTEPOINT_TYPE | REMOTEOUTPUT_CMDTIMEOUT | REMOTEOUTPUT_SBOMODE | DINPUTDNP3_DATATYPE¦DOUTPUTDNP3_INDATATYPE | REMOTEINPUTDNP3_INCOORDS¦REMOTEOUTPUTDNP3_INCOORDS | REMOTEINPUTDNP3_OUTREGISTER¦REMOTEOUTPUTDNP3_OUTREGISTER | REMOTEOUTPUTDNP3_POLLAFTERCMD | REMOTEOUTPUTDNP3_POLLDELAY | DOUTPUTDNP3_OUTDATATYPE | REMOTEOUTPUTDNP3_OUTCOORDS | DOUTPUTDNP3_CTRLCODES | DOUTPUTDNP3_CMDTIMES | CHATTERPROCESSING_ENABLE | CHATTERPROCESSING_NUMBEROFCHANGES | CHATTERPROCESSING_OSCILLATIONPERIOD | CHATTERPROCESSING_SUPPRESSIONPERIOD
Signal Name | Delete | Signal Alias | Signal Custom ID | Measurement Type | Signal AOR Group | Substation | Feeder | Feeder Object | Bank | Bay | Device | Device Mapping | Description | Signal Type | Phases | Side | Direction | Annual Schedule | Message Mapping | Normal Value | DOM Catalog | Remote Unit | Remote Point Name | Delete Remote Point | Remote Point Custom ID | Remote Point Alias | Remote Point Type | Command Timeout [s] | Commanding Mode | Input Data Type | Input Coordinates | Output Register | Scan After Command | Scan Delay [s] | Output Data Type | Output Coordinates | Control Codes | Command Times [s] | Enable Oscillation Processing | Number of Changes | Oscillation Period [s] | Suppression Period [s]
FWB_TR1_TR1_P_FSIN |  | FALHA IRIG B - SINCRONISMO | 1365b8c6-83f2-4fc6-ac0b-8ab6972e516f | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_P_FSIN |  | FWB_DS_00002 | 20260413 | Status |  |  | SingleBit | 1105 | FALSE
FWB_TR1_TR1_P_FLK1 |  | FALHA LINK 1 | 90255589-a07b-4d53-ae7e-a9332415436b | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_P_FLK1 |  | FWB_DS_00003 | 20260413 | Status |  |  | SingleBit | 1103 | FALSE
FWB_TR1_TR1_P_FLK2 |  | FALHA LINK 2 | 903518ff-d821-49a4-8b30-cbc87ed17fa2 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_P_FLK2 |  | FWB_DS_00004 | 20260413 | Status |  |  | SingleBit | 1104 | FALSE
FWB_TR1_TR1_P_87_T |  | 87 - TRIP DIFERENCIAL | 38edb42b-085b-4b19-be2f-ae18369f3fcb | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_P_PROT_87_T |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_P_87_T |  | FWB_DS_00005 | 20260413 | Status |  |  | SingleBit | 1106 | FALSE
FWB_TR1AT_P_52-2_62BF |  | 62 - FALHA DISJUNTOR BLOQUEIO | 20e047c9-e77d-4479-9e09-939e1c69f40e | Status | FWB Trans | [6 empty] | FWB_TR1AT_P_52-2_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1AT_P_52-2_62BF |  | FWB_DS_00006 | 20260413 | Status |  |  | SingleBit | 1107 | FALSE
FWB_TR1_TR1_P_FA |  | FASE A | c40fe386-a044-48a4-8d42-b5045606f293 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_P_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_P_FA |  | FWB_DS_00007 | 20260413 | Status |  |  | SingleBit | 1108 | FALSE
FWB_TR1_TR1_P_FB |  | FASE B | 65dfc6dd-ffd5-427b-b818-760ca35b1192 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_P_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_P_FB |  | FWB_DS_00008 | 20260413 | Status |  |  | SingleBit | 1109 | FALSE
FWB_TR1_TR1_P_FC |  | FASE C | 65595b31-ecae-4bd9-9f2b-71631d95f801 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_P_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_P_FC |  | FWB_DS_00009 | 20260413 | Status |  |  | SingleBit | 1110 | FALSE
FWB_TR1AT_TR1AT_P_50F |  | 50 - SOBRECORRENTE INSTANTANEA FASE | 84c6eb20-2177-4a7f-9013-908ddd703f66 | Status | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_P_PROT_50F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_P_50F |  | FWB_DS_00010 | 20260413 | Status |  |  | SingleBit | 1111 | FALSE
FWB_TR1AT_TR1AT_P_50N |  | 50 - SOBRECORRENTE INSTANTANEA NEUTRO | 924376d7-b52e-43b3-b8a9-22096f058b26 | Status | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_P_PROT_50N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_P_50N |  | FWB_DS_00011 | 20260413 | Status |  |  | SingleBit | 1112 | FALSE
FWB_TR1AT_TR1AT_P_51F |  | 51 - SOBRECORRENTE TEMPORIZADA FASE | 6608cebd-4913-4f50-92a9-f02232890be8 | Status | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_P_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_P_51F |  | FWB_DS_00012 | 20260413 | Status |  |  | SingleBit | 1113 | FALSE
FWB_TR1AT_TR1AT_P_51N1 |  | 51 - SOBRECORRENTE TEMPORIZADA NEUTRO E1 | 43ab27e7-d116-4899-9c5c-6f39efc9b12b | Status | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_P_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_P_51N1 |  | FWB_DS_00013 | 20260413 | Status |  |  | SingleBit | 1114 | FALSE
FWB_TR1AT_TR1AT_P_67F |  | 67 - DIRECIONAL SOBRECORRENTE FASE | 98c63cac-56ba-4a31-b03e-f63ee897ebeb | Status | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_P_PROT_67F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_P_67F |  | FWB_DS_00014 | 20260413 | Status |  |  | SingleBit | 1116 | FALSE
FWB_TR1AT_TR1AT_P_67N |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO | 26077309-e786-4c69-b7d8-afce1b4a0382 | Status | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_P_PROT_67N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_P_67N |  | FWB_DS_00015 | 20260413 | Status |  |  | SingleBit | 1115 | FALSE
FWB_TR1BT_P_52-6_62BF |  | 62 - FALHA DISJUNTOR BLOQUEIO | 442b47f2-7d53-494a-8529-21f9be18a2af | Status | FWB Trans | [6 empty] | FWB_TR1BT_P_52-10_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_P_52-6_62BF |  | FWB_DS_00016 | 20260413 | Status |  |  | SingleBit | 1117 | FALSE
FWB_TR1BT_TR1BT_P_50F |  | 50 - SOBRECORRENTE INSTANTANEA FASE | 6580cbdd-8cf4-4e4b-94c2-3195d8659618 | Status | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_P_PROT_50F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_P_50F |  | FWB_DS_00017 | 20260413 | Status |  |  | SingleBit | 1118 | FALSE
FWB_TR1BT_TR1BT_P_50N |  | 50 - SOBRECORRENTE INSTANTANEA NEUTRO | 0989f5cf-f325-4b92-bda3-98f409019ae7 | Status | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_P_PROT_50N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_P_50N |  | FWB_DS_00018 | 20260413 | Status |  |  | SingleBit | 1119 | FALSE
FWB_TR1BT_TR1BT_P_51F |  | 51 - SOBRECORRENTE TEMPORIZADA FASE | 05290ecf-d060-41a6-8097-70a818bdadb0 | Status | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_P_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_P_51F |  | FWB_DS_00019 | 20260413 | Status |  |  | SingleBit | 1120 | FALSE
FWB_TR1BT_TR1BT_P_51N1 |  | 51 - SOBRECORRENTE TEMPORIZADA NEUTRO E1 | ff028f4d-0b33-428d-a31f-439c61e4a92c | Status | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_P_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_P_51N1 |  | FWB_DS_00020 | 20260413 | Status |  |  | SingleBit | 1121 | FALSE
FWB_TR1_TR1_A_FSIN |  | FALHA IRIG B - SINCRONISMO | 1cb3af40-f890-4d7a-b683-0418fd302384 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_A_FSIN |  | FWB_DS_00028 | 20260413 | Status |  |  | SingleBit | 1132 | FALSE
FWB_TR1_TR1_A_FLK1 |  | FALHA LINK 1 | 8f762d84-6e2b-459e-9deb-7cd38621fc99 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_A_FLK1 |  | FWB_DS_00029 | 20260413 | Status |  |  | SingleBit | 1130 | FALSE
FWB_TR1_TR1_A_FLK2 |  | FALHA LINK 2 | 13f86309-6409-4560-92de-5247f12c5ceb | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_A_FLK2 |  | FWB_DS_00030 | 20260413 | Status |  |  | SingleBit | 1131 | FALSE
FWB_TR1_TR1_A_87_T |  | 87 - TRIP DIFERENCIAL | ba5054be-f2b6-4654-91a7-e65aa3d337c3 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_A_PROT_87_T |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_A_87_T |  | FWB_DS_00031 | 20260413 | Status |  |  | SingleBit | 1133 | FALSE
FWB_TR1AT_A_52-2_62BF |  | 62 - FALHA DISJUNTOR BLOQUEIO | 2ec65c3f-ddbe-47bb-bb24-7d0779a11047 | Status | FWB Trans | [6 empty] | FWB_TR1AT_A_52-2_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1AT_A_52-2_62BF |  | FWB_DS_00032 | 20260413 | Status |  |  | SingleBit | 1134 | FALSE
FWB_TR1_TR1_A_FA |  | FASE A | 766b30e4-de17-4c91-aaed-4491d7c02c05 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_A_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_A_FA |  | FWB_DS_00033 | 20260413 | Status |  |  | SingleBit | 1135 | FALSE
FWB_TR1_TR1_A_FB |  | FASE B | 90dfd9ba-b7b3-4e93-b096-7d6bfcde1938 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_A_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_A_FB |  | FWB_DS_00034 | 20260413 | Status |  |  | SingleBit | 1136 | FALSE
FWB_TR1_TR1_A_FC |  | FASE C | d4c11b14-aa06-431f-9108-767cd371c389 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_A_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_A_FC |  | FWB_DS_00035 | 20260413 | Status |  |  | SingleBit | 1137 | FALSE
FWB_TR1AT_TR1AT_A_50F |  | 50 - SOBRECORRENTE INSTANTANEA FASE | 0c8400a4-8de0-4f01-bb61-0e2aa4c14077 | Status | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_A_PROT_50F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_A_50F |  | FWB_DS_00036 | 20260413 | Status |  |  | SingleBit | 1138 | FALSE
FWB_TR1AT_TR1AT_A_50N |  | 50 - SOBRECORRENTE INSTANTANEA NEUTRO | ff13e902-7d53-4d3d-8f1e-e4b4a0e3725b | Status | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_A_PROT_50N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_A_50N |  | FWB_DS_00037 | 20260413 | Status |  |  | SingleBit | 1139 | FALSE
FWB_TR1AT_TR1AT_A_51F |  | 51 - SOBRECORRENTE TEMPORIZADA FASE | ade0ca52-b112-40b7-979c-c9316a83fded | Status | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_A_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_A_51F |  | FWB_DS_00038 | 20260413 | Status |  |  | SingleBit | 1140 | FALSE
FWB_TR1AT_TR1AT_A_51N1 |  | 51 - SOBRECORRENTE TEMPORIZADA NEUTRO E1 | 6e00db30-1793-400a-bf81-bf6b6b5d26d6 | Status | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_A_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_A_51N1 |  | FWB_DS_00039 | 20260413 | Status |  |  | SingleBit | 1141 | FALSE
FWB_TR1BT_TR1BT_A_67F |  | 67 - DIRECIONAL SOBRECORRENTE FASE | 2fa0bd86-4534-412a-bec3-4e72a62e2cd3 | Status | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_A_PROT_67F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_67F |  | FWB_DS_00040 | 20260413 | Status |  |  | SingleBit | 1143 | FALSE
FWB_TR1BT_TR1BT_A_67N |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO | e863e9d3-b684-4f8c-b0c0-ffbda63f643d | Status | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_A_PROT_67N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_67N |  | FWB_DS_00041 | 20260413 | Status |  |  | SingleBit | 1142 | FALSE
FWB_TR1BT_A_52-6_62BF |  | 62 - FALHA DISJUNTOR BLOQUEIO | 9c827aa1-c9c3-4d9b-8f7c-add75fb0bce5 | Status | FWB Trans | [6 empty] | FWB_TR1BT_A_52-10_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_A_52-6_62BF |  | FWB_DS_00042 | 20260413 | Status |  |  | SingleBit | 1144 | FALSE
FWB_TR1BT_TR1BT_A_50F |  | 50 - SOBRECORRENTE INSTANTANEA FASE | 40b81bf1-0e27-4e91-9cf7-cacb1200351a | Status | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_A_PROT_50F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_50F |  | FWB_DS_00043 | 20260413 | Status |  |  | SingleBit | 1145 | FALSE
FWB_TR1BT_TR1BT_A_50N |  | 50 - SOBRECORRENTE INSTANTANEA NEUTRO | e0870029-75a9-42dd-8e98-ff166d729393 | Status | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_A_PROT_50N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_50N |  | FWB_DS_00044 | 20260413 | Status |  |  | SingleBit | 1146 | FALSE
FWB_TR1BT_TR1BT_A_51F |  | 51 - SOBRECORRENTE TEMPORIZADA FASE | 8c21a0bb-032f-42de-94b2-152a38064cde | Status | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_A_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_51F |  | FWB_DS_00045 | 20260413 | Status |  |  | SingleBit | 1147 | FALSE
FWB_TR1BT_TR1BT_A_51N1 |  | 51 - SOBRECORRENTE TEMPORIZADA NEUTRO E1 | 41f4aace-4eea-4a9d-92f7-1b8f4ec7ba3f | Status | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_A_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_51N1 |  | FWB_DS_00046 | 20260413 | Status |  |  | SingleBit | 1148 | FALSE
FWB_TR1AT_P_52-2_BBA1 |  | BOBINA ABERTURA 1 | 720063b9-dd41-4484-aa53-7941f5637957 | Status | FWB Trans | [6 empty] | FWB_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR1AT_P_52-2_BBA1 |  | FWB_DS_00047 | 20260413 | Status |  |  | SingleBit | 1149 | FALSE
FWB_TR1AT_P_52-2_BBA2 |  | BOBINA ABERTURA 2 | d5572bd9-b15c-4798-888a-7a37d0ebeae2 | Status | FWB Trans | [6 empty] | FWB_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR1AT_P_52-2_BBA2 |  | FWB_DS_00048 | 20260413 | Status |  |  | SingleBit | 1150 | FALSE
FWB_TR1BT_P_52-6_BBA1 |  | BOBINA ABERTURA 1 | ea235699-e03d-4e62-adcf-fc7fb97db1ec | Status | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR1BT_P_52-6_BBA1 |  | FWB_DS_00049 | 20260413 | Status |  |  | SingleBit | 1151 | FALSE
FWB_TR1BT_P_52-6_BBA2 |  | BOBINA ABERTURA 2 | 2bbfd668-64bf-466f-854d-c51f3b76592c | Status | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR1BT_P_52-6_BBA2 |  | FWB_DS_00050 | 20260413 | Status |  |  | SingleBit | 1152 | FALSE
FWB_TR1AT_A_52-2_BBA1 |  | BOBINA ABERTURA 1 | 77aecebb-65ba-4551-9bd9-bce5a7347a17 | Status | FWB Trans | [6 empty] | FWB_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR1AT_A_52-2_BBA1 |  | FWB_DS_00051 | 20260413 | Status |  |  | SingleBit | 1153 | FALSE
FWB_TR1AT_A_52-2_BBA2 |  | BOBINA ABERTURA 2 | ea1ab82e-9c95-496f-8703-c66e232a092a | Status | FWB Trans | [6 empty] | FWB_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR1AT_A_52-2_BBA2 |  | FWB_DS_00052 | 20260413 | Status |  |  | SingleBit | 1154 | FALSE
FWB_TR1BT_A_52-6_BBA1 |  | BOBINA ABERTURA 1 | d4da7e65-9517-4d30-b4fe-77f72bc5f5dd | Status | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR1BT_A_52-6_BBA1 |  | FWB_DS_00053 | 20260413 | Status |  |  | SingleBit | 1155 | FALSE
FWB_TR1BT_A_52-6_BBA2 |  | BOBINA ABERTURA 2 | ff03d51c-cff7-4edb-9760-5c31ad1a60a7 | Status | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR1BT_A_52-6_BBA2 |  | FWB_DS_00054 | 20260413 | Status |  |  | SingleBit | 1156 | FALSE
FWB_TR1AT_52-2_SF6A |  | ALARME BAIXA PRESSAO SF6 | 76152d6e-7962-4699-8340-69f59b3cdea5 | Status | FWB Trans | [6 empty] | FWB_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1AT_52-2_SF6A |  | FWB_DS_00055 | 20260413 | Status |  |  | SingleBit | 1173 | FALSE
FWB_TR1AT_52-2_SF6B |  | BLOQUEIO BAIXA PRESSAO SF6 | 6c4f7972-c211-4129-96c8-cdf8c2140753 | Status | FWB Trans | [6 empty] | FWB_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1AT_52-2_SF6B |  | FWB_DS_00056 | 20260413 | Status |  |  | SingleBit | 1174 | FALSE
FWB_TR1AT_52-2_CCMO |  | FALTA VCC MOTOR | 05820b9b-2528-4970-ade6-4a9a03df0140 | Status | FWB Trans | [6 empty] | FWB_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1AT_52-2_CCMO |  | FWB_DS_00057 | 20260413 | Status |  |  | SingleBit | 1175 | FALSE
FWB_TR1AT_TR1AT_CCFL |  | FALTA VCC | 7866ce08-fcb1-4c61-ada9-4d3e3c658e2f | Status | FWB Trans | [6 empty] | FWB_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_CCFL |  | FWB_DS_00058 | 20260413 | Status |  |  | SingleBit | 1176 | FALSE
FWB_TR1_TR1_86 |  | 86 - BLOQUEIO | 39cd532c-6f4b-4732-904d-88b0760509bb | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_86 |  | FWB_DS_00059 | 20260413 | Status |  |  | SingleBit | 1177 | FALSE
FWB_TR1AT_89-8_DSEC |  | DEFEITO SECCIONADORA | e514444c-1cc4-4dc6-88f8-ff17a538d35c | Status | FWB Trans | [6 empty] | FWB_TR1AT_89-8_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1AT_89-8_DSEC |  | FWB_DS_00060 | 20260413 | Status |  |  | SingleBit | 1178 | FALSE
FWB_TR1_TR1_63CA |  | 63 - ALARME BUCHHOLZ CDC | 44fced58-4e40-40f7-96f6-5ef6bc77b077 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_63CA |  | FWB_DS_00061 | 20260413 | Status |  |  | SingleBit | 1179 | FALSE
FWB_TR1_TR1_63CD |  | 63 - TRIP BUCHHOLZ CDC | 19599116-5c7c-4d9d-b09b-745b9584da5e | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_63CD |  | FWB_DS_00062 | 20260413 | Status |  |  | SingleBit | 1180 | FALSE
FWB_TR1_TR1_20TA |  | 20 - ALARME VALVULA TRAFO | ab0edc22-608d-4b92-b323-e7cbb2256b75 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_20TA |  | FWB_DS_00063 | 20260413 | Status |  |  | SingleBit | 1181 | FALSE
FWB_TR1_TR1_20CA |  | 20 - ALARME VALVULA CDC | b2035492-e98e-427e-a898-50cc17d7e662 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_20CA |  | FWB_DS_00064 | 20260413 | Status |  |  | SingleBit | 1182 | FALSE
FWB_TR1_TR1_20CD |  | 20 - TRIP VALVULA CDC | 6c4e6360-c2bc-4f20-b18d-62dd7cb324d8 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_20CD |  | FWB_DS_00065 | 20260413 | Status |  |  | SingleBit | 1183 | FALSE
FWB_TR1_TR1_PERP |  | PERMISSAO PARALELISMO | fb494d15-92db-45f4-9a05-6526858260e4 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NÃO PERMITIDO@PERMITIDO___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_PERP |  | FWB_DS_00066 | 20260413 | Status |  |  | SingleBit | 1184 | FALSE
FWB_TR1_TR1_63TA |  | 63 - ALARME BUCHHOLZ TRAFO | 1fcc19d8-8d0b-47ae-87dc-35189545ef18 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_63TA |  | FWB_DS_00067 | 20260413 | Status |  |  | SingleBit | 1185 | FALSE
FWB_TR1_TR1_63TD |  | 63 - TRIP BUCHHOLZ TRAFO | 2d403046-1e59-4c5f-a61b-4cabc6413f2c | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_63TD |  | FWB_DS_00068 | 20260413 | Status |  |  | SingleBit | 1186 | FALSE
FWB_TR1_TR1_71T |  | 71 - NIVEL OLEO TRAFO | 49beaf94-5653-49f0-a317-4a20ebb51991 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_71T |  | FWB_DS_00069 | 20260413 | Status |  |  | SingleBit | 1187 | FALSE
FWB_TR1_TR1_20TD |  | 20 - TRIP VALVULA TRAFO | 4b8bd1f5-55ac-44f8-8bb0-3bdf8ae45410 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_20TD |  | FWB_DS_00070 | 20260413 | Status |  |  | SingleBit | 1188 | FALSE
FWB_TR1BT_52-6_43LR |  | 43 - CHAVE LOCAL REMOTO | 315888b3-53eb-49a3-93ab-f7ea46746e6f | Status | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_TR1BT_52-6_43LR |  | FWB_DS_00071 | 20260413 | Status |  |  | SingleBit | 1189 | FALSE
FWB_TR1BT_TR1BT_CCFL |  | FALTA VCC | 738e2584-f233-48f1-86bb-15f3b36bf1e4 | Status | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_CCFL |  | FWB_DS_00072 | 20260413 | Status |  |  | SingleBit | 1190 | FALSE
FWB_TR1_TR1_71C |  | 71 - NIVEL OLEO CDC | 84005fcd-33d5-4c80-8872-ed2f62d39f37 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_71C |  | FWB_DS_00073 | 20260413 | Status |  |  | SingleBit | 1191 | FALSE
FWB_TR1BT_52-6_SF6A |  | ALARME BAIXA PRESSAO SF6 | af341686-cdeb-496d-9b5a-5fe2935af6d3 | Status | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1BT_52-6_SF6A |  | FWB_DS_00074 | 20260413 | Status |  |  | SingleBit | 1192 | FALSE
FWB_TR1BT_52-6_SF6B |  | BLOQUEIO BAIXA PRESSAO SF6 | f15c7c67-6c3c-472d-bff2-bafc29ba1c2c | Status | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1BT_52-6_SF6B |  | FWB_DS_00075 | 20260413 | Status |  |  | SingleBit | 1193 | FALSE
FWB_TR1BT_52-6_CCMO |  | FALTA VCC MOTOR | 16286c3c-1068-43d4-bee1-af10dadf91ab | Status | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1BT_52-6_CCMO |  | FWB_DS_00076 | 20260413 | Status |  |  | SingleBit | 1194 | FALSE
FWB_TR1AT_52-2_43LR |  | 43 - CHAVE LOCAL REMOTO | 51cbc9fd-dd59-40ae-8bde-4937bd4bf57c | Status | FWB Trans | [6 empty] | FWB_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom___INV_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_TR1AT_52-2_43LR |  | FWB_DS_00077 | 20260413 | Status |  |  | SingleBit | 1195 | FALSE
FWB_TR1AT_89-10_DSEC |  | DEFEITO SECCIONADORA | 6695ec84-35dd-4ccf-b13e-bb41145fbd27 | Status | FWB Trans | [6 empty] | FWB_TR1AT_89-10_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1AT_89-10_DSEC |  | FWB_DS_00078 | 20260413 | Status |  |  | SingleBit | 1196 | FALSE
FWB_TR1_TR1_43TC |  | 43 - CHAVE TELECOMANDO | a286dad2-66a3-4817-a4da-48701a963171 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_43TC |  | FWB_DS_00079 | 20260413 | Status |  |  | SingleBit | 1203 | FALSE
FWB_TR1_TR1_INTR |  | 20 63 87 - PROTECOES INTRINSECAS | b575dec3-0e8e-485b-aed6-8297fe0dfc9a | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_INTR |  | FWB_DS_00081 | 20260413 | Status |  |  | SingleBit | 1206 | FALSE
FWB_TR1AT_TR1AT_FPBR |  | FALTA POTENCIAL BARRA | 919dc48c-3229-4c71-915a-9cfa1caad85f | Status | FWB Trans | [6 empty] | FWB_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_FPBR |  | FWB_DS_00082 | 20260413 | Status |  |  | SingleBit | 1100 | FALSE
FWB_TR1AT_52-2_BBFC |  | BOBINA FECHAMENTO | 44ec94fc-d889-47b3-ba9f-f6b69c6f1116 | Status | FWB Trans | [6 empty] | FWB_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR1AT_52-2_BBFC |  | FWB_DS_00083 | 20260413 | Status |  |  | SingleBit | 1212 | FALSE
FWB_TR1BT_52-6_BBFC |  | BOBINA FECHAMENTO | 4f3749ff-b147-4691-8464-e06b73085ca3 | Status | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR1BT_52-6_BBFC |  | FWB_DS_00084 | 20260413 | Status |  |  | SingleBit | 1213 | FALSE
FWB_TR1AT_52-2_MOLA |  | MOLA | 4018236c-fa18-47f2-8156-ca12fe3e4cf0 | Status | FWB Trans | [6 empty] | FWB_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1AT_52-2_MOLA |  | FWB_DS_00085 | 20260413 | Status |  |  | SingleBit | 1215 | FALSE
FWB_TR1BT_52-6_MOLA |  | MOLA | 8837c2d1-bd72-4c0f-8189-9ca24d5606c5 | Status | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1BT_52-6_MOLA |  | FWB_DS_00086 | 20260413 | Status |  |  | SingleBit | 1214 | FALSE
FWB_TR1AT_89-12_DSEC |  | DEFEITO SECCIONADORA | 9c714386-c5f5-4171-a8fb-82d4c1ba8eda | Status | FWB Trans | [6 empty] | FWB_TR1AT_89-12_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1AT_89-12_DSEC |  | FWB_DS_00089 | 20260413 | Status |  |  | SingleBit | 1227 | FALSE
FWB_TR1BT_89-40_DSEC |  | DEFEITO SECCIONADORA | 2057e1a4-a478-4f9b-988b-663c878378ef | Status | FWB Trans | [6 empty] | FWB_TR1BT_89-40_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1BT_89-40_DSEC |  | FWB_DS_00090 | 20260413 | Status |  |  | SingleBit | 1228 | FALSE
FWB_TR1_TR1_90LR |  | 43 - CHAVE LOCAL REMOTO RELE 90 | 252d54da-0ebe-4d2d-8fc6-351c923f6c67 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TAP_REG |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom___INV_S_TS_SS | 2 |  | UTR_FWB_1 | FWB_TR1_TR1_90LR |  | FWB_DS_00094 | 20260413 | Status |  |  | SingleBit | 2203 | FALSE
FWB_TR1_TR1_86CC |  | FALTA VCC CIRCUITO RELE 86 | 4b9bcb69-b1dc-4a77-af0d-7afd4bf9daff | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_86CC |  | FWB_DS_00096 | 20260413 | Status |  |  | SingleBit | 2313 | FALSE
FWB_TR1_TR1_FVF |  | FALHA VENTILACAO FORCADA | 3d5bbfda-28f1-4f95-926a-c47ddde6a28c | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_FVF |  | FWB_DS_00098 | 20260413 | Status |  |  | SingleBit | 2348 | FALSE
FWB_TR1_TR1_CAFL |  | FALTA VCA | 7fb89951-da6e-4285-b395-c93b471bfe5d | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_CAFL |  | FWB_DS_00099 | 20260413 | Status |  |  | SingleBit | 2349 | FALSE
FWB_TR1_TR1_BCDC |  | BLOQUEIO CDC | 676b40df-ce9f-4249-97be-81458c4db020 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_BCDC |  | FWB_DS_00100 | 20260413 | Status |  |  | SingleBit | 2350 | FALSE
FWB_TR1_TR1_CDLM |  | CDC LOCAL MANUAL | b59034f0-d614-4234-8f8d-b5e431ec54ad | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___MANUAL DESATIVOU@MANUAL ATIVOU___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_CDLM |  | FWB_DS_00101 | 20260413 | Status |  |  | SingleBit | 2351 | FALSE
FWB_TR1_TR1_CDLA |  | CDC LOCAL AUTOMATICO | 713d6fcf-de1b-4231-b6b4-10730579f725 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___AUTOM DESATIVADO@AUTOM ATIVOU___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_CDLA |  | FWB_DS_00102 | 20260413 | Status |  |  | SingleBit | 2353 | FALSE
FWB_TR1_TR1_CDRA |  | CDC REMOTO AUTOMATICO | 5c7fda75-15bd-4578-b6d5-5092cc4434e6 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___AUTOM DESATIVADO@AUTOM ATIVOU___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_CDRA |  | FWB_DS_00103 | 20260413 | Status |  |  | SingleBit | 2352 | FALSE
FWB_TR1_TR1_DR90 |  | DEFEITO RELE 90 | 74f7cd98-c569-4f9b-8d46-976e807e6500 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_DR90 |  | FWB_DS_00104 | 20260413 | Status |  |  | SingleBit | 2354 | FALSE
FWB_TR1AT_TR1AT_OI |  | OPERACAO INDEVIDA SECCIONADORA | 08a80ace-a539-4ac7-b245-0c477dc6a427 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_OI |  | FWB_DS_00106 | 20260413 | Status |  |  | SingleBit | 9002 | FALSE
FWB_TR1_TR1_P_DR |  | DEFEITO RELE | cb280fa1-0607-49bc-b905-03a17e4f3710 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_P_DR |  | FWB_DS_00109 | 20260413 | Status |  |  | SingleBit | 2316 | FALSE
FWB_TR1_TR1_P_FCOM |  | FALHA COMUNICACAO | 184c4c38-0170-44ec-8f30-f5f3b459e971 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_P_FCOM |  | FWB_DS_00110 | 20260413 | Status |  |  | SingleBit | 1157 | FALSE
FWB_TR1_TR1_SCAR |  | SECADOR DE AR | 97696018-edaf-4940-afa3-0e170b268926 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_SCAR |  | FWB_DS_00111 | 20260413 | Status |  |  | SingleBit | 9009 | FALSE
FWB_TR1_CDC_SCAR |  | SECADOR DE AR | c7385c2d-09e4-43ee-8958-3cfdd8830edf | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_CDC_SCAR |  | FWB_DS_00112 | 20260413 | Status |  |  | SingleBit | 9010 | FALSE
FWB_TR1_TR1_TOA |  | 26 - ALARME TEMPERATURA OLEO | e4a93460-eb2d-4d83-81c0-f1a09406dc33 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_TOA |  | FWB_DS_00113 | 20260413 | Status |  |  | SingleBit | 9011 | FALSE
FWB_TR1_TR1_TOD |  | 26 - TRIP TEMPERATURA OLEO | e346387a-34a9-4577-bf02-f396a05a797f | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_TOD |  | FWB_DS_00114 | 20260413 | Status |  |  | SingleBit | 9012 | FALSE
FWB_TR1BT_TR1BT_TEA |  | 49 - ALARME TEMPERATURA ENROLAMENTO | b9e0cb05-3550-4cb1-8427-4197d02771c9 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_TEA |  | FWB_DS_00115 | 20260413 | Status |  |  | SingleBit | 9013 | FALSE
FWB_TR1BT_TR1BT_TED |  | 49 - TRIP TEMPERATURA ENROLAMENTO | db24e25d-df10-4912-8dbf-4b6d79396978 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_TED |  | FWB_DS_00116 | 20260413 | Status |  |  | SingleBit | 9014 | FALSE
FWB_TR1AT_TR1AT_TEA |  | 49 - ALARME TEMPERATURA ENROLAMENTO | c653d28e-68cb-42e9-b1cd-f2d27a070504 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_TEA |  | FWB_DS_00117 | 20260413 | Status |  |  | SingleBit | 9015 | FALSE
FWB_TR1AT_TR1AT_TED |  | 49 - TRIP TEMPERATURA ENROLAMENTO | d6f07544-2945-4ece-838c-6692505cae27 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_TED |  | FWB_DS_00118 | 20260413 | Status |  |  | SingleBit | 9016 | FALSE
FWB_TR1_TR1_MDCD |  | MINI DISJUNTOR CDC | 249f3d4e-9d7c-4776-971c-24af8b5f9cde | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_MDCD |  | FWB_DS_00121 | 20260413 | Status |  |  | SingleBit | 9022 | FALSE
FWB_TR1AT_TR1AT_P_67 |  | 67 - FUNCAO DIRECIONAL SOBRECORRENTE | d5866e1f-387e-43d3-bfb6-ea597d9dafcc | Status | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_P_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_P_67 |  | FWB_DS_00125 | 20260413 | Status |  |  | SingleBit | 9031 | FALSE
FWB_TR1AT_TR1AT_P_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | d685aaa5-e542-4058-a5ab-53ed8007df37 | Status | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_P_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_P_67FT |  | FWB_DS_00127 | 20260413 | Status |  |  | SingleBit | 9033 | FALSE
FWB_TR1AT_TR1AT_P_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | 5dffad79-b7cc-4d39-9bd9-2a9daa2cb351 | Status | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_P_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_P_67NT |  | FWB_DS_00129 | 20260413 | Status |  |  | SingleBit | 9035 | FALSE
FWB_TR1AT_TR1AT_P_81E1 |  | 81 - TRIP SUB/SOBRE FREQUENCIA E1 | 793faaf3-3f6a-46e7-9a62-c6b577dd5003 | Status | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_P_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_P_81E1 |  | FWB_DS_00132 | 20260413 | Status |  |  | SingleBit | 9038 | FALSE
FWB_TR1AT_TR1AT_P_81E2 |  | 81 - TRIP SUB/SOBRE FREQUENCIA E2 | e8fe2cfb-a84f-450c-9041-3256e088a03f | Status | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_P_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_P_81E2 |  | FWB_DS_00133 | 20260413 | Status |  |  | SingleBit | 9039 | FALSE
FWB_TR1AT_TR1AT_P_81O1 |  | 81 - TRIP SOBRE FREQUENCIA E1 | 58d4bf71-eb56-4980-b69a-a2896c1d384c | Status | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_P_PROT_81O1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_P_81O1 |  | FWB_DS_00134 | 20260413 | Status |  |  | SingleBit | 9040 | FALSE
FWB_TR1AT_TR1AT_P_FUTP |  | FALHA FUSIVEL TP | 79eebd18-e93b-4540-9e38-ce54882d7ab5 | Status | FWB Trans | [6 empty] | FWB_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1AT_TR1AT_P_FUTP |  | FWB_DS_00135 | 20260413 | Status |  |  | SingleBit | 9041 | FALSE
FWB_TR1_TR1_A_DR |  | DEFEITO RELE | ec6adb87-6690-4889-81c3-6123a0c5c2fe | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_A_DR |  | FWB_DS_00141 | 20260413 | Status |  |  | SingleBit | 2317 | FALSE
FWB_TR1_TR1_A_FCOM |  | FALHA COMUNICACAO | aecb13a6-beeb-4ed9-8bba-ee6287ee3665 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_A_FCOM |  | FWB_DS_00142 | 20260413 | Status |  |  | SingleBit | 1158 | FALSE
FWB_TR1BT_TR1BT_A_67 |  | 67 - FUNCAO DIRECIONAL SOBRECORRENTE | e7dcae39-5c29-4f44-8c10-0c558b7ca15f | Status | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_A_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_67 |  | FWB_DS_00149 | 20260413 | Status |  |  | SingleBit | 9055 | FALSE
FWB_TR1BT_TR1BT_A_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | 4dd532c5-9de8-436c-8476-9d5181ffef05 | Status | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_A_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_67FT |  | FWB_DS_00151 | 20260413 | Status |  |  | SingleBit | 9057 | FALSE
FWB_TR1BT_TR1BT_A_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | f79d716b-291c-4f61-bc64-0ac95dbbe037 | Status | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_A_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_67NT |  | FWB_DS_00153 | 20260413 | Status |  |  | SingleBit | 9059 | FALSE
FWB_TR1BT_TR1BT_A_81BLOQ |  | 81 BLOQUEIO DINAMICO | 1b839be0-f385-4821-b763-c1a95afec028 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS | 2 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_81BLOQ |  | FWB_DS_00156 | 20260413 | Status |  |  | SingleBit | 9062 | FALSE
FWB_TR1BT_TR1BT_A_81E1 |  | 81 - TRIP SUB/SOBRE FREQUENCIA E1 | 994a8c31-1ce9-4c81-8be4-2477ab716a37 | Status | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_A_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_81E1 |  | FWB_DS_00157 | 20260413 | Status |  |  | SingleBit | 9063 | FALSE
FWB_TR1BT_TR1BT_A_81E2 |  | 81 - TRIP SUB/SOBRE FREQUENCIA E2 | aad03cb0-dcb8-464c-8429-a5cb8e41edfc | Status | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_A_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_81E2 |  | FWB_DS_00158 | 20260413 | Status |  |  | SingleBit | 9064 | FALSE
FWB_TR1BT_TR1BT_A_81E3 |  | 81 - TRIP SUB/SOBRE FREQUENCIA E3 | b74c097e-c289-4131-ba0b-91c16e1d85f4 | Status | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_A_PROT_81E3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_81E3 |  | FWB_DS_00159 | 20260413 | Status |  |  | SingleBit | 9065 | FALSE
FWB_TR1BT_TR1BT_A_81E4 |  | 81 - TRIP SUB/SOBRE FREQUENCIA E4 | 9eba0019-9f3c-465d-a31a-c4e4b7455a3c | Status | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_A_PROT_81E4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_81E4 |  | FWB_DS_00160 | 20260413 | Status |  |  | SingleBit | 9066 | FALSE
FWB_TR1BT_TR1BT_A_81E5 |  | 81 - TRIP SUB/SOBRE FREQUENCIA E5 | f9e76c30-98e8-4c5a-80cf-d646f7013c19 | Status | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_A_PROT_81E5 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_81E5 |  | FWB_DS_00161 | 20260413 | Status |  |  | SingleBit | 9067 | FALSE
FWB_TR1BT_TR1BT_A_81O1 |  | 81 - TRIP SOBRE FREQUENCIA E1 | 61104524-1166-48a8-9696-b7de2313e940 | Status | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_A_PROT_81O1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_81O1 |  | FWB_DS_00162 | 20260413 | Status |  |  | SingleBit | 9068 | FALSE
FWB_TR1BT_TR1BT_A_FUTP |  | FALHA FUSIVEL TP | eb5e4618-089f-49c8-a119-022630a68be7 | Status | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_FUTP |  | FWB_DS_00163 | 20260413 | Status |  |  | SingleBit | 9069 | FALSE
FWB_TR1_TR1_50CD |  | 50 - SOBRECORRENTE CDC | f0400b3b-f627-4bc7-bcb4-0aa7ef63a128 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_50CD |  | FWB_DS_00168 | 20260413 | Status |  |  | SingleBit | 9074 | FALSE
FWB_TR1_TR1_59CD |  | 59 - BLOQUEIO CDC SOBRETENSAO | 8e2b3fc6-8535-4b90-9cc9-f14b58fe36e7 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_59CD |  | FWB_DS_00169 | 20260413 | Status |  |  | SingleBit | 9075 | FALSE
FWB_TR1_TR1_27CD |  | 27 - BLOQUEIO SUBTENSAO CDC | 7865b456-3abb-41a2-992b-0153469c8a60 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_27CD |  | FWB_DS_00170 | 20260413 | Status |  |  | SingleBit | 9076 | FALSE
FWB_TR1_TR1_FPAR |  | FALHA SINCRONISMO PARALELISMO | 29d2df55-7364-431e-a6ef-1c80300cf7d9 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_FPAR |  | FWB_DS_00172 | 20260413 | Status |  |  | SingleBit | 9078 | FALSE
FWB_TR12_TR12_FCSP |  | FALHA COMUNICACAO SPS | 22c83d5b-9b9e-40aa-9b6f-d6dc048db512 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR12_TR12_FCSP |  | FWB_DS_00173 | 20260413 | Status |  |  | SingleBit | 2210 | FALSE
FWB_TR1_TR1_CDCO |  | ESTADO_PARALELISMO | f693b39a-5966-4ea9-bd7c-8db357b43ac5 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TAP_REG |  | Custom | ABC | None | Read |  | null@null@null___MESTRE@INDIVIDUAL@COMANDO___Custom___admsINV_D_TS_SS | 2 |  | UTR_FWB_1 | CNC_TR1_TR1_CDCO |  | 6f1ae994-910c-4c57-b39b-27de4829f45e | 20260415 | Status |  |  | MultiCoord | 2201;2202 | FALSE
FWB_TR1BT_TR1BT_A_81U1 |  | AJUSTE PARA 81 E1 | 146f5b1f-abdf-4411-993b-f8854eb1b5ac | Status | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_81U1 |  | FWB_DS_00021 | 20260413 | Status | 30 | DirectOperate | SingleBit | 1122 | FALSE | FALSE | 5 | SingleCoord | 221 | ClosePulseOn | 0.25
FWB_TR1BT_TR1BT_A_81U2 |  | AJUSTE PARA 81 E2 | f0803b46-2abe-41ad-a728-7321726af97c | Status | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_81U2 |  | FWB_DS_00022 | 20260413 | Status | 30 | DirectOperate | SingleBit | 1123 | FALSE | FALSE | 5 | SingleCoord | 222 | ClosePulseOn | 0.25
FWB_TR1BT_TR1BT_A_81U3 |  | AJUSTE PARA 81 E3 | db7991d5-21ed-4723-afcf-14aaa4587b10 | Status | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_81U3 |  | FWB_DS_00023 | 20260413 | Status | 30 | DirectOperate | SingleBit | 1124 | FALSE | FALSE | 5 | SingleCoord | 223 | ClosePulseOn | 0.25
FWB_TR1BT_TR1BT_A_81U4 |  | AJUSTE PARA 81 E4 | ac0a134d-810e-4b02-8045-102c52a19662 | Status | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_81U4 |  | FWB_DS_00024 | 20260413 | Status | 30 | DirectOperate | SingleBit | 1125 | FALSE | FALSE | 5 | SingleCoord | 224 | ClosePulseOn | 0.25
FWB_TR1BT_TR1BT_A_81U5 |  | AJUSTE PARA 81 E5 | e7e977ff-aec3-4050-9c13-9ab827847c47 | Status | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_81U5 |  | FWB_DS_00025 | 20260413 | Status | 30 | DirectOperate | SingleBit | 1126 | FALSE | FALSE | 5 | SingleCoord | 225 | ClosePulseOn | 0.25
FWB_TR1BT_TR1BT_A_81 |  | 81 - FUNCAO SUB/SOB FREQUENCIA | 66ca59ed-1ff2-4ac2-86e6-886adce3f830 | Status | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_A_PROT_81 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TR1BT_TR1BT_A_81 |  | FWB_DS_00026 | 20260413 | Status | 30 | DirectOperate | SingleBit | 1127 | FALSE | FALSE | 5 | SingleCoord | 226;226 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR2_TR2_CDCO |  | ESTADO_PARALELISMO | 9202dcad-5325-49f8-bd70-cbf976970f74 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TAP_REG |  | Custom | ABC | None | Read |  | null@null@null___MESTRE@INDIVIDUAL@COMANDO___Custom___admsINV_D_TS_SS | 2 |  | UTR_FWB_1 | CNC_TR2_TR2_CDCO |  | 22df27b6-0539-45f9-b5ff-abad980d90ed | 20260415 | Status |  |  | MultiCoord | 2206;2207 | FALSE
FWB_TR1_TR1_AJG2 |  | AJUSTE PARA GRUPO 2 | fe03e1f0-ad7b-4a41-9533-8c36dd3dacf2 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_AJG2 |  | FWB_DS_00080 | 20260413 | Status | 30 | DirectOperate | SingleBit | 1205 | FALSE | FALSE | 15 | MultiCoord | 228;229 | ClosePulseOn;ClosePulseOn | 0.25;0.25
FWB_TR1_TR1_R90 |  | 90 - FUNCAO REGULADOR | d6322246-290e-4c89-9cf5-d11a95a7078f | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TAP_REG |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_TR1_TR1_R90 |  | FWB_DS_00095 | 20260413 | Status | 30 | DirectOperate | SingleBit | 2204 | FALSE | FALSE | 15 | SingleCoord | 402;402 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR1_TR1_VF |  | VENTILACAO FORCADA | 2ae1f829-0f04-4255-b99a-51c6f19f2d8e | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TC_SV | 2 |  | UTR_FWB_1 | FWB_TR1_TR1_VF |  | FWB_DS_00097 | 20260413 | Status | 30 | DirectOperate | SingleBit | 2347 | FALSE | FALSE | 15 | SingleCoord | 425;425 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR1_TR1_CDC |  | COMUTADOR | 2fa3a4df-1e27-459b-a0ad-8422c7d5a06c | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_COMTAP |  | TapIncrement | ABC | None | Write |  | AUMENTAR@DIMINUIR___null@null___TapIncrement_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_TR1_TR1_CDC |  | FWB_DS_00176 | 20260413 | Status | 0 | DirectOperate | DoubleBit |  | FALSE | FALSE | 15 | SingleCoord | 400;400 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_TR1AT_52-2_DJF1 |  | DISJUNTOR NF | b248cdca-de7c-4f76-9363-c7f261888d41 | SwitchStatus | FWB Trans | [6 empty] | FWB_TR1AT_52-2_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_FWB_1 | FWB_TR1AT_52-2_DJF1 |  | FWB_DS_00177 | 20260413 | Status | 30 | DirectOperate | MultiCoord | 1159;1160 | FALSE | FALSE | 15 | SingleCoord | 232;232 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR1BT_52-6_DJF1 |  | DISJUNTOR NF | d50d8fcb-acef-4d00-b6a4-70987a293c80 | SwitchStatus | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_FWB_1 | FWB_TR1BT_52-6_DJF1 |  | FWB_DS_00178 | 20260413 | Status | 30 | DirectOperate | MultiCoord | 1161;1162 | FALSE | FALSE | 15 | SingleCoord | 233;233 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR1AT_89-8_SECF |  | SECCIONADORA FONTE | 9973fa3c-896d-4171-83a6-bc8fe8cac181 | SwitchStatus | FWB Trans | [6 empty] | FWB_TR1AT_89-8_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 2 |  | UTR_FWB_1 | FWB_TR1AT_89-8_SECF |  | FWB_DS_00179 | 20260413 | Status | 30 | DirectOperate | MultiCoord | 1163;1164 | FALSE | FALSE | 15 | SingleCoord | 234;234 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR1AT_89-10_SECC |  | SECCIONADORA CARGA | 381ac3ad-12f7-43f4-851b-2602062cc797 | SwitchStatus | FWB Trans | [6 empty] | FWB_TR1AT_89-10_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 2 |  | UTR_FWB_1 | FWB_TR1AT_89-10_SECC |  | FWB_DS_00180 | 20260413 | Status | 30 | DirectOperate | MultiCoord | 1165;1166 | FALSE | FALSE | 15 | SingleCoord | 237;237 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR1AT_89-12_SECB |  | SECCIONADORA BYPASS | 30dfc9da-a1de-4803-a071-716cfa60f965 | SwitchStatus | FWB Trans | [6 empty] | FWB_TR1AT_89-12_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 1 |  | UTR_FWB_1 | FWB_TR1AT_89-12_SECB |  | FWB_DS_00181 | 20260413 | Status | 30 | DirectOperate | MultiCoord | 1167;1168 | FALSE | FALSE | 15 | SingleCoord | 235;235 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR1BT_89-40_SECB |  | SECCIONADORA BYPASS | bd6bea8f-2b90-4f10-b8df-2cd3c771693b | SwitchStatus | FWB Trans | [6 empty] | FWB_TR1BT_89-40_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 1 |  | UTR_FWB_1 | FWB_TR1BT_89-40_SECB |  | FWB_DS_00182 | 20260413 | Status | 30 | DirectOperate | MultiCoord | 1169;1170 | FALSE | FALSE | 15 | SingleCoord | 236;236 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR1_TR1_FC14 |  | FALHA COMUNICACAO 2414 | 1f216899-1be0-40c0-a4bf-d268ed20d82c | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR1_TR1_FC14 |  | 31cb05e1-885d-437c-9c5e-61ab56b8e273 | 20260413 | Status |  |  | SingleBit | 2402 | FALSE
FWB_TR1_TR1_RLCD |  | 43 - CHAVE LOCAL REMOTO COMUTADOR | 78484e2c-f87c-4c4f-bd4c-0b3c25fc535f | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TAP_REG |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom___INV_S_TS_SS | 2 |  | UTR_FWB_1 | FWB_TR1_TR1_RLCD |  | 66108998-c04c-443a-b624-68fcf48d6637 | 20260413 | Status |  |  | SingleBit | 2400 | FALSE
FWB_B138_B138_86CC |  | FALTA VCC CIRCUITO RELE 86 | a0dec45c-b336-4b15-9453-211c4d1b29da | Status | FWB Trans | [8 empty] | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_B138_B138_86CC |  | 66d6ca3a-3812-452c-b5a3-ea4c944a2b96 | 20260413 | Status |  |  | SingleBit | 2312 | FALSE
FWB_LTPNT_89-34_DSEC |  | DEFEITO SECCIONADORA | 2e4857d8-abd8-4f4a-88d9-8d4701f659cc | Status | FWB Trans | [6 empty] | FWB_LTPNT_89-34_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_LTPNT_89-34_DSEC |  | 5b513d68-ade2-4cdc-b0b7-9cfcf96bf2cf | 20260413 | Status |  |  | SingleBit | 2346 | FALSE
FWB_TR1_TR1_CDAM |  | CDC AUTOMATICO MANUAL | 2b4c3439-b5ee-4508-80b1-ca2f3f205cb8 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TAP_REG |  | Custom | ABC | None | Read |  | null@null___AUTOMATICO@MANUAL___Custom___INV_S_TS_SS | 2 |  | UTR_FWB_1 | FWB_TR1_TR1_CDAM |  | a2935729-d652-4029-8164-0a10e4bb09ad | 20260413 | Status |  |  | SingleBit | 2401 | FALSE
FWB_LTPNT_89-34_SECF |  | SECCIONADORA FONTE | 6bc6a4ca-2a18-4675-8f89-cbb8c7f2997e | SwitchStatus | FWB Trans | [6 empty] | FWB_LTPNT_89-34_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 2 |  | UTR_FWB_1 | FWB_LTPNT_89-34_SECF |  | cca382fe-af73-4edf-995f-afd646762347 | 20260413 | Status | 30 | DirectOperate | MultiCoord | 2300;2301 | FALSE | FALSE | 15 | SingleCoord | 420;420 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_B138_B138_86BF |  | 86BF | 869eae84-8707-4185-8060-f71194f58674 | Status | FWB Trans | [8 empty] | Custom | ABC | None | ReadWrite |  | REARMAR@null___NORMAL@ATUADO___Custom_S_TC_SA | 1 |  | UTR_FWB_1 | FWB_B138_B138_86BF |  | 54d6159c-6ab6-411a-a75c-12e54d817396 | 20260327 | Status | 30 | DirectOperate | SingleBit | 2315 | FALSE | FALSE | 5 | SingleCoord | 422 | ClosePulseOn | 0
FWB_BP2_BP2_86BF |  | 86BF | 947c1a15-2115-4312-a91e-8cdf684d6321 | Status | FWB Trans | [8 empty] | Custom | ABC | None | ReadWrite |  | REARMAR@null___NORMAL@ATUADO___Custom_S_TC_SA | 1 |  | UTR_FWB_1 | FWB_BP2_BP2_86BF |  | 5a4d564c-3100-4a5b-a2aa-732e70cd1d30 | 20260414 | Status | 30 | DirectOperate | SingleBit | 2325 | FALSE | FALSE | 5 | SingleCoord | 424 | ClosePulseOn | 0
FWB_BP1_BP1_86BF |  | 86BF | ade7ebb8-81d7-43f5-9a5b-a3deae178843 | Status | FWB Trans | [8 empty] | Custom | ABC | None | ReadWrite |  | REARMAR@null___NORMAL@ATUADO___Custom_S_TC_SA | 1 |  | UTR_FWB_1 | FWB_BP1_BP1_86BF |  | 78fceca4-c697-4d86-8550-365eb2f405cb | 20260414 | Status | 30 | DirectOperate | SingleBit | 2323 | FALSE | FALSE | 5 | SingleCoord | 423 | ClosePulseOn | 0
FWB_TR2AT_TR2AT_FPBR |  | FALTA POTENCIAL BARRA | 3da9f915-7ce3-498c-89cf-558f4ab4baee | Status | FWB Trans | [6 empty] | FWB_TR2AT_52-3_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_FPBR |  | FWB_DS_00183 | 20260414 | Status |  |  | SingleBit | 1300 | FALSE
FWB_TR2_TR2_P_FLK1 |  | FALHA LINK 1 | d7b89ec7-f3d0-491f-9185-674ebac54ea2 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_P_FLK1 |  | FWB_DS_00186 | 20260414 | Status |  |  | SingleBit | 1303 | FALSE
FWB_TR2_TR2_P_FLK2 |  | FALHA LINK 2 | dcbe4f59-b8f4-4aad-84fa-77192af33f0e | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_P_FLK2 |  | FWB_DS_00187 | 20260414 | Status |  |  | SingleBit | 1304 | FALSE
FWB_TR2AT_TR2AT_P_51F |  | 51 - SOBRECORRENTE TEMPORIZADA FASE | 457a410a-1bc2-4866-899d-a2f127c0c65d | Status | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_P_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_P_51F |  | FWB_DS_00196 | 20260414 | Status |  |  | SingleBit | 1313 | FALSE
FWB_TR2AT_TR2AT_P_51N1 |  | 51 - SOBRECORRENTE TEMPORIZADA NEUTRO E1 | 75c47118-f066-4644-96f2-d5aeef93a236 | Status | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_P_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_P_51N1 |  | FWB_DS_00197 | 20260414 | Status |  |  | SingleBit | 1314 | FALSE
FWB_TR2_TR2_P_87_T |  | 87 - TRIP DIFERENCIAL | 2420739a-e0ab-428d-8d23-ed7461c4dabb | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_P_PROT_87_T |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_P_87_T |  | FWB_DS_00189 | 20260414 | Status |  |  | SingleBit | 1306 | FALSE
FWB_TR2BT_TR2BT_P_51F |  | 51 - SOBRECORRENTE TEMPORIZADA FASE | 81240424-2c0d-44ce-99c7-888ad1cc7919 | Status | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_P_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_P_51F |  | FWB_DS_00203 | 20260414 | Status |  |  | SingleBit | 1320 | FALSE
FWB_TR2_TR2_A_87_T |  | 87 - TRIP DIFERENCIAL | d8f35272-7b33-4e39-893b-23f01b524dc3 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_A_PROT_87_T |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_A_87_T |  | FWB_DS_00216 | 20260414 | Status |  |  | SingleBit | 1333 | FALSE
FWB_TR2BT_TR2BT_P_51N1 |  | 51 - SOBRECORRENTE TEMPORIZADA NEUTRO E1 | 75094ca2-a96e-41aa-b3fb-74ebd538d094 | Status | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_P_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_P_51N1 |  | FWB_DS_00204 | 20260414 | Status |  |  | SingleBit | 1321 | FALSE
FWB_TR2BT_TR2BT_P_50F |  | 50 - SOBRECORRENTE INSTANTANEA FASE | f51f505e-3fcc-4c19-819a-9c9496caa6d8 | Status | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_P_PROT_50F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_P_50F |  | FWB_DS_00201 | 20260414 | Status |  |  | SingleBit | 1318 | FALSE
FWB_TR2AT_P_52-3_62BF |  | 62 - FALHA DISJUNTOR BLOQUEIO | 552cf189-2601-4273-9b6a-acc046319ed4 | Status | FWB Trans | [6 empty] | FWB_TR2AT_P_52-3_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2AT_P_52-3_62BF |  | FWB_DS_00190 | 20260414 | Status |  |  | SingleBit | 1307 | FALSE
FWB_TR2_TR2_P_FB |  | FASE B | d3c716ed-b566-437c-a1d0-9fb83904e8de | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_P_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_P_FB |  | FWB_DS_00192 | 20260414 | Status |  |  | SingleBit | 1309 | FALSE
FWB_TR2AT_TR2AT_A_51F |  | 51 - SOBRECORRENTE TEMPORIZADA FASE | 81693b08-9831-400d-98cb-4fe2e4b7ac67 | Status | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_A_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_A_51F |  | FWB_DS_00223 | 20260414 | Status |  |  | SingleBit | 1340 | FALSE
FWB_TR2_TR2_A_FB |  | FASE B | 55c3af97-e7c1-4fc0-b458-ec75806d6b8e | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_A_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_A_FB |  | FWB_DS_00219 | 20260414 | Status |  |  | SingleBit | 1336 | FALSE
FWB_TR2AT_TR2AT_A_50N |  | 50 - SOBRECORRENTE INSTANTANEA NEUTRO | fb910e42-e0a2-4e1f-a560-62671051c5e5 | Status | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_A_PROT_50N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_A_50N |  | FWB_DS_00222 | 20260414 | Status |  |  | SingleBit | 1339 | FALSE
FWB_TR2AT_TR2AT_A_50F |  | 50 - SOBRECORRENTE INSTANTANEA FASE | 322ab4e7-8d30-468b-8fb3-e7a00c28c633 | Status | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_A_PROT_50F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_A_50F |  | FWB_DS_00221 | 20260414 | Status |  |  | SingleBit | 1338 | FALSE
FWB_TR2_TR2_A_FC |  | FASE C | 85eac6f6-cacb-459d-ad52-1207eab95604 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_A_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_A_FC |  | FWB_DS_00220 | 20260414 | Status |  |  | SingleBit | 1337 | FALSE
FWB_TR2BT_TR2BT_A_67F |  | 67 - DIRECIONAL SOBRECORRENTE FASE | 483fd136-ca99-470f-aba7-cb5133153158 | Status | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_A_PROT_67F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_67F |  | FWB_DS_00226 | 20260414 | Status |  |  | SingleBit | 1343 | FALSE
FWB_TR2BT_A_52-7_62BF |  | 62 - FALHA DISJUNTOR BLOQUEIO | 5ff77957-8d01-417e-8161-81eb4147ad2f | Status | FWB Trans | [6 empty] | FWB_TR2BT_A_52-20_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_A_52-7_62BF |  | FWB_DS_00227 | 20260414 | Status |  |  | SingleBit | 1344 | FALSE
FWB_TR2BT_TR2BT_A_50F |  | 50 - SOBRECORRENTE INSTANTANEA FASE | 151d90c2-b4a7-4b42-a2fc-1297b2cef237 | Status | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_A_PROT_50F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_50F |  | FWB_DS_00228 | 20260414 | Status |  |  | SingleBit | 1345 | FALSE
FWB_TR2BT_TR2BT_A_50N |  | 50 - SOBRECORRENTE INSTANTANEA NEUTRO | 9bd05fbc-4342-4baa-be4e-ab450317e041 | Status | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_A_PROT_50N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_50N |  | FWB_DS_00229 | 20260414 | Status |  |  | SingleBit | 1346 | FALSE
FWB_TR2_TR2_A_FA |  | FASE A | 872d0077-d1a6-46bc-884f-6a62c2a4e56d | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_A_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_A_FA |  | FWB_DS_00218 | 20260414 | Status |  |  | SingleBit | 1335 | FALSE
FWB_TR2BT_TR2BT_A_51N1 |  | 51 - SOBRECORRENTE TEMPORIZADA NEUTRO E1 | 6067fdd9-6182-45cd-a7e2-43718df4ff94 | Status | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_A_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_51N1 |  | FWB_DS_00231 | 20260414 | Status |  |  | SingleBit | 1348 | FALSE
FWB_TR2AT_P_52-3_BBA1 |  | BOBINA ABERTURA 1 | 1789eb21-7ab1-4764-9e6c-a8c01347364f | Status | FWB Trans | [6 empty] | FWB_TR2AT_52-3_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR2AT_P_52-3_BBA1 |  | FWB_DS_00232 | 20260414 | Status |  |  | SingleBit | 1349 | FALSE
FWB_TR2AT_P_52-3_BBA2 |  | BOBINA ABERTURA 2 | 94a25a9d-d7fd-41dc-abee-6db003679696 | Status | FWB Trans | [6 empty] | FWB_TR2AT_52-3_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR2AT_P_52-3_BBA2 |  | FWB_DS_00233 | 20260414 | Status |  |  | SingleBit | 1350 | FALSE
FWB_TR2BT_P_52-7_BBA1 |  | BOBINA ABERTURA 1 | 67ea6064-3562-4b3c-a76b-c4b036a73b19 | Status | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR2BT_P_52-7_BBA1 |  | FWB_DS_00234 | 20260414 | Status |  |  | SingleBit | 1351 | FALSE
FWB_TR2AT_A_52-3_BBA2 |  | BOBINA ABERTURA 2 | 8a73970c-ccc7-41c2-b0dc-476c76231686 | Status | FWB Trans | [6 empty] | FWB_TR2AT_52-3_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR2AT_A_52-3_BBA2 |  | FWB_DS_00237 | 20260414 | Status |  |  | SingleBit | 1354 | FALSE
FWB_TR2BT_P_52-7_BBA2 |  | BOBINA ABERTURA 2 | 8d010525-6495-403a-85eb-9218e4de24b1 | Status | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR2BT_P_52-7_BBA2 |  | FWB_DS_00235 | 20260414 | Status |  |  | SingleBit | 1352 | FALSE
FWB_TR2BT_A_52-7_BBA1 |  | BOBINA ABERTURA 1 | 971d67ba-6e09-45a1-b279-f31fbd43c0cf | Status | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR2BT_A_52-7_BBA1 |  | FWB_DS_00238 | 20260414 | Status |  |  | SingleBit | 1355 | FALSE
FWB_TR2BT_A_52-7_BBA2 |  | BOBINA ABERTURA 2 | 7c2b4488-df6e-4c49-8843-257c802b3ca3 | Status | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR2BT_A_52-7_BBA2 |  | FWB_DS_00239 | 20260414 | Status |  |  | SingleBit | 1356 | FALSE
FWB_TR2_TR2_P_FCOM |  | FALHA COMUNICACAO | cdc3b03c-3f9e-4e62-b447-d2bad2f55a26 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_P_FCOM |  | FWB_DS_00240 | 20260414 | Status |  |  | SingleBit | 1357 | FALSE
FWB_TR2BT_TR2BT_A_51F |  | 51 - SOBRECORRENTE TEMPORIZADA FASE | 6a87569a-c2ed-47f1-8c45-cf462c0213bc | Status | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_A_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_51F |  | FWB_DS_00230 | 20260414 | Status |  |  | SingleBit | 1347 | FALSE
FWB_TR2_TR2_A_FCOM |  | FALHA COMUNICACAO | 75518cc6-f55a-437a-90df-e6a92def9402 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_A_FCOM |  | FWB_DS_00241 | 20260414 | Status |  |  | SingleBit | 1358 | FALSE
FWB_TR2AT_52-3_BBFC |  | BOBINA FECHAMENTO | dcecbab7-b402-43fc-89e6-4ec86f6ffe7f | Status | FWB Trans | [6 empty] | FWB_TR2AT_52-3_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR2AT_52-3_BBFC |  | FWB_DS_00245 | 20260414 | Status |  |  | SingleBit | 1382 | FALSE
FWB_TR2_TR2_INTR |  | 20 63 87 - PROTECOES INTRINSECAS | 70c28aff-fe0e-4176-bc30-73146c00eb30 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_INTR |  | FWB_DS_00244 | 20260414 | Status |  |  | SingleBit | 1376 | FALSE
FWB_TR2AT_TR2AT_A_51N1 |  | 51 - SOBRECORRENTE TEMPORIZADA NEUTRO E1 | 46507813-f712-43db-ad37-d12c192f13ed | Status | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_A_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_A_51N1 |  | FWB_DS_00224 | 20260414 | Status |  |  | SingleBit | 1341 | FALSE
FWB_TR2BT_52-7_BBFC |  | BOBINA FECHAMENTO | a7a4201b-6f45-4c9e-945d-e7539109b100 | Status | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR2BT_52-7_BBFC |  | FWB_DS_00246 | 20260414 | Status |  |  | SingleBit | 1383 | FALSE
FWB_TR2_TR2_A_87 |  | 87 - FUNCAO DIFERENCIAL | 03e2a505-4d0f-4e94-ab3a-20075b90f7b6 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_PROT_87 |  | Custom | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_FWB_1 | FWB_TR2_TR2_A_87 |  | FWB_DS_00212 | 20260414 | Status |  |  | SingleBit | 1329 | FALSE
FWB_TR2BT_52-7_MOLA |  | MOLA | 07e2316c-276b-403f-b4d1-5c9aea508667 | Status | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2BT_52-7_MOLA |  | FWB_DS_00247 | 20260414 | Status |  |  | SingleBit | 1384 | FALSE
FWB_TR2AT_89-22_DSEC |  | DEFEITO SECCIONADORA | f2bccd86-1fb7-4a01-a596-51aa5563af5d | Status | FWB Trans | [6 empty] | FWB_TR2AT_89-22_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2AT_89-22_DSEC |  | FWB_DS_00249 | 20260414 | Status |  |  | SingleBit | 1397 | FALSE
FWB_TR2AT_A_52-3_BBA1 |  | BOBINA ABERTURA 1 | b78dc1fd-d177-4f1d-99d2-ea37521e04f3 | Status | FWB Trans | [6 empty] | FWB_TR2AT_52-3_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR2AT_A_52-3_BBA1 |  | FWB_DS_00236 | 20260414 | Status |  |  | SingleBit | 1353 | FALSE
FWB_TR2AT_52-3_MOLA |  | MOLA | 88f92a8d-a559-40ca-a052-1d5d7698d1b7 | Status | FWB Trans | [6 empty] | FWB_TR2AT_52-3_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2AT_52-3_MOLA |  | FWB_DS_00248 | 20260414 | Status |  |  | SingleBit | 1385 | FALSE
FWB_TR2AT_52-3_SF6B |  | BLOQUEIO BAIXA PRESSAO SF6 | f7e88d5f-d0c5-413d-94ad-66f251a2cc2a | Status | FWB Trans | [6 empty] | FWB_TR2AT_52-3_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2AT_52-3_SF6B |  | FWB_DS_00252 | 20260414 | Status |  |  | SingleBit | 1401 | FALSE
FWB_TR2BT_89-46_DSEC |  | DEFEITO SECCIONADORA | 6c1d35cc-0673-44bb-9c39-3c3756a3c8af | Status | FWB Trans | [6 empty] | FWB_TR2BT_89-46_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2BT_89-46_DSEC |  | FWB_DS_00250 | 20260414 | Status |  |  | SingleBit | 1398 | FALSE
FWB_TR2AT_52-3_CCMO |  | FALTA VCC MOTOR | c963c7f0-3954-44ce-8e47-9164fed5f695 | Status | FWB Trans | [6 empty] | FWB_TR2AT_52-3_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2AT_52-3_CCMO |  | FWB_DS_00253 | 20260414 | Status |  |  | SingleBit | 1402 | FALSE
FWB_TR2AT_TR2AT_P_67N |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO | fd2f1859-9f24-43f9-ad05-67fecd38fa5f | Status | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_P_PROT_67N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_P_67N |  | FWB_DS_00198 | 20260414 | Status |  |  | SingleBit | 1315 | FALSE
FWB_TR2AT_89-18_DSEC |  | DEFEITO SECCIONADORA | e6114660-a609-4bb1-ab67-ea90a65dffff | Status | FWB Trans | [6 empty] | FWB_TR2AT_89-18_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2AT_89-18_DSEC |  | FWB_DS_00256 | 20260414 | Status |  |  | SingleBit | 1405 | FALSE
FWB_TR2_TR2_86 |  | 86 - BLOQUEIO | c8a719e4-f509-41f7-b9ac-a2bc0c6a4747 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_86 |  | FWB_DS_00255 | 20260414 | Status |  |  | SingleBit | 1404 | FALSE
FWB_TR2_TR2_A_FLK1 |  | FALHA LINK 1 | ee6e919b-29da-4d34-8a43-65591b3cd3f4 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_A_FLK1 |  | FWB_DS_00213 | 20260414 | Status |  |  | SingleBit | 1330 | FALSE
FWB_TR2_TR2_20CA |  | 20 - ALARME VALVULA CDC | c7f5d917-c0ce-430a-841d-e30d72fc9aa2 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_20CA |  | FWB_DS_00260 | 20260414 | Status |  |  | SingleBit | 1409 | FALSE
FWB_TR2_TR2_20TA |  | 20 - ALARME VALVULA TRAFO | 19103579-ce61-43b4-bbc8-2842511f9e79 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_20TA |  | FWB_DS_00259 | 20260414 | Status |  |  | SingleBit | 1408 | FALSE
FWB_TR2_TR2_63CA |  | 63 - ALARME BUCHHOLZ CDC | 983d005a-f9c1-4a41-92b4-65f4d6152878 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_63CA |  | FWB_DS_00257 | 20260414 | Status |  |  | SingleBit | 1406 | FALSE
FWB_TR2_TR2_PERP |  | PERMISSAO PARALELISMO | 8bf678d5-717d-4cce-b77b-edb06960a264 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NÃO PERMITIDO@PERMITIDO___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_PERP |  | FWB_DS_00262 | 20260414 | Status |  |  | SingleBit | 1411 | FALSE
FWB_TR2AT_52-3_SF6A |  | ALARME BAIXA PRESSAO SF6 | 12736794-589f-45a4-897d-06212949cc3f | Status | FWB Trans | [6 empty] | FWB_TR2AT_52-3_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2AT_52-3_SF6A |  | FWB_DS_00251 | 20260414 | Status |  |  | SingleBit | 1399 | FALSE
FWB_TR2_TR2_63TD |  | 63 - TRIP BUCHHOLZ TRAFO | 06d38446-1d98-4759-b4d4-951c6cf07972 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_63TD |  | FWB_DS_00264 | 20260414 | Status |  |  | SingleBit | 1413 | FALSE
FWB_TR2_TR2_71T |  | 71 - NIVEL OLEO TRAFO | 0f87bcde-e5af-44ca-a942-c250b5c8cf51 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_71T |  | FWB_DS_00265 | 20260414 | Status |  |  | SingleBit | 1414 | FALSE
FWB_TR2BT_52-7_43LR |  | 43 - CHAVE LOCAL REMOTO | 921adbdf-7c22-4992-b88f-a4700a9c3ded | Status | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_TR2BT_52-7_43LR |  | FWB_DS_00267 | 20260414 | Status |  |  | SingleBit | 1416 | FALSE
FWB_TR2_TR2_71C |  | 71 - NIVEL OLEO CDC | 37d381dc-df62-4c3b-afb9-570130188a32 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_71C |  | FWB_DS_00269 | 20260414 | Status |  |  | SingleBit | 1418 | FALSE
FWB_TR2_TR2_20TD |  | 20 - TRIP VALVULA TRAFO | e84e3eca-adad-441f-8f91-2c41838f6b1d | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_20TD |  | FWB_DS_00266 | 20260414 | Status |  |  | SingleBit | 1415 | FALSE
FWB_TR2BT_TR2BT_CCFL |  | FALTA VCC | 405ddd13-3f65-4e2b-a2a1-33fa142cbeb7 | Status | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_CCFL |  | FWB_DS_00268 | 20260414 | Status |  |  | SingleBit | 1417 | FALSE
FWB_TR2BT_52-7_SF6B |  | BLOQUEIO BAIXA PRESSAO SF6 | 1ab2e171-3d36-4efd-ba10-ceedad8b614f | Status | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2BT_52-7_SF6B |  | FWB_DS_00271 | 20260414 | Status |  |  | SingleBit | 1420 | FALSE
FWB_TR2BT_52-7_CCMO |  | FALTA VCC MOTOR | dfeefe3b-d3e0-406c-ac3d-b1b425e776d2 | Status | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2BT_52-7_CCMO |  | FWB_DS_00272 | 20260414 | Status |  |  | SingleBit | 1421 | FALSE
FWB_TR2AT_52-3_43LR |  | 43 - CHAVE LOCAL REMOTO | df46e909-4124-43df-a2db-aeda27ece798 | Status | FWB Trans | [6 empty] | FWB_TR2AT_52-3_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom___INV_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_TR2AT_52-3_43LR |  | FWB_DS_00273 | 20260414 | Status |  |  | SingleBit | 1422 | FALSE
FWB_TR2BT_52-7_SF6A |  | ALARME BAIXA PRESSAO SF6 | 58d2f005-a96c-4bc5-91d1-88d241b25f71 | Status | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2BT_52-7_SF6A |  | FWB_DS_00270 | 20260414 | Status |  |  | SingleBit | 1419 | FALSE
FWB_TR2_TR2_90LR |  | 43 - CHAVE LOCAL REMOTO RELE 90 | 33e591ee-0ff4-4eb1-8f37-432530ceeca6 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TAP_REG |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom___INV_S_TS_SS | 2 |  | UTR_FWB_1 | FWB_TR2_TR2_90LR |  | FWB_DS_00278 | 20260414 | Status |  |  | SingleBit | 2208 | FALSE
FWB_TR2AT_A_52-3_62BF |  | 62 - FALHA DISJUNTOR BLOQUEIO | 9d141d7d-9625-4a94-89c4-7f3ed8f40999 | Status | FWB Trans | [6 empty] | FWB_TR2AT_A_52-3_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2AT_A_52-3_62BF |  | FWB_DS_00217 | 20260414 | Status |  |  | SingleBit | 1334 | FALSE
FWB_TR2_TR2_86CC |  | FALTA VCC CIRCUITO RELE 86 | 481edc00-a904-4663-a830-c046e6061fb2 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_86CC |  | FWB_DS_00280 | 20260414 | Status |  |  | SingleBit | 2314 | FALSE
FWB_TR2_TR2_P_DR |  | DEFEITO RELE | b34ce6f3-23f0-4a6f-8115-3446da79d805 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_P_DR |  | FWB_DS_00281 | 20260414 | Status |  |  | SingleBit | 2319 | FALSE
FWB_TR2_TR2_A_DR |  | DEFEITO RELE | a2964d94-37b7-4ec5-9406-e69bf901faa9 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_A_DR |  | FWB_DS_00282 | 20260414 | Status |  |  | SingleBit | 2320 | FALSE
FWB_TR2_TR2_FVF |  | FALHA VENTILACAO FORCADA | 3589e72c-0d41-4323-a8d4-59ba396bcd45 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_FVF |  | FWB_DS_00284 | 20260414 | Status |  |  | SingleBit | 2356 | FALSE
FWB_TR2_TR2_BCDC |  | BLOQUEIO CDC | 45d3c492-c2d6-4f08-83d5-c3a30247bd11 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_BCDC |  | FWB_DS_00286 | 20260414 | Status |  |  | SingleBit | 2358 | FALSE
FWB_TR2_TR2_CAFL |  | FALTA VCA | 2d710a64-3da0-4f6a-b94e-071a92aabd6c | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_CAFL |  | FWB_DS_00285 | 20260414 | Status |  |  | SingleBit | 2357 | FALSE
FWB_TR2_TR2_CDRA |  | CDC REMOTO AUTOMATICO | 084fbbc3-06b9-4649-a937-439260ee5996 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___AUTOM DESATIVADO@AUTOM ATIVOU___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_CDRA |  | FWB_DS_00288 | 20260414 | Status |  |  | SingleBit | 2360 | FALSE
FWB_TR2_TR2_CDLA |  | CDC LOCAL AUTOMATICO | b287d1a3-118f-4ef7-8c65-7d4d01f06cf4 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___AUTOM DESATIVADO@AUTOM ATIVOU___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_CDLA |  | FWB_DS_00289 | 20260414 | Status |  |  | SingleBit | 2361 | FALSE
FWB_TR2AT_89-20_DSEC |  | DEFEITO SECCIONADORA | d6d3871a-d383-479c-85c1-8cbdc0d08f63 | Status | FWB Trans | [6 empty] | FWB_TR2AT_89-20_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2AT_89-20_DSEC |  | FWB_DS_00274 | 20260414 | Status |  |  | SingleBit | 1423 | FALSE
FWB_TR2_TR2_DR90 |  | DEFEITO RELE 90 | 156a8a2e-75cb-4140-a358-cf4fd9084608 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_DR90 |  | FWB_DS_00290 | 20260414 | Status |  |  | SingleBit | 2362 | FALSE
FWB_TR2_TR2_RLCD |  | 43 - CHAVE LOCAL REMOTO COMUTADOR | db215d44-4493-42c4-a351-c7bf7da7f29d | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TAP_REG |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom___INV_S_TS_SS | 2 |  | UTR_FWB_1 | FWB_TR2_TR2_RLCD |  | FWB_DS_00291 | 20260414 | Status |  |  | SingleBit | 2450 | FALSE
FWB_TR2_TR2_CDAM |  | CDC AUTOMATICO MANUAL | b7112dc5-ba5e-40ff-b7bb-495fee84348f | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TAP_REG |  | Custom | ABC | None | Read |  | null@null___AUTOMATICO@MANUAL___Custom___INV_S_TS_SS | 2 |  | UTR_FWB_1 | FWB_TR2_TR2_CDAM |  | FWB_DS_00292 | 20260414 | Status |  |  | SingleBit | 2451 | FALSE
FWB_TR2_TR2_FC14 |  | FALHA COMUNICACAO 2414 | c73ae2ad-78a8-4160-8986-d5fda59b5fd7 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_FC14 |  | FWB_DS_00293 | 20260414 | Status |  |  | SingleBit | 2452 | FALSE
FWB_TR2_TR2_CDLM |  | CDC LOCAL MANUAL | d80b8519-e5e4-456d-8ecf-7a5839c02542 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___MANUAL DESATIVOU@MANUAL ATIVOU___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_CDLM |  | FWB_DS_00287 | 20260414 | Status |  |  | SingleBit | 2359 | FALSE
FWB_TR2_TR2_SCAR |  | SECADOR DE AR | 7013ad99-f1b8-4680-ba69-e6969a0b82b8 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_SCAR |  | FWB_DS_00298 | 20260414 | Status |  |  | SingleBit | 9105 | FALSE
FWB_TR2AT_TR2AT_OI |  | OPERACAO INDEVIDA SECCIONADORA | aac99b47-f3dc-4b00-96f7-c288b65b228c | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_OI |  | FWB_DS_00295 | 20260414 | Status |  |  | SingleBit | 9102 | FALSE
FWB_TR2_CDC_SCAR |  | SECADOR DE AR | 9701dd55-2df0-41ae-a6de-26a6a60bec68 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_CDC_SCAR |  | FWB_DS_00299 | 20260414 | Status |  |  | SingleBit | 9106 | FALSE
FWB_TR2_TR2_TOA |  | 26 - ALARME TEMPERATURA OLEO | 8dd5b8a7-9b71-4902-b634-fa95319b9eaa | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_TOA |  | FWB_DS_00300 | 20260414 | Status |  |  | SingleBit | 9107 | FALSE
FWB_TR2BT_TR2BT_TEA |  | 49 - ALARME TEMPERATURA ENROLAMENTO | 23e1114c-9038-4ad9-ad4c-25f18f5666a9 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_TEA |  | FWB_DS_00302 | 20260414 | Status |  |  | SingleBit | 9109 | FALSE
FWB_TR2BT_TR2BT_TED |  | 49 - TRIP TEMPERATURA ENROLAMENTO | 3c939b5b-a5e1-4da1-aaf1-f0c8e4b9b4e7 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_TED |  | FWB_DS_00303 | 20260414 | Status |  |  | SingleBit | 9110 | FALSE
FWB_TR2AT_TR2AT_CCFL |  | FALTA VCC | 0cae7b2d-522e-440c-8d81-32cb81e3a045 | Status | FWB Trans | [6 empty] | FWB_TR2AT_52-3_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_CCFL |  | FWB_DS_00254 | 20260414 | Status |  |  | SingleBit | 1403 | FALSE
FWB_TR2AT_TR2AT_TEA |  | 49 - ALARME TEMPERATURA ENROLAMENTO | cb6778ed-e0f6-4d72-8ffc-be259a522615 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_TEA |  | FWB_DS_00304 | 20260414 | Status |  |  | SingleBit | 9111 | FALSE
FWB_TR2_TR2_TOD |  | 26 - TRIP TEMPERATURA OLEO | b91ab3e2-f036-49f4-87ff-f3881983f611 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_TOD |  | FWB_DS_00301 | 20260414 | Status |  |  | SingleBit | 9108 | FALSE
FWB_TR2_TR2_MDCD |  | MINI DISJUNTOR CDC | 45977ab9-7af9-4ef6-85b2-828fabd8a166 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_MDCD |  | FWB_DS_00308 | 20260414 | Status |  |  | SingleBit | 9115 | FALSE
FWB_TR2AT_TR2AT_P_67 |  | 67 - FUNCAO DIRECIONAL SOBRECORRENTE | 727e153d-3cf6-49c4-a6d9-bbca9ae5a3f5 | Status | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_P_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_P_67 |  | FWB_DS_00312 | 20260414 | Status |  |  | SingleBit | 9119 | FALSE
FWB_TR2BT_TR2BT_P_50N |  | 50 - SOBRECORRENTE INSTANTANEA NEUTRO | fc3f661b-bb57-448c-94e7-199a2f202c5a | Status | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_P_PROT_50N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_P_50N |  | FWB_DS_00202 | 20260414 | Status |  |  | SingleBit | 1319 | FALSE
FWB_TR2AT_TR2AT_P_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | b9830cfd-7b52-4fda-a4ac-1d2b5aa31a60 | Status | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_P_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_P_67FT |  | FWB_DS_00314 | 20260414 | Status |  |  | SingleBit | 9121 | FALSE
FWB_TR2AT_TR2AT_P_81E1 |  | 81 - TRIP SUB/SOBRE FREQUENCIA E1 | 9aa9af4d-0fd3-40d6-9601-8e213dda4d0e | Status | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_P_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_P_81E1 |  | FWB_DS_00319 | 20260414 | Status |  |  | SingleBit | 9126 | FALSE
FWB_TR2AT_TR2AT_P_81O1 |  | 81 - TRIP SOBRE FREQUENCIA E1 | 97d2a2d6-7ba0-4d8e-85bb-c11982967193 | Status | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_P_PROT_81O1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_P_81O1 |  | FWB_DS_00321 | 20260414 | Status |  |  | SingleBit | 9128 | FALSE
FWB_TR2AT_TR2AT_P_FUTP |  | FALHA FUSIVEL TP | ef112ed4-2cd7-4ca3-9fca-a2063c01c6fb | Status | FWB Trans | [6 empty] | FWB_TR2AT_52-3_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_P_FUTP |  | FWB_DS_00322 | 20260414 | Status |  |  | SingleBit | 9129 | FALSE
FWB_TR2AT_TR2AT_P_81E2 |  | 81 - TRIP SUB/SOBRE FREQUENCIA E2 | a70fd921-474e-41ca-93a0-ad2162ec0862 | Status | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_P_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_P_81E2 |  | FWB_DS_00320 | 20260414 | Status |  |  | SingleBit | 9127 | FALSE
FWB_TR2BT_TR2BT_A_67N |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO | 4ac1c066-5152-4b20-8cb6-9ef3b2b881b5 | Status | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_A_PROT_67N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_67N |  | FWB_DS_00225 | 20260414 | Status |  |  | SingleBit | 1342 | FALSE
FWB_TR2BT_TR2BT_A_67 |  | 67 - FUNCAO DIRECIONAL SOBRECORRENTE | 053709da-880f-42ff-8ece-4961e094addc | Status | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_A_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_67 |  | FWB_DS_00334 | 20260414 | Status |  |  | SingleBit | 9141 | FALSE
FWB_TR2BT_TR2BT_A_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | e301b635-b8a6-47c4-85ac-559053a27e48 | Status | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_A_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_67NT |  | FWB_DS_00338 | 20260414 | Status |  |  | SingleBit | 9145 | FALSE
FWB_TR2BT_TR2BT_A_81BLOQ |  | 81 BLOQUEIO DINAMICO | 7e7949b8-65bd-4c31-8583-7e7d88541aa8 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS | 2 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_81BLOQ |  | FWB_DS_00341 | 20260414 | Status |  |  | SingleBit | 9148 | FALSE
FWB_TR2BT_TR2BT_A_81E1 |  | 81 - TRIP SUB/SOBRE FREQUENCIA E1 | fb0c978c-d0d8-48aa-923d-f706f0169d03 | Status | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_A_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_81E1 |  | FWB_DS_00342 | 20260414 | Status |  |  | SingleBit | 9149 | FALSE
FWB_TR2BT_TR2BT_A_81E2 |  | 81 - TRIP SUB/SOBRE FREQUENCIA E2 | c7085198-a443-4080-b18c-9b203ebc96fd | Status | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_A_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_81E2 |  | FWB_DS_00343 | 20260414 | Status |  |  | SingleBit | 9150 | FALSE
FWB_TR2BT_TR2BT_A_81E3 |  | 81 - TRIP SUB/SOBRE FREQUENCIA E3 | adea48ed-2317-49f8-a9f1-580b929c4212 | Status | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_A_PROT_81E3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_81E3 |  | FWB_DS_00344 | 20260414 | Status |  |  | SingleBit | 9151 | FALSE
FWB_TR2BT_TR2BT_A_81E4 |  | 81 - TRIP SUB/SOBRE FREQUENCIA E4 | 50b6c7f2-4fdc-4a1f-9edf-022773154195 | Status | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_A_PROT_81E4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_81E4 |  | FWB_DS_00345 | 20260414 | Status |  |  | SingleBit | 9152 | FALSE
FWB_TR2BT_TR2BT_A_81E5 |  | 81 - TRIP SUB/SOBRE FREQUENCIA E5 | d924cf7b-3f38-41c9-a7b2-88ae6c232cde | Status | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_A_PROT_81E5 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_81E5 |  | FWB_DS_00346 | 20260414 | Status |  |  | SingleBit | 9153 | FALSE
FWB_TR2BT_TR2BT_A_81O1 |  | 81 - TRIP SOBRE FREQUENCIA E1 | 8dabeb1f-23d7-4ec3-8571-cb6bb255cc08 | Status | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_A_PROT_81O1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_81O1 |  | FWB_DS_00347 | 20260414 | Status |  |  | SingleBit | 9154 | FALSE
FWB_TR2BT_TR2BT_A_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | 495dd349-d8a9-4044-8f77-90efa2cf8f57 | Status | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_A_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_67FT |  | FWB_DS_00336 | 20260414 | Status |  |  | SingleBit | 9143 | FALSE
FWB_TR2BT_TR2BT_A_FUTP |  | FALHA FUSIVEL TP | c6073490-3ceb-434a-83d6-76e0dbc70d34 | Status | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_FUTP |  | FWB_DS_00348 | 20260414 | Status |  |  | SingleBit | 9155 | FALSE
FWB_TR2_TR2_50CD |  | 50 - SOBRECORRENTE CDC | 25207054-a20e-4e5d-82c3-da8052bd2425 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_50CD |  | FWB_DS_00353 | 20260414 | Status |  |  | SingleBit | 9160 | FALSE
FWB_TR2_TR2_59CD |  | 59 - BLOQUEIO CDC SOBRETENSAO | 720e3ab4-8eeb-4468-b4b1-e73725da9757 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_59CD |  | FWB_DS_00354 | 20260414 | Status |  |  | SingleBit | 9161 | FALSE
FWB_TR2_TR2_63CD |  | 63 - TRIP BUCHHOLZ CDC | 29c128da-299e-4c7e-8fd3-33df535919db | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_63CD |  | FWB_DS_00258 | 20260414 | Status |  |  | SingleBit | 1407 | FALSE
FWB_TR2_TR2_27CD |  | 27 - BLOQUEIO SUBTENSAO CDC | f13c74a1-67e9-4bc2-8d4b-aee99dbaf35a | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_27CD |  | FWB_DS_00355 | 20260414 | Status |  |  | SingleBit | 9162 | FALSE
FWB_TR2_TR2_FPAR |  | FALHA SINCRONISMO PARALELISMO | 279e8fc8-57e1-4c38-976d-52641dab2ac9 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_FPAR |  | FWB_DS_00357 | 20260414 | Status |  |  | SingleBit | 9164 | FALSE
FWB_TR1_TR1_P_87 |  | 87 - FUNCAO DIFERENCIAL | 6e30af84-8cc1-404a-9b8e-9c0041d37447 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_PROT_87 |  | Custom | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_FWB_1 | FWB_TR1_TR1_P_87 |  | badfa28d-3dca-487d-9a35-6ba9012a0a30 | 20260414 | Status |  |  | SingleBit | 1102 | FALSE
FWB_TR1_TR1_A_87 |  | 87 - FUNCAO DIFERENCIAL | 1f084e54-7b7c-4a51-b174-e3e41b8001f2 | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_PROT_87 |  | Custom | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_FWB_1 | FWB_TR1_TR1_A_87 |  | e6f878ab-ed1d-470f-be29-d47643d854d0 | 20260414 | Status |  |  | SingleBit | 1129 | FALSE
FWB_TR2AT_TR2AT_P_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | 2445ba55-075e-425b-9200-1a559a948c42 | Status | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_P_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_P_67NT |  | FWB_DS_00316 | 20260414 | Status |  |  | SingleBit | 9123 | FALSE
FWB_TR2AT_TR2AT_TED |  | 49 - TRIP TEMPERATURA ENROLAMENTO | 7cfaa5ef-8a88-429f-ae82-d65fe90cb402 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_TED |  | FWB_DS_00305 | 20260414 | Status |  |  | SingleBit | 9112 | FALSE
FWB_TR2_TR2_P_FSIN |  | FALHA IRIG B - SINCRONISMO | 2abe992a-9c95-472c-bf1c-00486f17a2aa | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_P_FSIN |  | FWB_DS_00188 | 20260414 | Status |  |  | SingleBit | 1305 | FALSE
FWB_TR2AT_TR2AT_P_50F |  | 50 - SOBRECORRENTE INSTANTANEA FASE | a54de8cb-2ca8-4057-88b3-0c54f99b6fe7 | Status | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_P_PROT_50F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_P_50F |  | FWB_DS_00194 | 20260414 | Status |  |  | SingleBit | 1311 | FALSE
FWB_TR2AT_TR2AT_P_50N |  | 50 - SOBRECORRENTE INSTANTANEA NEUTRO | 83430668-b5b5-443e-a3c1-d67617164696 | Status | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_P_PROT_50N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_P_50N |  | FWB_DS_00195 | 20260414 | Status |  |  | SingleBit | 1312 | FALSE
FWB_TR2AT_TR2AT_P_67F |  | 67 - DIRECIONAL SOBRECORRENTE FASE | 226b63f4-6813-4759-819e-8dfa0cef4f7d | Status | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_P_PROT_67F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2AT_TR2AT_P_67F |  | FWB_DS_00199 | 20260414 | Status |  |  | SingleBit | 1316 | FALSE
FWB_TR2BT_P_52-7_62BF |  | 62 - FALHA DISJUNTOR BLOQUEIO | f8fe4bf9-be79-43df-86d6-b4364dd9c4cc | Status | FWB Trans | [6 empty] | FWB_TR2BT_P_52-20_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2BT_P_52-7_62BF |  | FWB_DS_00200 | 20260414 | Status |  |  | SingleBit | 1317 | FALSE
FWB_TR2_TR2_A_FSIN |  | FALHA IRIG B - SINCRONISMO | c4aaab3a-8cda-4f2f-bb4c-15c27b56ffc2 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_A_FSIN |  | FWB_DS_00215 | 20260414 | Status |  |  | SingleBit | 1332 | FALSE
FWB_TR2_TR2_43TC |  | 43 - CHAVE TELECOMANDO | 275199c7-f05b-4049-8e7a-792d1b706278 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_43TC |  | FWB_DS_00242 | 20260414 | Status |  |  | SingleBit | 1373 | FALSE
FWB_TR2_TR2_P_FC |  | FASE C | 06537831-e953-4d7e-adb4-5eb0111cb931 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_P_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_P_FC |  | FWB_DS_00193 | 20260414 | Status |  |  | SingleBit | 1310 | FALSE
FWB_TR2_TR2_P_87 |  | 87 - FUNCAO DIFERENCIAL | c8dbedde-3f1d-4893-af53-1b4e45583b85 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_PROT_87 |  | Custom | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_FWB_1 | FWB_TR2_TR2_P_87 |  | FWB_DS_00185 | 20260414 | Status |  |  | SingleBit | 1302 | FALSE
FWB_TR2_TR2_A_FLK2 |  | FALHA LINK 2 | a763b66d-d198-44e4-a1f0-6bb756b7698d | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_A_FLK2 |  | FWB_DS_00214 | 20260414 | Status |  |  | SingleBit | 1331 | FALSE
FWB_TR2_TR2_20CD |  | 20 - TRIP VALVULA CDC | dd128662-d601-4cb5-891c-d1065ff0e438 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_20CD |  | FWB_DS_00261 | 20260414 | Status |  |  | SingleBit | 1410 | FALSE
FWB_TR2_TR2_P_FA |  | FASE A | 6e670b08-bc70-4760-a76f-273f891f307f | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_P_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_P_FA |  | FWB_DS_00191 | 20260414 | Status |  |  | SingleBit | 1308 | FALSE
FWB_TR2_TR2_63TA |  | 63 - ALARME BUCHHOLZ TRAFO | 9423079f-e1f7-4c64-af7a-0435202cf3b7 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_63TA |  | FWB_DS_00263 | 20260414 | Status |  |  | SingleBit | 1412 | FALSE
FWB_TR2BT_TR2BT_A_81U1 |  | AJUSTE PARA 81 E1 | adb09895-bc56-4173-8c77-61c3d0d115cc | Status | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_81U1 |  | FWB_DS_00205 | 20260414 | Status | 30 | DirectOperate | SingleBit | 1322 | FALSE | FALSE | 5 | SingleCoord | 241 | ClosePulseOn | 0.25
FWB_TR2AT_52-3_43EP |  | 43 EP | 25bd70c7-fd45-459c-9f77-e58cc8de4168 | Status | FWB Trans | [6 empty] | FWB_TR2AT_52-3_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TR2AT_52-3_43EP |  | FWB_DS_00184 | 20260414 | Status | 30 | DirectOperate | SingleBit | 1301 | FALSE | FALSE | 5 | SingleCoord | 250;250 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR2BT_TR2BT_A_81U3 |  | AJUSTE PARA 81 E3 | 5f4755b9-0534-4566-97e7-6033fd8a3e5a | Status | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_81U3 |  | FWB_DS_00207 | 20260414 | Status | 30 | DirectOperate | SingleBit | 1324 | FALSE | FALSE | 5 | SingleCoord | 243 | ClosePulseOn | 0.25
FWB_TR2BT_TR2BT_A_81U4 |  | AJUSTE PARA 81 E4 | 93e7641f-509d-473a-95a8-c278d05e8c98 | Status | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_81U4 |  | FWB_DS_00208 | 20260414 | Status | 30 | DirectOperate | SingleBit | 1325 | FALSE | FALSE | 5 | SingleCoord | 244 | ClosePulseOn | 0.25
FWB_TR2BT_TR2BT_A_81U2 |  | AJUSTE PARA 81 E2 | 0a081493-b061-40b1-a500-777eab0f9098 | Status | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_81U2 |  | FWB_DS_00206 | 20260414 | Status | 30 | DirectOperate | SingleBit | 1323 | FALSE | FALSE | 5 | SingleCoord | 242 | ClosePulseOn | 0.25
FWB_TR2_TR2_VF |  | VENTILACAO FORCADA | cb64391f-b180-4b56-96c8-7bbbffda4dab | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TC_SV | 2 |  | UTR_FWB_1 | FWB_TR2_TR2_VF |  | FWB_DS_00283 | 20260414 | Status | 30 | DirectOperate | SingleBit | 2355 | FALSE | FALSE | 15 | SingleCoord | 426;426 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR2BT_89-46_SECB |  | SECCIONADORA BYPASS | b78cc1f6-7ab1-44e4-a74f-f16cda0f1d86 | SwitchStatus | FWB Trans | [6 empty] | FWB_TR2BT_89-46_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 1 |  | UTR_FWB_1 | FWB_TR2BT_89-46_SECB |  | FWB_DS_00362 | 20260414 | Status | 30 | DirectOperate | MultiCoord | 1361;1362 | FALSE | FALSE | 15 | SingleCoord | 252;252 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR2BT_52-7_DJF1 |  | DISJUNTOR NF | 888aa545-f25d-4649-ba95-23854984b9df | SwitchStatus | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_FWB_1 | FWB_TR2BT_52-7_DJF1 |  | FWB_DS_00366 | 20260414 | Status | 30 | DirectOperate | MultiCoord | 1369;1370 | FALSE | FALSE | 15 | SingleCoord | 255;255 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR1BT_52-6_43EP |  | 43 EP | 944798dd-5376-44f1-b341-470d0e89a70a | Status | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TR1BT_52-6_43EP |  | 55e5d351-e8ec-412f-a37e-d54c7d6cda4f | 20260414 | Status | 30 | DirectOperate | SingleBit | 1128 | FALSE | FALSE | 5 | SingleCoord | 231;231 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR2_TR2_AJG2 |  | AJUSTE PARA GRUPO 2 | e5484798-2b93-41df-b895-398ddb29b7f7 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 1 |  | UTR_FWB_1 | FWB_TR2_TR2_AJG2 |  | FWB_DS_00243 | 20260414 | Status | 30 | DirectOperate | SingleBit | 1375 | FALSE | FALSE | 15 | MultiCoord | 248;249 | ClosePulseOn;ClosePulseOn | 0.25;0.25
FWB_TR2AT_89-18_SECF |  | SECCIONADORA FONTE | 7111fb2d-29f8-484c-82a1-3ccaf73e6ae5 | SwitchStatus | FWB Trans | [6 empty] | FWB_TR2AT_89-18_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 2 |  | UTR_FWB_1 | FWB_TR2AT_89-18_SECF |  | FWB_DS_00363 | 20260414 | Status | 30 | DirectOperate | MultiCoord | 1363;1364 | FALSE | FALSE | 15 | SingleCoord | 256;256 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR2_TR2_R90 |  | 90 - FUNCAO REGULADOR | c2f50988-625a-4c9d-930f-b3d8a2cc7da1 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TAP_REG |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_TR2_TR2_R90 |  | FWB_DS_00279 | 20260414 | Status | 30 | DirectOperate | SingleBit | 2209 | FALSE | FALSE | 15 | SingleCoord | 407;407 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR1AT_52-2_43EP |  | 43 EP | 6fa66eed-136f-4ada-925b-1a37e55a9dc3 | Status | FWB Trans | [6 empty] | FWB_TR1AT_52-2_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TR1AT_52-2_43EP |  | 1aef84b5-126b-4d23-b0e4-99ca3097fc06 | 20260414 | Status | 30 | DirectOperate | SingleBit | 1101 | FALSE | FALSE | 5 | SingleCoord | 230;230 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR2BT_52-7_43EP |  | 43 EP | a301ce3e-0239-4f14-8b78-82dee7075e24 | Status | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TR2BT_52-7_43EP |  | FWB_DS_00211 | 20260414 | Status | 30 | DirectOperate | SingleBit | 1328 | FALSE | FALSE | 5 | SingleCoord | 251;251 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR2_TR2_CDC |  | COMUTADOR | 244bd929-c822-4585-aed5-67128a8fe5d9 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_COMTAP |  | TapIncrement | ABC | None | Write |  | AUMENTAR@DIMINUIR___null@null___TapIncrement_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_TR2_TR2_CDC |  | FWB_DS_00360 | 20260414 | Status | 0 | DirectOperate | DoubleBit |  | FALSE | FALSE | 15 | SingleCoord | 405;405 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_TR2AT_52-3_DJF1 |  | DISJUNTOR NF | 242dfd9d-d545-4a5f-8849-986313eb7f4d | SwitchStatus | FWB Trans | [6 empty] | FWB_TR2AT_52-3_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_FWB_1 | FWB_TR2AT_52-3_DJF1 |  | FWB_DS_00365 | 20260414 | Status | 30 | DirectOperate | MultiCoord | 1367;1368 | FALSE | FALSE | 15 | SingleCoord | 254;254 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR2BT_TR2BT_A_81U5 |  | AJUSTE PARA 81 E5 | 34b4968a-d1c9-49b5-a3b1-d2294f4813ed | Status | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_81U5 |  | FWB_DS_00209 | 20260414 | Status | 30 | DirectOperate | SingleBit | 1326 | FALSE | FALSE | 5 | SingleCoord | 245 | ClosePulseOn | 0.25
FWB_TR2AT_89-20_SECC |  | SECCIONADORA CARGA | 0353c6d2-7ff0-4254-840b-e0528443959d | SwitchStatus | FWB Trans | [6 empty] | FWB_TR2AT_89-20_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 1 |  | UTR_FWB_1 | FWB_TR2AT_89-20_SECC |  | FWB_DS_00364 | 20260414 | Status | 30 | DirectOperate | MultiCoord | 1365;1366 | FALSE | FALSE | 15 | SingleCoord | 253;253 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR2AT_89-22_SECB |  | SECCIONADORA BYPASS | 52a3ee5c-d0aa-44d7-bac0-ff48ee8d5c26 | SwitchStatus | FWB Trans | [6 empty] | FWB_TR2AT_89-22_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 2 |  | UTR_FWB_1 | FWB_TR2AT_89-22_SECB |  | FWB_DS_00361 | 20260414 | Status | 30 | DirectOperate | MultiCoord | 1359;1360 | FALSE | FALSE | 15 | SingleCoord | 257;257 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR2BT_TR2BT_A_81 |  | 81 - FUNCAO SUB/SOB FREQUENCIA | 2f1d4426-0da9-435d-8142-376e9f379652 | Status | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_A_PROT_81 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TR2BT_TR2BT_A_81 |  | FWB_DS_00210 | 20260414 | Status | 30 | DirectOperate | SingleBit | 1327 | FALSE | FALSE | 5 | SingleCoord | 246;246 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TR1_TR1_CDCO_CTRL |  |  | 5d7f616c-7c3b-420e-9151-c1b9231d0d2a | Status | FWB Trans | [6 empty] | FWB_TR1_TR1_TAP_REG |  | Custom | ABC | None | Write |  | MESTRE@INDIVIDUAL@COMANDO___null@null@null___Custom___admsINV_D_TC_SS | 2 |  | UTR_FWB_1 | FWB_TR1_TR1_CDCO_CTRL |  | 9964e95c-0ef5-4633-b8ef-2fb038509fba | 20260415 | Status | 30 | AutoSelectWithValue | MultiCoord |  | FALSE | FALSE | 15 | MultiCoord | 401;403;401 | ClosePulseOn;ClosePulseOn;TripPulseOn | 1;1;1
FWB_TR2_TR2_CDCO_CTRL |  |  | 78de10c3-46b2-4c84-971f-62c193c0b940 | Status | FWB Trans | [6 empty] | FWB_TR2_TR2_TAP_REG |  | Custom | ABC | None | Write |  | MESTRE@INDIVIDUAL@COMANDO___null@null@null___Custom___admsINV_D_TC_SS | 2 |  | UTR_FWB_1 | FWB_TR2_TR2_CDCO_CTRL |  | 06f3d461-65de-4848-9226-fe68ee9a15be | 20260415 | Status | 30 | AutoSelectWithValue | MultiCoord |  | FALSE | FALSE | 15 | MultiCoord | 406;404;406 | ClosePulseOn;ClosePulseOn;TripPulseOn | 1;1;1
FWB_AL12_52-12_43TC |  | 43 - CHAVE TELECOMANDO | 33c51089-39ab-4697-89bc-289dd1d0ca31 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_43TC |  | FWB_DS_00367 | 20260415 | Status |  |  | SingleBit | 100 | FALSE
FWB_AL12_52-12_SF6A |  | ALARME BAIXA PRESSAO SF6 | 8c050e30-e995-49a4-a4d8-709dabb1d537 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_SF6A |  | FWB_DS_00369 | 20260415 | Status |  |  | SingleBit | 106 | FALSE
FWB_AL12_52-12_62BF |  | 62 - FALHA DISJUNTOR BLOQUEIO | 40c38079-84e9-4b40-81b0-b581e0614447 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_62BF |  | FWB_DS_00390 | 20260415 | Status |  |  | SingleBit | 127 | FALSE
FWB_AL12_52-12_CCMO |  | FALTA VCC MOTOR | 64207780-b2e7-40c7-a81b-d7b6142f6ab8 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_CCMO |  | FWB_DS_00374 | 20260415 | Status |  |  | SingleBit | 111 | FALSE
FWB_AL12_52-12_MOLA |  | MOLA | fbdd9e73-3f80-42f4-8c97-188140cca8d6 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_MOLA |  | FWB_DS_00371 | 20260415 | Status |  |  | SingleBit | 108 | FALSE
FWB_AL12_52-12_50F |  | 50 - SOBRECORRENTE INSTANTANEA FASE | daeb4102-f3b8-434a-bb10-f308d1706b1a | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_PROT_50F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_50F |  | FWB_DS_00391 | 20260415 | Status |  |  | SingleBit | 128 | FALSE
FWB_AL12_52-12_81SU |  | 81 - TRIP SUB FREQUENCIA | 0d141dd2-a2e2-4742-b7df-e0e8ab824746 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_PROT_81SU |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_81SU |  | FWB_DS_00396 | 20260415 | Status |  |  | SingleBit | 133 | FALSE
FWB_AL12_52-12_SF6B |  | BLOQUEIO BAIXA PRESSAO SF6 | bc03c908-f7a9-491f-8492-94f705622983 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_SF6B |  | FWB_DS_00370 | 20260415 | Status |  |  | SingleBit | 107 | FALSE
FWB_AL12_52-12_FLK1 |  | FALHA LINK 1 | d1b80cd8-be14-47c8-8439-3554cc71d857 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_FLK1 |  | FWB_DS_00401 | 20260415 | Status |  |  | SingleBit | 139 | FALSE
FWB_AL12_52-12_FLK2 |  | FALHA LINK 2 | 994e27c0-a628-46fc-b5b2-96983ea4366e | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_FLK2 |  | FWB_DS_00402 | 20260415 | Status |  |  | SingleBit | 140 | FALSE
FWB_AL12_52-12_51N1 |  | 51 - SOBRECORRENTE TEMPORIZADA NEUTRO | 1ad40f10-76ad-4598-a49e-58663cb04ec8 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_51N1 |  | FWB_DS_00394 | 20260415 | Status |  |  | SingleBit | 131 | FALSE
FWB_AL12_52-12_79LO |  | 79 - RELIGAMENTO BLOQUEADO | 4361046d-751f-4eac-afe1-17f82ab6b22e | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_79LO |  | FWB_DS_00399 | 20260415 | Status |  |  | SingleBit | 136 | FALSE
FWB_AL12_52-12_43LR |  | 43 - CHAVE LOCAL REMOTO | bc04caeb-f108-45e0-ae25-28e17af97e7e | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_43LR |  | FWB_DS_00376 | 20260415 | Status |  |  | SingleBit | 113 | FALSE
FWB_AL12_52-12_CAFL |  | FALTA VCA | eb1a97bd-7b22-40ec-b759-9475bfc63aa8 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_AL12_52-12_CAFL |  | FWB_DS_00372 | 20260415 | Status |  |  | SingleBit | 109 | FALSE
FWB_AL12_52-12_79_1 |  | 79 - PARTIDA RELIGAMENTO | 9f62434c-236a-428e-bca3-0bafe946408c | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_79_1 |  | FWB_DS_00397 | 20260415 | Status |  |  | SingleBit | 134 | FALSE
FWB_AL12_52-12_CCAB |  | FALTA VCC CIRCUITO ABERTURA | 7efae229-833a-4f78-86ed-b42602030023 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_CCAB |  | FWB_DS_00375 | 20260415 | Status |  |  | SingleBit | 112 | FALSE
FWB_AL12_52-12_79OK |  | 79 - RELIGAMENTO COM SUCESSO | c7401662-2db4-45e9-8587-d563959cdcb3 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_79OK |  | FWB_DS_00398 | 20260415 | Status |  |  | SingleBit | 135 | FALSE
FWB_AL12_52-12_FSIH |  | FALHA SINCRONISMO HORA | ad645623-9487-4060-93b4-a57b37a4f399 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_FSIH |  | FWB_DS_00400 | 20260415 | Status |  |  | SingleBit | 138 | FALSE
FWB_AL12_52-12_FCOM |  | FALHA COMUNICACAO | 3a6cae9d-ab46-4fa6-8a93-56bd5de29d6e | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_FCOM |  | FWB_DS_00403 | 20260415 | Status |  |  | SingleBit | 141 | FALSE
FWB_AL12_52-12_BBAB |  | BOBINA ABERTURA | 44190ca8-eef0-40c6-99ab-79b3bf838d10 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_BBAB |  | FWB_DS_00378 | 20260415 | Status |  |  | SingleBit | 115 | FALSE
FWB_AL12_52-12_51F |  | 51 - SOBRECORRENTE TEMPORIZADA FASE | d6d7df31-6c14-4f64-9f61-aa48ae3eda08 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_51F |  | FWB_DS_00392 | 20260415 | Status |  |  | SingleBit | 129 | FALSE
FWB_AL12_52-12_SGFT |  | TRIP SGF | 68bed409-96a0-45bc-b757-d09803b41855 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_SGFT |  | FWB_DS_00395 | 20260415 | Status |  |  | SingleBit | 132 | FALSE
FWB_AL12_52-12_TEXT |  | TRIP EXTERNO | 83fdb242-943c-4512-8b8e-0bce9cbf1afb | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_TEXT |  | FWB_DS_00389 | 20260415 | Status |  |  | SingleBit | 126 | FALSE
FWB_AL12_52-12_TOED |  | 26 49 - TRIP TEMPERATURA | b55259e4-6160-4632-a195-fb5a567e4465 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_TOED |  | FWB_DS_00405 | 20260415 | Status |  |  | SingleBit | 142 | FALSE
FWB_AL12_52-12_BBFC |  | BOBINA FECHAMENTO | 4e968b50-ccaa-4693-b0fc-7756e410ae07 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_BBFC |  | FWB_DS_00377 | 20260415 | Status |  |  | SingleBit | 114 | FALSE
FWB_AL12_52-12_50N |  | 50 - SOBRECORRENTE INSTANTANEA NEUTRO | ba77a650-cc6f-4c3d-9279-f5d623091dec | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_PROT_50N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_50N |  | FWB_DS_00393 | 20260415 | Status |  |  | SingleBit | 130 | FALSE
FWB_AL12_52-12_CCFL |  | FALTA VCC | 2ab408be-8587-4d7f-a1ff-fe474910bbc7 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_AL12_52-12_CCFL |  | FWB_DS_00379 | 20260415 | Status |  |  | SingleBit | 116 | FALSE
FWB_AL12_52-12_CCCO |  | FALTA VCC COMANDO | 482afffa-cde5-43a3-8d9c-63e8d5eac4d4 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_CCCO |  | FWB_DS_00373 | 20260415 | Status |  |  | SingleBit | 110 | FALSE
FWB_AL12_52-12_AJG2 |  | AJUSTE PARA GRUPO 2 | f526f430-34cc-4978-ae26-a6ee588ae7c5 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 2 |  | UTR_FWB_1 | FWB_AL12_52-12_AJG2 |  | FWB_DS_00368 | 20260415 | Status | 30 | DirectOperate | SingleBit | 102 | FALSE | FALSE | 15 | MultiCoord | 31;32 | ClosePulseOn;ClosePulseOn | 0.25;0.25
FWB_AL12_52-12_79 |  | 79 - FUNCAO RELIGAMENTO | bcca67f6-4e82-477a-b6a9-6a04a6d1a4e2 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL12_52-12_79 |  | FWB_DS_00380 | 20260415 | Status | 30 | DirectOperate | SingleBit | 117 | FALSE | FALSE | 15 | SingleCoord | 22;22 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_AL12_52-12_81U2 |  | AJUSTE PARA 81 E2 | 22dda42e-091a-4433-b9e4-9a6a613caf05 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_81U2 |  | FWB_DS_00384 | 20260415 | Status | 30 | DirectOperate | SingleBit | 121 | FALSE | FALSE | 5 | SingleCoord | 26 | ClosePulseOn | 0.25
FWB_AL12_52-12_2649 |  | 26 49 - FUNCAO TEMPERATURA | 2f5375a4-46b9-4c20-bc77-71f6dff42e39 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_2649 |  | FWB_DS_00381 | 20260415 | Status | 30 | DirectOperate | SingleBit | 118 | FALSE | FALSE | 15 | SingleCoord | 24;24 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_AL12_52-12_81 |  | 81 - FUNCAO SUB/SOB FREQUENCIA | 55956f6b-a213-4135-bcac-e95810f17ed1 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL12_52-12_81 |  | FWB_DS_00388 | 20260415 | Status | 30 | DirectOperate | SingleBit | 125 | FALSE | FALSE | 5 | SingleCoord | 30;30 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL12_52-12_81U4 |  | AJUSTE PARA 81 E4 | a91ee67a-f2bf-4bd6-bb79-40dc31545493 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_81U4 |  | FWB_DS_00386 | 20260415 | Status | 30 | DirectOperate | SingleBit | 123 | FALSE | FALSE | 5 | SingleCoord | 28 | ClosePulseOn | 0.25
FWB_AL12_52-12_81U5 |  | AJUSTE PARA 81 E5 | 336360c6-f765-49df-9a21-3b653fb4654b | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_81U5 |  | FWB_DS_00387 | 20260415 | Status | 30 | DirectOperate | SingleBit | 124 | FALSE | FALSE | 5 | SingleCoord | 29 | ClosePulseOn | 0.25
FWB_AL12_52-12_81U1 |  | AJUSTE PARA 81 E1 | cd09b1e0-70f0-4672-aaf0-0d08821e7090 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_81U1 |  | FWB_DS_00383 | 20260415 | Status | 30 | DirectOperate | SingleBit | 120 | FALSE | FALSE | 5 | SingleCoord | 25 | ClosePulseOn | 0.25
FWB_AL12_52-12_81U3 |  | AJUSTE PARA 81 E3 | 43ca96e5-9b0e-4f31-b441-d9da3e01ac82 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_81U3 |  | FWB_DS_00385 | 20260415 | Status | 30 | DirectOperate | SingleBit | 122 | FALSE | FALSE | 5 | SingleCoord | 27 | ClosePulseOn | 0.25
FWB_AL12_52-12_DJF1 |  | DISJUNTOR NF | b88d5123-fdad-489a-9a69-e81c95180b2a | SwitchStatus | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_FWB_1 | FWB_AL12_52-12_DJF1 |  | FWB_DS_00404 | 20260415 | Status | 30 | DirectOperate | MultiCoord | 103;104 | FALSE | FALSE | 15 | SingleCoord | 21;21 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL12_52-12_51N |  | 51N | d4cabc9b-4583-492f-b8e8-3fceeee604a0 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL12_52-12_51N |  | FWB_DS_00382 | 20260415 | Status | 30 | DirectOperate | SingleBit | 119 | FALSE | FALSE | 15 | SingleCoord | 23;23 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL13_52-13_43TC |  | 43 - CHAVE TELECOMANDO | 53dacbda-d5cf-41e3-94e5-b86bf8767395 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_43TC |  | FWB_DS_00406 | 20260416 | Status |  |  | SingleBit | 200 | FALSE
FWB_AL13_52-13_CCCO |  | FALTA VCC COMANDO | 70c75392-92a3-483e-bd3e-9d0326727c5d | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_CCCO |  | FWB_DS_00412 | 20260416 | Status |  |  | SingleBit | 210 | FALSE
FWB_AL13_52-13_79LO |  | 79 - RELIGAMENTO BLOQUEADO | 567f9709-5d45-4243-80f7-e2e4ef59097e | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_79LO |  | FWB_DS_00438 | 20260416 | Status |  |  | SingleBit | 236 | FALSE
FWB_AL13_52-13_50N |  | 50 - SOBRECORRENTE INSTANTANEA NEUTRO | 237938c8-20b5-40ab-9f8d-04c0c89c7baf | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_PROT_50N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_50N |  | FWB_DS_00432 | 20260416 | Status |  |  | SingleBit | 230 | FALSE
FWB_AL13_52-13_50F |  | 50 - SOBRECORRENTE INSTANTANEA FASE | f4e46b08-aa49-4c43-9af7-5b59389f8475 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_PROT_50F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_50F |  | FWB_DS_00430 | 20260416 | Status |  |  | SingleBit | 228 | FALSE
FWB_AL13_52-13_SF6B |  | BLOQUEIO BAIXA PRESSAO SF6 | f7334c01-a1ff-45df-acbe-3e953147d050 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_SF6B |  | FWB_DS_00409 | 20260416 | Status |  |  | SingleBit | 207 | FALSE
FWB_AL13_52-13_FSIH |  | FALHA SINCRONISMO HORA | 1bf7b6cc-8c10-4d68-8534-d3c2ecfb826e | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_FSIH |  | FWB_DS_00439 | 20260416 | Status |  |  | SingleBit | 238 | FALSE
FWB_AL13_52-13_SF6A |  | ALARME BAIXA PRESSAO SF6 | 5cd53091-e6fb-4157-801a-0479d29438dc | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_SF6A |  | FWB_DS_00408 | 20260416 | Status |  |  | SingleBit | 206 | FALSE
FWB_AL13_52-13_FCOM |  | FALHA COMUNICACAO | e8fce504-a706-4a77-ba31-1366cd359f95 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_FCOM |  | FWB_DS_00442 | 20260416 | Status |  |  | SingleBit | 241 | FALSE
FWB_AL14_52-14_43TC |  | 43 - CHAVE TELECOMANDO | 9973cbc9-d8f9-4203-b610-e8b86cf30c02 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_43TC |  | FWB_DS_00445 | 20260416 | Status |  |  | SingleBit | 300 | FALSE
FWB_AL13_52-13_81SU |  | 81 - TRIP SUB FREQUENCIA | 84ed224c-4412-4413-8d19-b1be02777866 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_PROT_81SU |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_81SU |  | FWB_DS_00435 | 20260416 | Status |  |  | SingleBit | 233 | FALSE
FWB_AL14_52-14_SF6A |  | ALARME BAIXA PRESSAO SF6 | aa1bb683-78df-4eca-b0aa-e773c75fbbc6 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_SF6A |  | FWB_DS_00447 | 20260416 | Status |  |  | SingleBit | 306 | FALSE
FWB_AL14_52-14_MOLA |  | MOLA | 8da4e7f8-2771-4c75-b055-53ef0e39c7d5 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_MOLA |  | FWB_DS_00449 | 20260416 | Status |  |  | SingleBit | 308 | FALSE
FWB_AL13_52-13_SGFT |  | TRIP SGF | cf900cb8-d0f7-4400-b61d-4028cd6fa30c | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_SGFT |  | FWB_DS_00434 | 20260416 | Status |  |  | SingleBit | 232 | FALSE
FWB_AL14_52-14_CAFL |  | FALTA VCA | b92857f6-d136-4d8f-b60d-9d9b1f047ced | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_AL14_52-14_CAFL |  | FWB_DS_00450 | 20260416 | Status |  |  | SingleBit | 309 | FALSE
FWB_AL14_52-14_CCMO |  | FALTA VCC MOTOR | e999c2a6-9e1e-489a-894a-9fbdfefeddfd | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_CCMO |  | FWB_DS_00452 | 20260416 | Status |  |  | SingleBit | 311 | FALSE
FWB_AL13_52-13_FLK2 |  | FALHA LINK 2 | c692e470-6ac9-48c8-9c11-52e23e6c1538 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_FLK2 |  | FWB_DS_00441 | 20260416 | Status |  |  | SingleBit | 240 | FALSE
FWB_AL14_52-14_CCAB |  | FALTA VCC CIRCUITO ABERTURA | 60844a98-241b-4e49-b41f-845c46d58c61 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_CCAB |  | FWB_DS_00453 | 20260416 | Status |  |  | SingleBit | 312 | FALSE
FWB_AL14_52-14_43LR |  | 43 - CHAVE LOCAL REMOTO | 722a9650-8b93-4493-bdef-9258f4f819e4 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_43LR |  | FWB_DS_00454 | 20260416 | Status |  |  | SingleBit | 313 | FALSE
FWB_AL13_52-13_51F |  | 51 - SOBRECORRENTE TEMPORIZADA FASE | ff3dfab4-55fb-4683-a924-7b90f326818d | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_51F |  | FWB_DS_00431 | 20260416 | Status |  |  | SingleBit | 229 | FALSE
FWB_AL14_52-14_CCFL |  | FALTA VCC | d343224e-4417-4807-b503-fdd4b085e04b | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_AL14_52-14_CCFL |  | FWB_DS_00457 | 20260416 | Status |  |  | SingleBit | 316 | FALSE
FWB_AL14_52-14_BBAB |  | BOBINA ABERTURA | 36fa0a6b-73d2-4cc5-a160-4a0250687199 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_BBAB |  | FWB_DS_00456 | 20260416 | Status |  |  | SingleBit | 315 | FALSE
FWB_AL14_52-14_SF6B |  | BLOQUEIO BAIXA PRESSAO SF6 | d4d5444e-fa64-4239-b0c9-78ddb1947cbf | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_SF6B |  | FWB_DS_00448 | 20260416 | Status |  |  | SingleBit | 307 | FALSE
FWB_AL14_52-14_50F |  | 50 - SOBRECORRENTE INSTANTANEA FASE | 06415bed-35ff-4585-88b4-82e7b54de40e | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_PROT_50F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_50F |  | FWB_DS_00469 | 20260416 | Status |  |  | SingleBit | 328 | FALSE
FWB_AL14_52-14_62BF |  | 62 - FALHA DISJUNTOR BLOQUEIO | 1eee23bd-adb3-4431-a2b3-a9af2deea20a | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_62BF |  | FWB_DS_00468 | 20260416 | Status |  |  | SingleBit | 327 | FALSE
FWB_AL13_52-13_CCMO |  | FALTA VCC MOTOR | 65dcb5b5-31bc-4fa7-a883-f32404735774 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_CCMO |  | FWB_DS_00413 | 20260416 | Status |  |  | SingleBit | 211 | FALSE
FWB_AL14_52-14_51N1 |  | 51 - SOBRECORRENTE TEMPORIZADA NEUTRO | 69ca6ecc-9498-4a42-a906-7a0f499b271f | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_51N1 |  | FWB_DS_00472 | 20260416 | Status |  |  | SingleBit | 331 | FALSE
FWB_AL13_52-13_CCAB |  | FALTA VCC CIRCUITO ABERTURA | 3eba956b-770d-4fc4-91af-abf9fb89d7bf | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_CCAB |  | FWB_DS_00414 | 20260416 | Status |  |  | SingleBit | 212 | FALSE
FWB_AL14_52-14_51F |  | 51 - SOBRECORRENTE TEMPORIZADA FASE | 33cedbae-306a-44df-95c4-e5d28bb4334a | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_51F |  | FWB_DS_00470 | 20260416 | Status |  |  | SingleBit | 329 | FALSE
FWB_AL14_52-14_50N |  | 50 - SOBRECORRENTE INSTANTANEA NEUTRO | f9b0aa91-0b4e-43a1-aaad-ad3ccefb6fd5 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_PROT_50N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_50N |  | FWB_DS_00471 | 20260416 | Status |  |  | SingleBit | 330 | FALSE
FWB_AL14_52-14_79OK |  | 79 - RELIGAMENTO COM SUCESSO | dc1dbd85-f07c-47c4-992b-25ff3c4b543d | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_79OK |  | FWB_DS_00476 | 20260416 | Status |  |  | SingleBit | 335 | FALSE
FWB_AL14_52-14_79LO |  | 79 - RELIGAMENTO BLOQUEADO | cc14f32b-f662-45d4-940a-d34e128931f2 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_79LO |  | FWB_DS_00477 | 20260416 | Status |  |  | SingleBit | 336 | FALSE
FWB_AL14_52-14_FSIH |  | FALHA SINCRONISMO HORA | ad8c9e5b-eeaa-4cb4-81c1-061c0ad2a058 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_FSIH |  | FWB_DS_00478 | 20260416 | Status |  |  | SingleBit | 338 | FALSE
FWB_AL14_52-14_FLK1 |  | FALHA LINK 1 | d5728229-960d-4b92-98e0-2c879aefd6bf | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_FLK1 |  | FWB_DS_00479 | 20260416 | Status |  |  | SingleBit | 339 | FALSE
FWB_AL14_52-14_FLK2 |  | FALHA LINK 2 | 95921cc2-7030-446f-968a-4f03d3e3d008 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_FLK2 |  | FWB_DS_00480 | 20260416 | Status |  |  | SingleBit | 340 | FALSE
FWB_AL14_52-14_FCOM |  | FALHA COMUNICACAO | 3764a7b8-ddbd-49ae-a1f9-1aeddaa53f53 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_FCOM |  | FWB_DS_00481 | 20260416 | Status |  |  | SingleBit | 341 | FALSE
FWB_AL14_52-14_TOED |  | 26 49 - TRIP TEMPERATURA | 6e895901-f118-41df-b825-41af62a8d2d2 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_TOED |  | FWB_DS_00482 | 20260416 | Status |  |  | SingleBit | 342 | FALSE
FWB_AL21_52-21_43TC |  | 43 - CHAVE TELECOMANDO | a58aa256-b54a-4b84-b18d-694a182be120 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_43TC |  | FWB_DS_00517 | 20260416 | Status |  |  | SingleBit | 500 | FALSE
FWB_AL13_52-13_79_1 |  | 79 - PARTIDA RELIGAMENTO | eb05c2e6-7406-4d54-bc5d-09ca2ddaf8a2 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_79_1 |  | FWB_DS_00436 | 20260416 | Status |  |  | SingleBit | 234 | FALSE
FWB_AL14_52-14_81SU |  | 81 - TRIP SUB FREQUENCIA | 4f6e8c38-c2b5-404d-888b-26542d713567 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_PROT_81SU |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_81SU |  | FWB_DS_00474 | 20260416 | Status |  |  | SingleBit | 333 | FALSE
FWB_AL21_52-21_SF6B |  | BLOQUEIO BAIXA PRESSAO SF6 | 80a039bb-b3dc-4aae-8062-d315d90b2b7d | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_SF6B |  | FWB_DS_00520 | 20260416 | Status |  |  | SingleBit | 507 | FALSE
FWB_AL21_52-21_MOLA |  | MOLA | 12fda903-3868-47d0-ac0e-8b2b534c63a6 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_MOLA |  | FWB_DS_00521 | 20260416 | Status |  |  | SingleBit | 508 | FALSE
FWB_AL21_52-21_CAFL |  | FALTA VCA | d0793a59-f00f-47e6-9b35-2ba64b98bdd8 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_AL21_52-21_CAFL |  | FWB_DS_00522 | 20260416 | Status |  |  | SingleBit | 509 | FALSE
FWB_AL21_52-21_CCAB |  | FALTA VCC CIRCUITO ABERTURA | 417e19e2-b5f5-4487-91d9-9726b1969104 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_CCAB |  | FWB_DS_00525 | 20260416 | Status |  |  | SingleBit | 512 | FALSE
FWB_AL21_52-21_CCMO |  | FALTA VCC MOTOR | 869a7ebc-29ee-4eeb-9982-16cf3be6b616 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_CCMO |  | FWB_DS_00524 | 20260416 | Status |  |  | SingleBit | 511 | FALSE
FWB_AL21_52-21_43LR |  | 43 - CHAVE LOCAL REMOTO | 58adfb87-a51a-48bd-ab02-b2aa6296bc2f | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_43LR |  | FWB_DS_00526 | 20260416 | Status |  |  | SingleBit | 513 | FALSE
FWB_AL14_52-14_BBFC |  | BOBINA FECHAMENTO | c8845f35-9ee8-490c-aa0e-a6f573c5c40d | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_BBFC |  | FWB_DS_00455 | 20260416 | Status |  |  | SingleBit | 314 | FALSE
FWB_AL21_52-21_CCFL |  | FALTA VCC | be8b3776-0441-4c76-9f15-7707ae3fb72f | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_AL21_52-21_CCFL |  | FWB_DS_00529 | 20260416 | Status |  |  | SingleBit | 516 | FALSE
FWB_AL21_52-21_SF6A |  | ALARME BAIXA PRESSAO SF6 | 79155272-84b7-4278-96cb-7da5afc3b17d | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_SF6A |  | FWB_DS_00519 | 20260416 | Status |  |  | SingleBit | 506 | FALSE
FWB_AL21_52-21_TEXT |  | TRIP EXTERNO | 4c44f5f8-c98a-42ab-a206-a62a92f887f7 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_TEXT |  | FWB_DS_00539 | 20260416 | Status |  |  | SingleBit | 526 | FALSE
FWB_AL21_52-21_BBAB |  | BOBINA ABERTURA | 7b43afe7-c5fe-4156-919b-c94188a4aa9b | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_BBAB |  | FWB_DS_00528 | 20260416 | Status |  |  | SingleBit | 515 | FALSE
FWB_AL21_52-21_50F |  | 50 - SOBRECORRENTE INSTANTANEA FASE | 3b85ee27-778f-46e3-8876-7fd0f907a716 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_PROT_50F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_50F |  | FWB_DS_00541 | 20260416 | Status |  |  | SingleBit | 528 | FALSE
FWB_AL21_52-21_51F |  | 51 - SOBRECORRENTE TEMPORIZADA FASE | 00ed3ee0-8e35-469e-8dcc-4b18aa7fead0 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_51F |  | FWB_DS_00542 | 20260416 | Status |  |  | SingleBit | 529 | FALSE
FWB_AL21_52-21_62BF |  | 62 - FALHA DISJUNTOR BLOQUEIO | 59e62e7d-3187-4aed-a275-c8bb1d4b2edc | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_62BF |  | FWB_DS_00540 | 20260416 | Status |  |  | SingleBit | 527 | FALSE
FWB_AL21_52-21_51N1 |  | 51 - SOBRECORRENTE TEMPORIZADA NEUTRO | d6627ac7-e7f9-40ce-8741-4e2ec316bb92 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_51N1 |  | FWB_DS_00544 | 20260416 | Status |  |  | SingleBit | 531 | FALSE
FWB_AL21_52-21_SGFT |  | TRIP SGF | 53fc4eb2-4c42-42ce-bd44-a525bde63333 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_SGFT |  | FWB_DS_00545 | 20260416 | Status |  |  | SingleBit | 532 | FALSE
FWB_AL14_52-14_SGFT |  | TRIP SGF | 8bccf1c0-d31a-45ca-8f30-e2f32e94a60c | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_SGFT |  | FWB_DS_00473 | 20260416 | Status |  |  | SingleBit | 332 | FALSE
FWB_AL21_52-21_79_1 |  | 79 - PARTIDA RELIGAMENTO | 2eac6d8a-2241-43a5-a3d5-b52d24060b57 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_79_1 |  | FWB_DS_00547 | 20260416 | Status |  |  | SingleBit | 534 | FALSE
FWB_AL21_52-21_79OK |  | 79 - RELIGAMENTO COM SUCESSO | f414de3f-4747-4ebe-bb87-77bb5d191763 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_79OK |  | FWB_DS_00548 | 20260416 | Status |  |  | SingleBit | 535 | FALSE
FWB_AL21_52-21_79LO |  | 79 - RELIGAMENTO BLOQUEADO | efe8ce02-8da4-46a1-9d51-1d0fa7d55836 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_79LO |  | FWB_DS_00555 | 20260416 | Status |  |  | SingleBit | 536 | FALSE
FWB_AL21_52-21_FSIH |  | FALHA SINCRONISMO HORA | 3ee17fd8-910f-4e47-a386-becd7fe881f0 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_FSIH |  | FWB_DS_00549 | 20260416 | Status |  |  | SingleBit | 538 | FALSE
FWB_AL21_52-21_81SU |  | 81 - TRIP SUB FREQUENCIA | 54e9a583-c0fe-43e2-828a-2986b1fbe519 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_PROT_81SU |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_81SU |  | FWB_DS_00546 | 20260416 | Status |  |  | SingleBit | 533 | FALSE
FWB_AL21_52-21_FLK1 |  | FALHA LINK 1 | 772fdd4e-f2a4-4be3-a578-dfdd9ff05aff | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_FLK1 |  | FWB_DS_00550 | 20260416 | Status |  |  | SingleBit | 539 | FALSE
FWB_AL21_52-21_FCOM |  | FALHA COMUNICACAO | 7173da5e-4508-4f61-a257-4d1b321857e1 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_FCOM |  | FWB_DS_00552 | 20260416 | Status |  |  | SingleBit | 541 | FALSE
FWB_AL21_52-21_TOED |  | 26 49 - TRIP TEMPERATURA | e42ab83b-d108-47cd-86b6-3ffc17c399a8 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_TOED |  | FWB_DS_00553 | 20260416 | Status |  |  | SingleBit | 542 | FALSE
FWB_AL22_52-22_43TC |  | 43 - CHAVE TELECOMANDO | 0f468a14-27a8-40ee-b66e-81d993cd52d2 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_43TC |  | FWB_DS_00556 | 20260416 | Status |  |  | SingleBit | 600 | FALSE
FWB_AL22_52-22_SF6A |  | ALARME BAIXA PRESSAO SF6 | e2146224-71fa-4aa7-95cf-f2e5a77b3ef8 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_SF6A |  | FWB_DS_00558 | 20260416 | Status |  |  | SingleBit | 606 | FALSE
FWB_AL22_52-22_SF6B |  | BLOQUEIO BAIXA PRESSAO SF6 | 4e4cac1f-0105-4b78-9139-38c5b52cefb9 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_SF6B |  | FWB_DS_00559 | 20260416 | Status |  |  | SingleBit | 607 | FALSE
FWB_AL22_52-22_MOLA |  | MOLA | b870421d-0926-472d-8d88-e14a14fa7a9a | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_MOLA |  | FWB_DS_00560 | 20260416 | Status |  |  | SingleBit | 608 | FALSE
FWB_AL22_52-22_CCCO |  | FALTA VCC COMANDO | 22a501a0-87b7-4056-b172-3e1db9ee47ac | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_CCCO |  | FWB_DS_00562 | 20260416 | Status |  |  | SingleBit | 610 | FALSE
FWB_AL22_52-22_CAFL |  | FALTA VCA | f0fc9710-7b0d-4e11-9663-b96aaa34eba8 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_AL22_52-22_CAFL |  | FWB_DS_00561 | 20260416 | Status |  |  | SingleBit | 609 | FALSE
FWB_AL22_52-22_CCMO |  | FALTA VCC MOTOR | 93660b0e-4200-4664-8a0c-301a242b7d27 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_CCMO |  | FWB_DS_00563 | 20260416 | Status |  |  | SingleBit | 611 | FALSE
FWB_AL22_52-22_CCAB |  | FALTA VCC CIRCUITO ABERTURA | 3bfb8988-7a54-4d01-a7fe-46b84fb04322 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_CCAB |  | FWB_DS_00564 | 20260416 | Status |  |  | SingleBit | 612 | FALSE
FWB_AL22_52-22_43LR |  | 43 - CHAVE LOCAL REMOTO | 32101f07-56fa-4339-ac8c-8edcf3a3a481 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_43LR |  | FWB_DS_00565 | 20260416 | Status |  |  | SingleBit | 613 | FALSE
FWB_AL22_52-22_BBAB |  | BOBINA ABERTURA | eea87df6-e1d8-457e-a7a5-e3b5118c1122 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_BBAB |  | FWB_DS_00567 | 20260416 | Status |  |  | SingleBit | 615 | FALSE
FWB_AL22_52-22_CCFL |  | FALTA VCC | c4ef9515-5560-4cc3-ba3f-849dc2e59548 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_AL22_52-22_CCFL |  | FWB_DS_00568 | 20260416 | Status |  |  | SingleBit | 616 | FALSE
FWB_AL22_52-22_TEXT |  | TRIP EXTERNO | 2c8662fd-7c1a-4444-be3f-f9d584ac7d2b | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_TEXT |  | FWB_DS_00578 | 20260416 | Status |  |  | SingleBit | 626 | FALSE
FWB_AL22_52-22_BBFC |  | BOBINA FECHAMENTO | 780de483-ae93-4f75-ae85-0c90e38399d8 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_BBFC |  | FWB_DS_00566 | 20260416 | Status |  |  | SingleBit | 614 | FALSE
FWB_AL22_52-22_62BF |  | 62 - FALHA DISJUNTOR BLOQUEIO | fb15076d-716e-4ab8-b464-dfde747a1f57 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_62BF |  | FWB_DS_00579 | 20260416 | Status |  |  | SingleBit | 627 | FALSE
FWB_AL22_52-22_50F |  | 50 - SOBRECORRENTE INSTANTANEA FASE | 2d72cb07-0b75-4539-815c-dd8400cb2b6f | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_PROT_50F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_50F |  | FWB_DS_00580 | 20260416 | Status |  |  | SingleBit | 628 | FALSE
FWB_AL22_52-22_51F |  | 51 - SOBRECORRENTE TEMPORIZADA FASE | d192068e-3351-4fd0-8fe4-744321a2848e | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_51F |  | FWB_DS_00581 | 20260416 | Status |  |  | SingleBit | 629 | FALSE
FWB_AL21_52-21_CCCO |  | FALTA VCC COMANDO | e74bc90c-4e0e-430d-a94a-ad941208583a | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_CCCO |  | FWB_DS_00523 | 20260416 | Status |  |  | SingleBit | 510 | FALSE
FWB_AL22_52-22_51N1 |  | 51 - SOBRECORRENTE TEMPORIZADA NEUTRO | 6c49d1cd-3eec-4dac-8890-4daaa29930ba | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_51N1 |  | FWB_DS_00583 | 20260416 | Status |  |  | SingleBit | 631 | FALSE
FWB_AL22_52-22_SGFT |  | TRIP SGF | 6f16345d-0052-443e-8118-a5eb25e7aefc | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_SGFT |  | FWB_DS_00584 | 20260416 | Status |  |  | SingleBit | 632 | FALSE
FWB_AL22_52-22_50N |  | 50 - SOBRECORRENTE INSTANTANEA NEUTRO | 5d439a7f-4dfc-4ac9-8b22-b96550c61951 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_PROT_50N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_50N |  | FWB_DS_00582 | 20260416 | Status |  |  | SingleBit | 630 | FALSE
FWB_AL13_52-13_BBAB |  | BOBINA ABERTURA | bf6bea2f-12e4-4d5c-98c2-28a8f98f7bb6 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_BBAB |  | FWB_DS_00417 | 20260416 | Status |  |  | SingleBit | 215 | FALSE
FWB_AL22_52-22_79OK |  | 79 - RELIGAMENTO COM SUCESSO | 8dbb33f0-fcee-457d-a51e-00ba0569ac46 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_79OK |  | FWB_DS_00587 | 20260416 | Status |  |  | SingleBit | 635 | FALSE
FWB_AL22_52-22_79LO |  | 79 - RELIGAMENTO BLOQUEADO | 778b1125-8560-4b47-a351-e702386b847b | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_79LO |  | FWB_DS_00588 | 20260416 | Status |  |  | SingleBit | 636 | FALSE
FWB_AL22_52-22_81SU |  | 81 - TRIP SUB FREQUENCIA | 0ca4f1f6-92eb-4978-b85b-68427a368112 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_PROT_81SU |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_81SU |  | FWB_DS_00585 | 20260416 | Status |  |  | SingleBit | 633 | FALSE
FWB_AL22_52-22_FSIH |  | FALHA SINCRONISMO HORA | 13e42757-fcda-4dae-8148-878435ae8b3c | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_FSIH |  | FWB_DS_00589 | 20260416 | Status |  |  | SingleBit | 638 | FALSE
FWB_AL22_52-22_FLK2 |  | FALHA LINK 2 | 1470c741-f4a8-4253-ac30-23b46b32f456 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_FLK2 |  | FWB_DS_00591 | 20260416 | Status |  |  | SingleBit | 640 | FALSE
FWB_AL22_52-22_FCOM |  | FALHA COMUNICACAO | b58466b9-6a8c-450f-9364-9b2b544e9870 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_FCOM |  | FWB_DS_00592 | 20260416 | Status |  |  | SingleBit | 641 | FALSE
FWB_AL22_52-22_TOED |  | 26 49 - TRIP TEMPERATURA | 7e4c45c6-236d-47d6-b81b-fdec250ef8ac | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_TOED |  | FWB_DS_00593 | 20260416 | Status |  |  | SingleBit | 642 | FALSE
FWB_AL15_52-15_43TC |  | 43 - CHAVE TELECOMANDO | c669fd3f-81a9-4b5b-aae2-d6391812cfe8 | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_43TC |  | FWB_DS_00728 | 20260416 | Status |  |  | SingleBit | 400 | FALSE
FWB_AL15_52-15_SF6A |  | ALARME BAIXA PRESSAO SF6 | feed2b52-90dd-4c20-b704-fa2fdb403d2e | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_SF6A |  | FWB_DS_00730 | 20260416 | Status |  |  | SingleBit | 406 | FALSE
FWB_AL22_52-22_79_1 |  | 79 - PARTIDA RELIGAMENTO | b320fb52-e39f-415a-ae76-fe64e1477762 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_79_1 |  | FWB_DS_00586 | 20260416 | Status |  |  | SingleBit | 634 | FALSE
FWB_AL15_52-15_SF6B |  | BLOQUEIO BAIXA PRESSAO SF6 | 8e35ae56-7711-48e9-a5c2-9d7ce64efe0e | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_SF6B |  | FWB_DS_00731 | 20260416 | Status |  |  | SingleBit | 407 | FALSE
FWB_AL13_52-13_CCFL |  | FALTA VCC | dacee612-84f3-42d9-813e-316796114fe4 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_AL13_52-13_CCFL |  | FWB_DS_00418 | 20260416 | Status |  |  | SingleBit | 216 | FALSE
FWB_AL15_52-15_CAFL |  | FALTA VCA | 0a7965f0-9a1d-4624-9a93-4ed88d9f86d7 | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_AL15_52-15_CAFL |  | FWB_DS_00733 | 20260416 | Status |  |  | SingleBit | 409 | FALSE
FWB_AL15_52-15_MOLA |  | MOLA | 79ddc3a7-5ee4-4338-b83f-b93334d1156a | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_MOLA |  | FWB_DS_00732 | 20260416 | Status |  |  | SingleBit | 408 | FALSE
FWB_AL15_52-15_CCMO |  | FALTA VCC MOTOR | b0add575-af2b-4b25-8e92-3dc65cfe005a | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_CCMO |  | FWB_DS_00735 | 20260416 | Status |  |  | SingleBit | 411 | FALSE
FWB_AL15_52-15_BBFC |  | BOBINA FECHAMENTO | e70274f1-8644-411b-98f1-a5481f3e11ea | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_BBFC |  | FWB_DS_00738 | 20260416 | Status |  |  | SingleBit | 414 | FALSE
FWB_AL15_52-15_43LR |  | 43 - CHAVE LOCAL REMOTO | 1af48c7c-c44c-48e5-b663-19fa1f2a07ea | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_43LR |  | FWB_DS_00737 | 20260416 | Status |  |  | SingleBit | 413 | FALSE
FWB_AL15_52-15_CCCO |  | FALTA VCC COMANDO | 48d39d29-4932-43c7-97fb-737f86ef1163 | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_CCCO |  | FWB_DS_00734 | 20260416 | Status |  |  | SingleBit | 410 | FALSE
FWB_AL15_52-15_BBAB |  | BOBINA ABERTURA | 3b372a40-2bd8-445f-b856-08a064889e4b | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_BBAB |  | FWB_DS_00739 | 20260416 | Status |  |  | SingleBit | 415 | FALSE
FWB_AL15_52-15_CCFL |  | FALTA VCC | abf6233f-fa83-4edc-8e28-41948c798e7e | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_AL15_52-15_CCFL |  | FWB_DS_00740 | 20260416 | Status |  |  | SingleBit | 416 | FALSE
FWB_AL15_52-15_TEXT |  | TRIP EXTERNO | b15f4a1f-f52a-463c-b643-e7d212f1667a | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_TEXT |  | FWB_DS_00750 | 20260416 | Status |  |  | SingleBit | 426 | FALSE
FWB_AL15_52-15_50F |  | 50 - SOBRECORRENTE INSTANTANEA FASE | dae90a5f-6e1a-4775-ada0-6672a09041ea | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_PROT_50F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_50F |  | FWB_DS_00752 | 20260416 | Status |  |  | SingleBit | 428 | FALSE
FWB_AL15_52-15_51F |  | 51 - SOBRECORRENTE TEMPORIZADA FASE | b2b5444f-5810-4974-91a6-66590ae2426a | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_51F |  | FWB_DS_00753 | 20260416 | Status |  |  | SingleBit | 429 | FALSE
FWB_AL15_52-15_51N1 |  | 51 - SOBRECORRENTE TEMPORIZADA NEUTRO | 4dfcaf33-11ec-4fdd-9b1a-05d0d5acbbbc | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_51N1 |  | FWB_DS_00755 | 20260416 | Status |  |  | SingleBit | 431 | FALSE
FWB_AL15_52-15_CCAB |  | FALTA VCC CIRCUITO ABERTURA | 11ab2a2a-e4ad-4c6d-b217-ef00d2591ad1 | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_CCAB |  | FWB_DS_00736 | 20260416 | Status |  |  | SingleBit | 412 | FALSE
FWB_AL15_52-15_50N |  | 50 - SOBRECORRENTE INSTANTANEA NEUTRO | 4603292e-c5b9-4bdb-8b1f-f492a5723b94 | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_PROT_50N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_50N |  | FWB_DS_00754 | 20260416 | Status |  |  | SingleBit | 430 | FALSE
FWB_AL15_52-15_81SU |  | 81 - TRIP SUB FREQUENCIA | fc525711-6720-44a0-9635-4bbf7638f0bf | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_PROT_81SU |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_81SU |  | FWB_DS_00757 | 20260416 | Status |  |  | SingleBit | 433 | FALSE
FWB_AL15_52-15_79LO |  | 79 - RELIGAMENTO BLOQUEADO | 90a580a8-fb75-4540-84bf-906688bb4b7c | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_79LO |  | FWB_DS_00760 | 20260416 | Status |  |  | SingleBit | 436 | FALSE
FWB_AL15_52-15_79_1 |  | 79 - PARTIDA RELIGAMENTO | b4b7182f-9b4b-4287-8afc-4c993bf280c6 | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_79_1 |  | FWB_DS_00758 | 20260416 | Status |  |  | SingleBit | 434 | FALSE
FWB_AL13_52-13_51N1 |  | 51 - SOBRECORRENTE TEMPORIZADA NEUTRO | 33a1621c-5ef4-428b-bcd6-a2ba2d25367a | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_51N1 |  | FWB_DS_00433 | 20260416 | Status |  |  | SingleBit | 231 | FALSE
FWB_AL15_52-15_FSIH |  | FALHA SINCRONISMO HORA | c5c3dfed-7d19-42f4-b8aa-fe0d59cb4844 | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_FSIH |  | FWB_DS_00761 | 20260416 | Status |  |  | SingleBit | 438 | FALSE
FWB_AL13_52-13_MOLA |  | MOLA | 06c200c8-78ad-4d2c-8009-ff7ea4a14287 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_MOLA |  | FWB_DS_00410 | 20260416 | Status |  |  | SingleBit | 208 | FALSE
FWB_AL15_52-15_FLK1 |  | FALHA LINK 1 | 72ad4302-a4d2-4916-a426-f1fcc3e7b671 | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_FLK1 |  | FWB_DS_00762 | 20260416 | Status |  |  | SingleBit | 439 | FALSE
FWB_AL15_52-15_FLK2 |  | FALHA LINK 2 | 6d9688cf-1145-44df-a9f4-f103a76f6f28 | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_FLK2 |  | FWB_DS_00763 | 20260416 | Status |  |  | SingleBit | 440 | FALSE
FWB_AL15_52-15_FCOM |  | FALHA COMUNICACAO | 865090db-2ba9-4f54-a735-d46f2ea5b334 | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_FCOM |  | FWB_DS_00764 | 20260416 | Status |  |  | SingleBit | 441 | FALSE
FWB_AL13_52-13_79OK |  | 79 - RELIGAMENTO COM SUCESSO | bfb3de02-65c3-483d-a9a2-18a7519fca5b | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_79OK |  | FWB_DS_00437 | 20260416 | Status |  |  | SingleBit | 235 | FALSE
FWB_AL24_52-24_43TC |  | 43 - CHAVE TELECOMANDO | 30c133e8-c83b-4dcc-b702-36bb6e420999 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_43TC |  | FWB_DS_00650 | 20260416 | Status |  |  | SingleBit | 1900 | FALSE
FWB_AL24_52-24_SF6B |  | BLOQUEIO BAIXA PRESSAO SF6 | 0fc1ea1f-efcf-4fa5-bd10-3e14bf065823 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_SF6B |  | FWB_DS_00653 | 20260416 | Status |  |  | SingleBit | 1907 | FALSE
FWB_AL24_52-24_MOLA |  | MOLA | a267a979-11f3-4b92-a25a-0c9c628d16bf | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_MOLA |  | FWB_DS_00654 | 20260416 | Status |  |  | SingleBit | 1908 | FALSE
FWB_AL24_52-24_CCCO |  | FALTA VCC COMANDO | 9dd725a2-ceb9-48f3-b21f-f56bcb21a0f3 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_CCCO |  | FWB_DS_00656 | 20260416 | Status |  |  | SingleBit | 1910 | FALSE
FWB_AL13_52-13_TOED |  | 26 49 - TRIP TEMPERATURA | 44314292-9e10-46ea-ab43-3a0563bf383c | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_TOED |  | FWB_DS_00443 | 20260416 | Status |  |  | SingleBit | 242 | FALSE
FWB_AL24_52-24_CCMO |  | FALTA VCC MOTOR | 7c30d196-080b-46d7-9e57-923717232e56 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_CCMO |  | FWB_DS_00657 | 20260416 | Status |  |  | SingleBit | 1911 | FALSE
FWB_AL24_52-24_SF6A |  | ALARME BAIXA PRESSAO SF6 | 12241c14-af3b-48fc-9670-e7ff10d28eb2 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_SF6A |  | FWB_DS_00652 | 20260416 | Status |  |  | SingleBit | 1906 | FALSE
FWB_AL24_52-24_CCAB |  | FALTA VCC CIRCUITO ABERTURA | c8cc5784-3640-4913-b35a-6973f8c43d18 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_CCAB |  | FWB_DS_00658 | 20260416 | Status |  |  | SingleBit | 1912 | FALSE
FWB_AL15_52-15_TOED |  | 26 49 - TRIP TEMPERATURA | 35a3bb4f-ff3a-4440-ad81-dafc04e3168d | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_TOED |  | FWB_DS_00765 | 20260416 | Status |  |  | SingleBit | 442 | FALSE
FWB_AL24_52-24_BBFC |  | BOBINA FECHAMENTO | 911159a8-ca2a-4b34-816f-d28f021c1fed | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_BBFC |  | FWB_DS_00660 | 20260416 | Status |  |  | SingleBit | 1914 | FALSE
FWB_AL24_52-24_BBAB |  | BOBINA ABERTURA | b1b9ddc1-1015-4117-b20e-68d4122e1ad4 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_BBAB |  | FWB_DS_00661 | 20260416 | Status |  |  | SingleBit | 1915 | FALSE
FWB_AL24_52-24_TEXT |  | TRIP EXTERNO | e61b2621-60f5-4dbf-8cd1-dccca3b33eb6 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_TEXT |  | FWB_DS_00672 | 20260416 | Status |  |  | SingleBit | 1926 | FALSE
FWB_AL24_52-24_CCFL |  | FALTA VCC | 825a29d0-aea9-4195-ac61-91306db3ab3d | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_AL24_52-24_CCFL |  | FWB_DS_00662 | 20260416 | Status |  |  | SingleBit | 1916 | FALSE
FWB_AL24_52-24_62BF |  | 62 - FALHA DISJUNTOR BLOQUEIO | 0423b089-85d0-4c18-b6ae-4430df9a0f66 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_62BF |  | FWB_DS_00673 | 20260416 | Status |  |  | SingleBit | 1927 | FALSE
FWB_AL24_52-24_50F |  | 50 - SOBRECORRENTE INSTANTANEA FASE | addc5c82-55d1-48ec-aa28-fc705b6c6678 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_PROT_50F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_50F |  | FWB_DS_00674 | 20260416 | Status |  |  | SingleBit | 1928 | FALSE
FWB_AL24_52-24_CAFL |  | FALTA VCA | 20e9c2e8-78ff-4be8-bf34-a705dffddd2d | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_AL24_52-24_CAFL |  | FWB_DS_00655 | 20260416 | Status |  |  | SingleBit | 1909 | FALSE
FWB_AL24_52-24_50N |  | 50 - SOBRECORRENTE INSTANTANEA NEUTRO | 8b1aae40-b054-4b00-98a7-c582e47f762d | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_PROT_50N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_50N |  | FWB_DS_00676 | 20260416 | Status |  |  | SingleBit | 1930 | FALSE
FWB_AL24_52-24_51N1 |  | 51 - SOBRECORRENTE TEMPORIZADA NEUTRO | b108dafe-a2e9-40f7-b7ef-fe6136598929 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_51N1 |  | FWB_DS_00677 | 20260416 | Status |  |  | SingleBit | 1931 | FALSE
FWB_AL15_52-15_79OK |  | 79 - RELIGAMENTO COM SUCESSO | 8d0937f0-42e3-46ea-b143-492c0b6a42ed | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_79OK |  | FWB_DS_00759 | 20260416 | Status |  |  | SingleBit | 435 | FALSE
FWB_AL24_52-24_81SU |  | 81 - TRIP SUB FREQUENCIA | 967b06d2-1051-4c70-a73a-8c54691e91ed | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_PROT_81SU |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_81SU |  | FWB_DS_00679 | 20260416 | Status |  |  | SingleBit | 1933 | FALSE
FWB_AL24_52-24_79_1 |  | 79 - PARTIDA RELIGAMENTO | 46f8ebca-874b-437a-950f-59ad138665a0 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_79_1 |  | FWB_DS_00680 | 20260416 | Status |  |  | SingleBit | 1934 | FALSE
FWB_AL24_52-24_79OK |  | 79 - RELIGAMENTO COM SUCESSO | 72eb9b3a-55de-4ebf-b112-fde16bd35a54 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_79OK |  | FWB_DS_00681 | 20260416 | Status |  |  | SingleBit | 1935 | FALSE
FWB_AL24_52-24_79LO |  | 79 - RELIGAMENTO BLOQUEADO | 99b7e565-5996-446e-80ba-0b2f680b66a4 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_79LO |  | FWB_DS_00682 | 20260416 | Status |  |  | SingleBit | 1936 | FALSE
FWB_AL24_52-24_FSIH |  | FALHA SINCRONISMO HORA | a205eb18-c35b-4c00-8ad5-68a9a71508d6 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_FSIH |  | FWB_DS_00683 | 20260416 | Status |  |  | SingleBit | 1938 | FALSE
FWB_AL24_52-24_FLK2 |  | FALHA LINK 2 | babec8f1-e4a7-4e86-a0d1-97e0705aa2fb | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_FLK2 |  | FWB_DS_00685 | 20260416 | Status |  |  | SingleBit | 1940 | FALSE
FWB_AL24_52-24_FLK1 |  | FALHA LINK 1 | a79c0888-7122-4c13-a063-fb24a60c4faa | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_FLK1 |  | FWB_DS_00684 | 20260416 | Status |  |  | SingleBit | 1939 | FALSE
FWB_AL24_52-24_FCOM |  | FALHA COMUNICACAO | 7353d93c-e615-4856-841b-99c2c3201bc1 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_FCOM |  | FWB_DS_00686 | 20260416 | Status |  |  | SingleBit | 1941 | FALSE
FWB_AL24_52-24_TOED |  | 26 49 - TRIP TEMPERATURA | 28a3d7fa-e1d6-46b1-90b3-66aacc25f805 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_TOED |  | FWB_DS_00687 | 20260416 | Status |  |  | SingleBit | 1942 | FALSE
FWB_AL25_52-25_SF6B |  | BLOQUEIO BAIXA PRESSAO SF6 | 8f1a450a-746d-4321-b606-38cee5855172 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_SF6B |  | FWB_DS_00692 | 20260416 | Status |  |  | SingleBit | 2007 | FALSE
FWB_AL25_52-25_SF6A |  | ALARME BAIXA PRESSAO SF6 | 67ca8de5-d931-468a-a72b-3970d99ef4fd | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_SF6A |  | FWB_DS_00691 | 20260416 | Status |  |  | SingleBit | 2006 | FALSE
FWB_AL25_52-25_43TC |  | 43 - CHAVE TELECOMANDO | 20a40741-8d45-4c6f-8034-56e5a352109d | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_43TC |  | FWB_DS_00689 | 20260416 | Status |  |  | SingleBit | 2000 | FALSE
FWB_AL25_52-25_CAFL |  | FALTA VCA | 8e3b7126-c023-4e2a-8476-5d385723f874 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_AL25_52-25_CAFL |  | FWB_DS_00694 | 20260416 | Status |  |  | SingleBit | 2009 | FALSE
FWB_AL25_52-25_CCCO |  | FALTA VCC COMANDO | 3986e396-f7ff-45bd-8713-72a090ecf7b4 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_CCCO |  | FWB_DS_00695 | 20260416 | Status |  |  | SingleBit | 2010 | FALSE
FWB_AL25_52-25_CCMO |  | FALTA VCC MOTOR | e33c125c-b5a1-406d-b202-4e762a5162e9 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_CCMO |  | FWB_DS_00696 | 20260416 | Status |  |  | SingleBit | 2011 | FALSE
FWB_AL25_52-25_CCAB |  | FALTA VCC CIRCUITO ABERTURA | 5cb86a5b-cb99-4ab6-a990-520d8b57e02d | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_CCAB |  | FWB_DS_00697 | 20260416 | Status |  |  | SingleBit | 2012 | FALSE
FWB_AL25_52-25_MOLA |  | MOLA | a72829f5-5188-4b43-ad37-9e76da07509f | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_MOLA |  | FWB_DS_00693 | 20260416 | Status |  |  | SingleBit | 2008 | FALSE
FWB_AL25_52-25_BBFC |  | BOBINA FECHAMENTO | dd5c116a-9f23-4bb8-a768-3f2e494dc595 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_BBFC |  | FWB_DS_00699 | 20260416 | Status |  |  | SingleBit | 2014 | FALSE
FWB_AL25_52-25_BBAB |  | BOBINA ABERTURA | 6335d671-c08f-4d5c-a286-7c85f378a849 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_BBAB |  | FWB_DS_00700 | 20260416 | Status |  |  | SingleBit | 2015 | FALSE
FWB_AL25_52-25_CCFL |  | FALTA VCC | d4ddd2da-3112-4c7d-858a-edd2861ec9e2 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_AL25_52-25_CCFL |  | FWB_DS_00701 | 20260416 | Status |  |  | SingleBit | 2016 | FALSE
FWB_AL25_52-25_43LR |  | 43 - CHAVE LOCAL REMOTO | 14d99d3f-9724-4d84-a970-ad83c38a744c | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_43LR |  | FWB_DS_00698 | 20260416 | Status |  |  | SingleBit | 2013 | FALSE
FWB_AL25_52-25_TEXT |  | TRIP EXTERNO | 92c5da40-090d-4f07-954d-c52ca0c02854 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_TEXT |  | FWB_DS_00711 | 20260416 | Status |  |  | SingleBit | 2026 | FALSE
FWB_AL25_52-25_62BF |  | 62 - FALHA DISJUNTOR BLOQUEIO | 3844c483-83a4-4ee7-adb7-8d4a03e9d31e | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_62BF |  | FWB_DS_00712 | 20260416 | Status |  |  | SingleBit | 2027 | FALSE
FWB_AL25_52-25_50F |  | 50 - SOBRECORRENTE INSTANTANEA FASE | f672d177-7574-4c18-a5cf-b63ccafd4359 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_PROT_50F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_50F |  | FWB_DS_00713 | 20260416 | Status |  |  | SingleBit | 2028 | FALSE
FWB_AL25_52-25_51F |  | 51 - SOBRECORRENTE TEMPORIZADA FASE | 67260852-9d7b-43b6-9bd8-094557459f82 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_51F |  | FWB_DS_00714 | 20260416 | Status |  |  | SingleBit | 2029 | FALSE
FWB_AL25_52-25_51N1 |  | 51 - SOBRECORRENTE TEMPORIZADA NEUTRO | dc365161-a9b4-45dc-a91a-ce1afb3d2968 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_51N1 |  | FWB_DS_00716 | 20260416 | Status |  |  | SingleBit | 2031 | FALSE
FWB_AL25_52-25_50N |  | 50 - SOBRECORRENTE INSTANTANEA NEUTRO | 18c854cd-1fab-4867-a0d9-d0d4f09bc0d6 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_PROT_50N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_50N |  | FWB_DS_00715 | 20260416 | Status |  |  | SingleBit | 2030 | FALSE
FWB_AL25_52-25_SGFT |  | TRIP SGF | 5a622560-6037-494f-bb53-e5aa62141eb1 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_SGFT |  | FWB_DS_00717 | 20260416 | Status |  |  | SingleBit | 2032 | FALSE
FWB_AL25_52-25_81SU |  | 81 - TRIP SUB FREQUENCIA | bc1a453d-1a3f-466b-8269-d90acb8b856c | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_PROT_81SU |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_81SU |  | FWB_DS_00718 | 20260416 | Status |  |  | SingleBit | 2033 | FALSE
FWB_AL24_52-24_43LR |  | 43 - CHAVE LOCAL REMOTO | 888fea5b-752e-418f-9dfd-d3d8fe320265 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_43LR |  | FWB_DS_00659 | 20260416 | Status |  |  | SingleBit | 1913 | FALSE
FWB_AL25_52-25_79OK |  | 79 - RELIGAMENTO COM SUCESSO | 59543bde-4ec0-406f-a0e9-6fa31ace0ca9 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_79OK |  | FWB_DS_00720 | 20260416 | Status |  |  | SingleBit | 2035 | FALSE
FWB_AL25_52-25_FSIH |  | FALHA SINCRONISMO HORA | fe0f7192-8f7b-4c0f-84da-21d88d34d09d | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_FSIH |  | FWB_DS_00722 | 20260416 | Status |  |  | SingleBit | 2038 | FALSE
FWB_AL24_52-24_51F |  | 51 - SOBRECORRENTE TEMPORIZADA FASE | 3b7ac695-66e0-4db1-8de0-7596019b51fe | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_51F |  | FWB_DS_00675 | 20260416 | Status |  |  | SingleBit | 1929 | FALSE
FWB_AL25_52-25_FLK2 |  | FALHA LINK 2 | d8661260-cffc-4067-baf9-d6d050325057 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_FLK2 |  | FWB_DS_00724 | 20260416 | Status |  |  | SingleBit | 2040 | FALSE
FWB_AL25_52-25_79_1 |  | 79 - PARTIDA RELIGAMENTO | 2f4bc196-0804-459a-997b-5c4516977be3 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_79_1 |  | FWB_DS_00719 | 20260416 | Status |  |  | SingleBit | 2034 | FALSE
FWB_AL25_52-25_FCOM |  | FALHA COMUNICACAO | 150cc959-771c-41d2-a334-bb99ad658e30 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_FCOM |  | FWB_DS_00725 | 20260416 | Status |  |  | SingleBit | 2041 | FALSE
FWB_AL25_52-25_TOED |  | 26 49 - TRIP TEMPERATURA | c3f863c6-e9bc-4476-a551-1402d8dfe9f8 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_TOED |  | FWB_DS_00726 | 20260416 | Status |  |  | SingleBit | 2042 | FALSE
FWB_AL25_52-25_FLK1 |  | FALHA LINK 1 | ac20869a-2bb1-49c6-a9cc-c1176e89ed11 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_FLK1 |  | FWB_DS_00723 | 20260416 | Status |  |  | SingleBit | 2039 | FALSE
FWB_AL25_52-25_79LO |  | 79 - RELIGAMENTO BLOQUEADO | 59ccddb1-ccc9-4c26-bd91-98e049ed8f0f | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_79LO |  | FWB_DS_00721 | 20260416 | Status |  |  | SingleBit | 2036 | FALSE
FWB_AL15_52-15_62BF |  | 62 - FALHA DISJUNTOR BLOQUEIO | a0499fee-069b-42d9-9800-7758dda81cd0 | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_62BF |  | FWB_DS_00751 | 20260416 | Status |  |  | SingleBit | 427 | FALSE
FWB_AL15_52-15_SGFT |  | TRIP SGF | 319ef666-d121-4e4e-9d6d-cffefcdc6730 | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_SGFT |  | FWB_DS_00756 | 20260416 | Status |  |  | SingleBit | 432 | FALSE
FWB_AL24_52-24_SGFT |  | TRIP SGF | 625a5480-ac5a-418f-a808-dd24d13031bf | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_SGFT |  | FWB_DS_00678 | 20260416 | Status |  |  | SingleBit | 1932 | FALSE
FWB_AL13_52-13_CAFL |  | FALTA VCA | 457a62bc-a00a-4dc6-b7ab-c4e734d59f2e | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_AL13_52-13_CAFL |  | FWB_DS_00411 | 20260416 | Status |  |  | SingleBit | 209 | FALSE
FWB_AL13_52-13_BBFC |  | BOBINA FECHAMENTO | c2494550-ecc2-4552-bdbd-398fad9ca81d | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_BBFC |  | FWB_DS_00416 | 20260416 | Status |  |  | SingleBit | 214 | FALSE
FWB_AL13_52-13_62BF |  | 62 - FALHA DISJUNTOR BLOQUEIO | 92509cb1-bda5-4f1e-99e6-f25a0bcba155 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_62BF |  | FWB_DS_00429 | 20260416 | Status |  |  | SingleBit | 227 | FALSE
FWB_AL13_52-13_TEXT |  | TRIP EXTERNO | 5193f57e-4302-47bc-881f-c67dcb0d5411 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_TEXT |  | FWB_DS_00428 | 20260416 | Status |  |  | SingleBit | 226 | FALSE
FWB_AL13_52-13_43LR |  | 43 - CHAVE LOCAL REMOTO | 8d9150d4-29a3-4b8a-a128-b670e47bfb7e | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_43LR |  | FWB_DS_00415 | 20260416 | Status |  |  | SingleBit | 213 | FALSE
FWB_AL14_52-14_CCCO |  | FALTA VCC COMANDO | dd61cc38-6129-40c8-9e45-21b47c3d4798 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_CCCO |  | FWB_DS_00451 | 20260416 | Status |  |  | SingleBit | 310 | FALSE
FWB_AL14_52-14_79_1 |  | 79 - PARTIDA RELIGAMENTO | 997263a5-0597-4dc3-a559-2d10dc2ce1b6 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_79_1 |  | FWB_DS_00475 | 20260416 | Status |  |  | SingleBit | 334 | FALSE
FWB_AL21_52-21_BBFC |  | BOBINA FECHAMENTO | 813a9e04-3729-4c93-a186-d2067868806c | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_BBFC |  | FWB_DS_00527 | 20260416 | Status |  |  | SingleBit | 514 | FALSE
FWB_AL13_52-13_FLK1 |  | FALHA LINK 1 | 92143eb9-5662-43e0-9b84-98bcc95388a1 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_FLK1 |  | FWB_DS_00440 | 20260416 | Status |  |  | SingleBit | 239 | FALSE
FWB_AL14_52-14_TEXT |  | TRIP EXTERNO | 4df7d552-c16c-443c-908e-a7ddb2c8776c | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_TEXT |  | FWB_DS_00467 | 20260416 | Status |  |  | SingleBit | 326 | FALSE
FWB_AL21_52-21_FLK2 |  | FALHA LINK 2 | 0b854a54-465e-416b-9ff1-2c61c961aa9f | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_FLK2 |  | FWB_DS_00551 | 20260416 | Status |  |  | SingleBit | 540 | FALSE
FWB_AL22_52-22_FLK1 |  | FALHA LINK 1 | 8c460671-fca7-4e1b-b853-d92b81aeac5b | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_FLK1 |  | FWB_DS_00590 | 20260416 | Status |  |  | SingleBit | 639 | FALSE
FWB_AL21_52-21_50N |  | 50 - SOBRECORRENTE INSTANTANEA NEUTRO | 9354727c-51a5-45cc-9946-33e63be8a032 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_PROT_50N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_50N |  | FWB_DS_00543 | 20260416 | Status |  |  | SingleBit | 530 | FALSE
FWB_AL13_52-13_81U5 |  | AJUSTE PARA 81 E5 | c10b6aff-35cb-4fac-b6a8-43fcfee5802b | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_81U5 |  | FWB_DS_00426 | 20260416 | Status | 30 | DirectOperate | SingleBit | 224 | FALSE | FALSE | 5 | SingleCoord | 49 | ClosePulseOn | 0.25
FWB_AL13_52-13_51N |  | 51N | 370de65b-2c7a-43a2-8da3-35742adfecc6 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL13_52-13_51N |  | FWB_DS_00421 | 20260416 | Status | 30 | DirectOperate | SingleBit | 219 | FALSE | FALSE | 15 | SingleCoord | 43;43 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL14_52-14_51N |  | 51N | 9cf88979-f041-4e2a-92c8-478b3a580907 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL14_52-14_51N |  | FWB_DS_00460 | 20260416 | Status | 30 | DirectOperate | SingleBit | 319 | FALSE | FALSE | 15 | SingleCoord | 63;63 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL14_52-14_81U4 |  | AJUSTE PARA 81 E4 | 43e7e73f-a1c0-4307-be94-6b6aa7671a99 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_81U4 |  | FWB_DS_00464 | 20260416 | Status | 30 | DirectOperate | SingleBit | 323 | FALSE | FALSE | 5 | SingleCoord | 68 | ClosePulseOn | 0.25
FWB_AL14_52-14_81U2 |  | AJUSTE PARA 81 E2 | bd0ddf44-9d53-4f5b-aa42-5c61a7ccd6e0 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_81U2 |  | FWB_DS_00462 | 20260416 | Status | 30 | DirectOperate | SingleBit | 321 | FALSE | FALSE | 5 | SingleCoord | 66 | ClosePulseOn | 0.25
FWB_AL14_52-14_81 |  | 81 - FUNCAO SUB/SOB FREQUENCIA | b4c3c299-e8ea-41ac-9eb5-1c5826badd0f | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL14_52-14_81 |  | FWB_DS_00466 | 20260416 | Status | 30 | DirectOperate | SingleBit | 325 | FALSE | FALSE | 5 | SingleCoord | 70;70 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL21_52-21_2649 |  | 26 49 - FUNCAO TEMPERATURA | 165bf7e0-54d9-4642-a8d6-4caf0b7b1c0e | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_2649 |  | FWB_DS_00531 | 20260416 | Status | 30 | DirectOperate | SingleBit | 518 | FALSE | FALSE | 15 | SingleCoord | 104;104 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_AL13_52-13_81 |  | 81 - FUNCAO SUB/SOB FREQUENCIA | c961bd72-2b09-4de2-ac99-fe2b03f71d0f | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL13_52-13_81 |  | FWB_DS_00427 | 20260416 | Status | 30 | DirectOperate | SingleBit | 225 | FALSE | FALSE | 5 | SingleCoord | 50;50 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL13_52-13_2649 |  | 26 49 - FUNCAO TEMPERATURA | f9d92552-f323-4787-ad89-8f8ab4949d92 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_2649 |  | FWB_DS_00420 | 20260416 | Status | 30 | DirectOperate | SingleBit | 218 | FALSE | FALSE | 15 | SingleCoord | 44;44 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_AL21_52-21_79 |  | 79 - FUNCAO RELIGAMENTO | 752fc3a3-acf7-475c-88f2-ad988ac87c50 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL21_52-21_79 |  | FWB_DS_00530 | 20260416 | Status | 30 | DirectOperate | SingleBit | 517 | FALSE | FALSE | 15 | SingleCoord | 102;102 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_AL21_52-21_81U1 |  | AJUSTE PARA 81 E1 | c29c5ab1-313c-4e1b-9162-304cccbfce4b | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_81U1 |  | FWB_DS_00533 | 20260416 | Status | 30 | DirectOperate | SingleBit | 520 | FALSE | FALSE | 5 | SingleCoord | 105 | ClosePulseOn | 0.25
FWB_AL21_52-21_81U3 |  | AJUSTE PARA 81 E3 | aabb3616-f70c-4fa1-9a79-6388782d4396 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_81U3 |  | FWB_DS_00535 | 20260416 | Status | 30 | DirectOperate | SingleBit | 522 | FALSE | FALSE | 5 | SingleCoord | 107 | ClosePulseOn | 0.25
FWB_AL21_52-21_81U5 |  | AJUSTE PARA 81 E5 | 12e8ad78-b5a7-445f-bbb7-a2c775f67d11 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_81U5 |  | FWB_DS_00537 | 20260416 | Status | 30 | DirectOperate | SingleBit | 524 | FALSE | FALSE | 5 | SingleCoord | 109 | ClosePulseOn | 0.25
FWB_AL13_52-13_AJG2 |  | AJUSTE PARA GRUPO 2 | a091ae20-3712-4180-9642-3893b2dc6796 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 2 |  | UTR_FWB_1 | FWB_AL13_52-13_AJG2 |  | FWB_DS_00407 | 20260416 | Status | 30 | DirectOperate | SingleBit | 202 | FALSE | FALSE | 15 | MultiCoord | 51;52 | ClosePulseOn;ClosePulseOn | 0.25;0.25
FWB_AL21_52-21_81 |  | 81 - FUNCAO SUB/SOB FREQUENCIA | cb2541ba-bf71-469e-a009-1238668998f1 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL21_52-21_81 |  | FWB_DS_00538 | 20260416 | Status | 30 | DirectOperate | SingleBit | 525 | FALSE | FALSE | 5 | SingleCoord | 110;110 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL22_52-22_AJG2 |  | AJUSTE PARA GRUPO 2 | fa13dc4b-d857-48e9-a4ec-6bedc8b52688 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 2 |  | UTR_FWB_1 | FWB_AL22_52-22_AJG2 |  | FWB_DS_00557 | 20260416 | Status | 30 | DirectOperate | SingleBit | 602 | FALSE | FALSE | 15 | MultiCoord | 131;132 | ClosePulseOn;ClosePulseOn | 0.25;0.25
FWB_AL22_52-22_79 |  | 79 - FUNCAO RELIGAMENTO | 8263722e-0eef-4fc0-bf75-71bebe4f0f7c | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL22_52-22_79 |  | FWB_DS_00569 | 20260416 | Status | 30 | DirectOperate | SingleBit | 617 | FALSE | FALSE | 15 | SingleCoord | 122;122 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_AL14_52-14_81U3 |  | AJUSTE PARA 81 E3 | 4b09637c-19f7-4607-9d3d-2e88977aa81d | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_81U3 |  | FWB_DS_00463 | 20260416 | Status | 30 | DirectOperate | SingleBit | 322 | FALSE | FALSE | 5 | SingleCoord | 67 | ClosePulseOn | 0.25
FWB_AL21_52-21_AJG2 |  | AJUSTE PARA GRUPO 2 | 6a609c8a-2e30-4c05-a4fd-ba484a450c8b | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 2 |  | UTR_FWB_1 | FWB_AL21_52-21_AJG2 |  | FWB_DS_00518 | 20260416 | Status | 30 | DirectOperate | SingleBit | 502 | FALSE | FALSE | 15 | MultiCoord | 111;112 | ClosePulseOn;ClosePulseOn | 0.25;0.25
FWB_AL22_52-22_51N |  | 51N | bfbea8db-8f3f-4ff4-8d14-233e552e69b0 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL22_52-22_51N |  | FWB_DS_00571 | 20260416 | Status | 30 | DirectOperate | SingleBit | 619 | FALSE | FALSE | 15 | SingleCoord | 123;123 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL22_52-22_81U1 |  | AJUSTE PARA 81 E1 | 0fb1b2af-c6d2-448c-9e56-0d73a7f1da2b | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_81U1 |  | FWB_DS_00572 | 20260416 | Status | 30 | DirectOperate | SingleBit | 620 | FALSE | FALSE | 5 | SingleCoord | 125 | ClosePulseOn | 0.25
FWB_AL22_52-22_81U2 |  | AJUSTE PARA 81 E2 | 298c3957-4e61-4fad-a604-d5ac613cb907 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_81U2 |  | FWB_DS_00573 | 20260416 | Status | 30 | DirectOperate | SingleBit | 621 | FALSE | FALSE | 5 | SingleCoord | 126 | ClosePulseOn | 0.25
FWB_AL22_52-22_81U3 |  | AJUSTE PARA 81 E3 | f8179819-f864-4587-87cc-8d8c92031531 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_81U3 |  | FWB_DS_00574 | 20260416 | Status | 30 | DirectOperate | SingleBit | 622 | FALSE | FALSE | 5 | SingleCoord | 127 | ClosePulseOn | 0.25
FWB_AL22_52-22_81U4 |  | AJUSTE PARA 81 E4 | 099f7ac0-c32c-4dd7-9157-feaf171fdada | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_81U4 |  | FWB_DS_00575 | 20260416 | Status | 30 | DirectOperate | SingleBit | 623 | FALSE | FALSE | 5 | SingleCoord | 128 | ClosePulseOn | 0.25
FWB_AL22_52-22_81U5 |  | AJUSTE PARA 81 E5 | 693e4762-48ec-4203-8d83-22e80cec72da | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_81U5 |  | FWB_DS_00576 | 20260416 | Status | 30 | DirectOperate | SingleBit | 624 | FALSE | FALSE | 5 | SingleCoord | 129 | ClosePulseOn | 0.25
FWB_AL22_52-22_81 |  | 81 - FUNCAO SUB/SOB FREQUENCIA | 7fd51ae9-2a5a-4370-9381-305c9c67fe57 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL22_52-22_81 |  | FWB_DS_00577 | 20260416 | Status | 30 | DirectOperate | SingleBit | 625 | FALSE | FALSE | 5 | SingleCoord | 130;130 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL22_52-22_DJF1 |  | DISJUNTOR NF | 0462653e-d4c5-417c-a23e-943bc21e9319 | SwitchStatus | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_FWB_1 | FWB_AL22_52-22_DJF1 |  | FWB_DS_00594 | 20260416 | Status | 30 | DirectOperate | MultiCoord | 603;604 | FALSE | FALSE | 15 | SingleCoord | 121;121 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL21_52-21_81U4 |  | AJUSTE PARA 81 E4 | ee8c322e-1145-4e2f-82d8-d337dd39ac0d | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_81U4 |  | FWB_DS_00536 | 20260416 | Status | 30 | DirectOperate | SingleBit | 523 | FALSE | FALSE | 5 | SingleCoord | 108 | ClosePulseOn | 0.25
FWB_AL15_52-15_79 |  | 79 - FUNCAO RELIGAMENTO | df930c2c-92af-4e33-8a82-a271ea8cc970 | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL15_52-15_79 |  | FWB_DS_00741 | 20260416 | Status | 30 | DirectOperate | SingleBit | 417 | FALSE | FALSE | 15 | SingleCoord | 82;82 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_AL15_52-15_51N |  | 51N | 00360fd6-a147-449f-99c9-a87c6bda12f9 | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL15_52-15_51N |  | FWB_DS_00743 | 20260416 | Status | 30 | DirectOperate | SingleBit | 419 | FALSE | FALSE | 15 | SingleCoord | 83;83 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL15_52-15_2649 |  | 26 49 - FUNCAO TEMPERATURA | 38c6e60c-79f3-4a9d-846e-a62ff04bb72f | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_2649 |  | FWB_DS_00742 | 20260416 | Status | 30 | DirectOperate | SingleBit | 418 | FALSE | FALSE | 15 | SingleCoord | 84;84 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_AL13_52-13_81U4 |  | AJUSTE PARA 81 E4 | 6e311ede-6b93-44ab-97d5-dc837b1cc679 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_81U4 |  | FWB_DS_00425 | 20260416 | Status | 30 | DirectOperate | SingleBit | 223 | FALSE | FALSE | 5 | SingleCoord | 48 | ClosePulseOn | 0.25
FWB_AL21_52-21_DJF1 |  | DISJUNTOR NF | fbf98ebf-6faf-44e6-8b60-c1c9ae8f9c56 | SwitchStatus | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_FWB_1 | FWB_AL21_52-21_DJF1 |  | FWB_DS_00554 | 20260416 | Status | 30 | DirectOperate | MultiCoord | 503;504 | FALSE | FALSE | 15 | SingleCoord | 101;101 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL15_52-15_81U1 |  | AJUSTE PARA 81 E1 | e4a84d08-1c05-4013-b0d1-57e5d9e2ab61 | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_81U1 |  | FWB_DS_00744 | 20260416 | Status | 30 | DirectOperate | SingleBit | 420 | FALSE | FALSE | 5 | SingleCoord | 85 | ClosePulseOn | 0.25
FWB_AL15_52-15_81U2 |  | AJUSTE PARA 81 E2 | 60447bc8-a9fe-4179-8d52-ed63053a416f | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_81U2 |  | FWB_DS_00745 | 20260416 | Status | 30 | DirectOperate | SingleBit | 421 | FALSE | FALSE | 5 | SingleCoord | 86 | ClosePulseOn | 0.25
FWB_AL14_52-14_79 |  | 79 - FUNCAO RELIGAMENTO | 6f561b75-9a53-401e-96bd-19d1134f8142 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL14_52-14_79 |  | FWB_DS_00458 | 20260416 | Status | 30 | DirectOperate | SingleBit | 317 | FALSE | FALSE | 15 | SingleCoord | 62;62 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_AL15_52-15_81U5 |  | AJUSTE PARA 81 E5 | e6c35240-ae73-49cd-8ded-89b03990375d | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_81U5 |  | FWB_DS_00748 | 20260416 | Status | 30 | DirectOperate | SingleBit | 424 | FALSE | FALSE | 5 | SingleCoord | 89 | ClosePulseOn | 0.25
FWB_AL15_52-15_DJF1 |  | DISJUNTOR NF | adf29be8-4f63-4032-ab71-ca186b38fea4 | SwitchStatus | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_FWB_1 | FWB_AL15_52-15_DJF1 |  | FWB_DS_00766 | 20260416 | Status | 30 | DirectOperate | MultiCoord | 403;404 | FALSE | FALSE | 15 | SingleCoord | 81;81 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL15_52-15_81U3 |  | AJUSTE PARA 81 E3 | 93f69455-f6db-4964-ad36-510f27208953 | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_81U3 |  | FWB_DS_00746 | 20260416 | Status | 30 | DirectOperate | SingleBit | 422 | FALSE | FALSE | 5 | SingleCoord | 87 | ClosePulseOn | 0.25
FWB_AL24_52-24_AJG2 |  | AJUSTE PARA GRUPO 2 | 724e1838-4b0c-4502-a4d3-5f79a5093e81 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 2 |  | UTR_FWB_1 | FWB_AL24_52-24_AJG2 |  | FWB_DS_00651 | 20260416 | Status | 30 | DirectOperate | SingleBit | 1902 | FALSE | FALSE | 15 | MultiCoord | 371;372 | ClosePulseOn;ClosePulseOn | 0.25;0.25
FWB_AL13_52-13_81U2 |  | AJUSTE PARA 81 E2 | 72145e82-8ac6-4b72-b432-a689fe540f70 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_81U2 |  | FWB_DS_00423 | 20260416 | Status | 30 | DirectOperate | SingleBit | 221 | FALSE | FALSE | 5 | SingleCoord | 46 | ClosePulseOn | 0.25
FWB_AL24_52-24_81U1 |  | AJUSTE PARA 81 E1 | 5ef45c73-dafe-435a-afa0-01829c972327 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_81U1 |  | FWB_DS_00666 | 20260416 | Status | 30 | DirectOperate | SingleBit | 1920 | FALSE | FALSE | 5 | SingleCoord | 365 | ClosePulseOn | 0.25
FWB_AL24_52-24_81U2 |  | AJUSTE PARA 81 E2 | 7a4f79e3-0210-4267-b815-ff2589ff745e | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_81U2 |  | FWB_DS_00667 | 20260416 | Status | 30 | DirectOperate | SingleBit | 1921 | FALSE | FALSE | 5 | SingleCoord | 366 | ClosePulseOn | 0.25
FWB_AL24_52-24_81U3 |  | AJUSTE PARA 81 E3 | 10d6edae-0e79-4edb-a268-72c6118d2730 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_81U3 |  | FWB_DS_00668 | 20260416 | Status | 30 | DirectOperate | SingleBit | 1922 | FALSE | FALSE | 5 | SingleCoord | 367 | ClosePulseOn | 0.25
FWB_AL24_52-24_79 |  | 79 - FUNCAO RELIGAMENTO | ae373566-c125-4450-b270-167de8d98c0d | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL24_52-24_79 |  | FWB_DS_00663 | 20260416 | Status | 30 | DirectOperate | SingleBit | 1917 | FALSE | FALSE | 15 | SingleCoord | 362;362 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_AL24_52-24_2649 |  | 26 49 - FUNCAO TEMPERATURA | c1b15c41-eece-413b-8296-8699a3d49d3b | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_2649 |  | FWB_DS_00664 | 20260416 | Status | 30 | DirectOperate | SingleBit | 1918 | FALSE | FALSE | 15 | SingleCoord | 364;364 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_AL24_52-24_81 |  | 81 - FUNCAO SUB/SOB FREQUENCIA | 5556b50b-3455-4d88-b398-19ce981627e8 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL24_52-24_81 |  | FWB_DS_00671 | 20260416 | Status | 30 | DirectOperate | SingleBit | 1925 | FALSE | FALSE | 5 | SingleCoord | 370;370 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL15_52-15_81U4 |  | AJUSTE PARA 81 E4 | 45d83c72-dfd2-496c-b597-6daa8b05601e | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_81U4 |  | FWB_DS_00747 | 20260416 | Status | 30 | DirectOperate | SingleBit | 423 | FALSE | FALSE | 5 | SingleCoord | 88 | ClosePulseOn | 0.25
FWB_AL25_52-25_AJG2 |  | AJUSTE PARA GRUPO 2 | 390179a9-40ce-484d-a935-be3ff39e540b | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 2 |  | UTR_FWB_1 | FWB_AL25_52-25_AJG2 |  | FWB_DS_00690 | 20260416 | Status | 30 | DirectOperate | SingleBit | 2002 | FALSE | FALSE | 15 | MultiCoord | 391;392 | ClosePulseOn;ClosePulseOn | 0.25;0.25
FWB_AL24_52-24_81U4 |  | AJUSTE PARA 81 E4 | a8169082-8c5f-4731-9e0f-ec6b5854d62c | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_81U4 |  | FWB_DS_00669 | 20260416 | Status | 30 | DirectOperate | SingleBit | 1923 | FALSE | FALSE | 5 | SingleCoord | 368 | ClosePulseOn | 0.25
FWB_AL24_52-24_DJF1 |  | DISJUNTOR NF | ba0e00c7-a717-4a64-b77f-967aa7d99d04 | SwitchStatus | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_FWB_1 | FWB_AL24_52-24_DJF1 |  | FWB_DS_00688 | 20260416 | Status | 30 | DirectOperate | MultiCoord | 1903;1904 | FALSE | FALSE | 15 | SingleCoord | 361;361 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL14_52-14_81U5 |  | AJUSTE PARA 81 E5 | da0e8c95-c5e3-4a40-9e47-1f7b9d3ff9c5 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_81U5 |  | FWB_DS_00465 | 20260416 | Status | 30 | DirectOperate | SingleBit | 324 | FALSE | FALSE | 5 | SingleCoord | 69 | ClosePulseOn | 0.25
FWB_AL24_52-24_51N |  | 51N | 60a0bfe3-a792-4bbe-af49-96c018f696fe | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL24_52-24_51N |  | FWB_DS_00665 | 20260416 | Status | 30 | DirectOperate | SingleBit | 1919 | FALSE | FALSE | 15 | SingleCoord | 363;363 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL25_52-25_51N |  | 51N | d8baf587-e315-4d76-98cb-cf3f4ac2403f | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL25_52-25_51N |  | FWB_DS_00704 | 20260416 | Status | 30 | DirectOperate | SingleBit | 2019 | FALSE | FALSE | 15 | SingleCoord | 383;383 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL25_52-25_81U1 |  | AJUSTE PARA 81 E1 | af0cdfee-8dfc-4787-b355-a89192b9a0bc | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_81U1 |  | FWB_DS_00705 | 20260416 | Status | 30 | DirectOperate | SingleBit | 2020 | FALSE | FALSE | 5 | SingleCoord | 385 | ClosePulseOn | 0.25
FWB_AL25_52-25_81U3 |  | AJUSTE PARA 81 E3 | 7b4b8473-4e1a-40bc-b8bb-7c7ab3353cad | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_81U3 |  | FWB_DS_00707 | 20260416 | Status | 30 | DirectOperate | SingleBit | 2022 | FALSE | FALSE | 5 | SingleCoord | 387 | ClosePulseOn | 0.25
FWB_AL25_52-25_81U5 |  | AJUSTE PARA 81 E5 | 4f58199c-8c4a-447f-b960-496c18f59d27 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_81U5 |  | FWB_DS_00709 | 20260416 | Status | 30 | DirectOperate | SingleBit | 2024 | FALSE | FALSE | 5 | SingleCoord | 389 | ClosePulseOn | 0.25
FWB_AL25_52-25_81U4 |  | AJUSTE PARA 81 E4 | f8bbf73c-44d2-43b2-80af-1a5ad0e91075 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_81U4 |  | FWB_DS_00708 | 20260416 | Status | 30 | DirectOperate | SingleBit | 2023 | FALSE | FALSE | 5 | SingleCoord | 388 | ClosePulseOn | 0.25
FWB_AL25_52-25_81 |  | 81 - FUNCAO SUB/SOB FREQUENCIA | fe1cd4cd-6c8e-4bd7-ad63-c5c7170398b8 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL25_52-25_81 |  | FWB_DS_00710 | 20260416 | Status | 30 | DirectOperate | SingleBit | 2025 | FALSE | FALSE | 5 | SingleCoord | 390;390 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL25_52-25_81U2 |  | AJUSTE PARA 81 E2 | 854ee087-f2c5-463d-aa74-632f314a4f04 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_81U2 |  | FWB_DS_00706 | 20260416 | Status | 30 | DirectOperate | SingleBit | 2021 | FALSE | FALSE | 5 | SingleCoord | 386 | ClosePulseOn | 0.25
FWB_AL25_52-25_DJF1 |  | DISJUNTOR NF | 0e8ec1dd-774b-4889-aa6b-e693d5cc941d | SwitchStatus | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_FWB_1 | FWB_AL25_52-25_DJF1 |  | FWB_DS_00727 | 20260416 | Status | 30 | DirectOperate | MultiCoord | 2003;2004 | FALSE | FALSE | 15 | SingleCoord | 381;381 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL15_52-15_AJG2 |  | AJUSTE PARA GRUPO 2 | 8ffa886b-6559-4509-952a-838a3591670a | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 2 |  | UTR_FWB_1 | FWB_AL15_52-15_AJG2 |  | FWB_DS_00729 | 20260416 | Status | 30 | DirectOperate | SingleBit | 402 | FALSE | FALSE | 15 | MultiCoord | 91;92 | ClosePulseOn;ClosePulseOn | 0.25;0.25
FWB_AL25_52-25_2649 |  | 26 49 - FUNCAO TEMPERATURA | 4a37b9eb-0914-4b4c-bc82-0d59fd124a07 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_2649 |  | FWB_DS_00703 | 20260416 | Status | 30 | DirectOperate | SingleBit | 2018 | FALSE | FALSE | 15 | SingleCoord | 384;384 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_AL24_52-24_81U5 |  | AJUSTE PARA 81 E5 | 149f26eb-e108-4bad-a18f-3880effb94e8 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_81U5 |  | FWB_DS_00670 | 20260416 | Status | 30 | DirectOperate | SingleBit | 1924 | FALSE | FALSE | 5 | SingleCoord | 369 | ClosePulseOn | 0.25
FWB_AL25_52-25_79 |  | 79 - FUNCAO RELIGAMENTO | 022bb267-5a88-43ce-bdee-e9ce9bb2e405 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL25_52-25_79 |  | FWB_DS_00702 | 20260416 | Status | 30 | DirectOperate | SingleBit | 2017 | FALSE | FALSE | 15 | SingleCoord | 382;382 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_AL15_52-15_81 |  | 81 - FUNCAO SUB/SOB FREQUENCIA | 45adf9a6-7f17-4585-a240-b9105963b02d | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL15_52-15_81 |  | FWB_DS_00749 | 20260416 | Status | 30 | DirectOperate | SingleBit | 425 | FALSE | FALSE | 5 | SingleCoord | 90;90 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL13_52-13_79 |  | 79 - FUNCAO RELIGAMENTO | a8a25e73-60c9-440c-870d-7671dbfc398c | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL13_52-13_79 |  | FWB_DS_00419 | 20260416 | Status | 30 | DirectOperate | SingleBit | 217 | FALSE | FALSE | 15 | SingleCoord | 42;42 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_AL13_52-13_81U3 |  | AJUSTE PARA 81 E3 | 6392eea3-1989-4a97-a0e1-5e5f055b4df6 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_81U3 |  | FWB_DS_00424 | 20260416 | Status | 30 | DirectOperate | SingleBit | 222 | FALSE | FALSE | 5 | SingleCoord | 47 | ClosePulseOn | 0.25
FWB_AL13_52-13_DJF1 |  | DISJUNTOR NF | 169539fb-c895-4163-9d59-b471b8b1fea3 | SwitchStatus | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_FWB_1 | FWB_AL13_52-13_DJF1 |  | FWB_DS_00444 | 20260416 | Status | 30 | DirectOperate | MultiCoord | 203;204 | FALSE | FALSE | 15 | SingleCoord | 41;41 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL14_52-14_2649 |  | 26 49 - FUNCAO TEMPERATURA | a7871850-efbf-4e36-8cb1-599b431955bf | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_2649 |  | FWB_DS_00459 | 20260416 | Status | 30 | DirectOperate | SingleBit | 318 | FALSE | FALSE | 15 | SingleCoord | 64;64 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_AL14_52-14_DJF1 |  | DISJUNTOR NF | 187ee881-61d6-4c49-87f4-f5f209305ce2 | SwitchStatus | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_FWB_1 | FWB_AL14_52-14_DJF1 |  | FWB_DS_00483 | 20260416 | Status | 30 | DirectOperate | MultiCoord | 303;304 | FALSE | FALSE | 15 | SingleCoord | 61;61 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL21_52-21_51N |  | 51N | 7e27273d-80e4-4adc-9b57-4afb9b744663 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_AL21_52-21_51N |  | FWB_DS_00532 | 20260416 | Status | 30 | DirectOperate | SingleBit | 519 | FALSE | FALSE | 15 | SingleCoord | 103;103 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL21_52-21_81U2 |  | AJUSTE PARA 81 E2 | 70084d7e-ea64-45c5-ad73-be0707409794 | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_81U2 |  | FWB_DS_00534 | 20260416 | Status | 30 | DirectOperate | SingleBit | 521 | FALSE | FALSE | 5 | SingleCoord | 106 | ClosePulseOn | 0.25
FWB_AL14_52-14_81U1 |  | AJUSTE PARA 81 E1 | a2f607d0-55cf-41ba-b26c-dd5606dce737 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_81U1 |  | FWB_DS_00461 | 20260416 | Status | 30 | DirectOperate | SingleBit | 320 | FALSE | FALSE | 5 | SingleCoord | 65 | ClosePulseOn | 0.25
FWB_AL13_52-13_81U1 |  | AJUSTE PARA 81 E1 | 8178b8d8-a607-4390-9a2d-a704e81ba6c2 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_81U1 |  | FWB_DS_00422 | 20260416 | Status | 30 | DirectOperate | SingleBit | 220 | FALSE | FALSE | 5 | SingleCoord | 45 | ClosePulseOn | 0.25
FWB_AL14_52-14_AJG2 |  | AJUSTE PARA GRUPO 2 | 9b0935a5-7b42-484c-a5e6-bee452b2a56d | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 2 |  | UTR_FWB_1 | FWB_AL14_52-14_AJG2 |  | FWB_DS_00446 | 20260416 | Status | 30 | DirectOperate | SingleBit | 302 | FALSE | FALSE | 15 | MultiCoord | 71;72 | ClosePulseOn;ClosePulseOn | 0.25;0.25
FWB_AL22_52-22_2649 |  | 26 49 - FUNCAO TEMPERATURA | 1d2c471c-5e1a-435e-8361-5d242ad02366 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_2649 |  | FWB_DS_00570 | 20260416 | Status | 30 | DirectOperate | SingleBit | 618 | FALSE | FALSE | 15 | SingleCoord | 124;124 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_AL12_52-12_DR |  | DEFEITO RELE | f2635b05-8a54-4012-845b-2d1a4506f599 | Status | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL12_52-12_DR |  | aea2daa5-3efa-459a-acfa-d5bc712a3109 | 20260416 | Status |  |  | SingleBit | 2328 | FALSE
FWB_AL13_52-13_DR |  | DEFEITO RELE | 5e68befc-76b0-4461-8930-79f1be2ce090 | Status | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL13_52-13_DR |  | b20491a3-77b8-4801-a95b-a2e6fd1bd808 | 20260416 | Status |  |  | SingleBit | 2329 | FALSE
FWB_TRF1_24-1_43TC |  | 43 - CHAVE TELECOMANDO | de91ee65-2548-44ca-a621-098ad5dd9f7d | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_43TC |  | FWB_DS_00767 | 20260416 | Status |  |  | SingleBit | 800 | FALSE
FWB_AL14_52-14_DR |  | DEFEITO RELE | da9f2fd0-9abd-4010-ba45-2d98bcbe7293 | Status | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL14_52-14_DR |  | 4988bc3d-e155-4749-bd5f-636641ae8a6a | 20260416 | Status |  |  | SingleBit | 2331 | FALSE
FWB_TRF1_24-1_CAFL |  | FALTA VCA | 736172f6-d983-42b8-9097-ea4ee0da8077 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_TRF1_24-1_CAFL |  | FWB_DS_00772 | 20260416 | Status |  |  | SingleBit | 808 | FALSE
FWB_TRF1_24-1_BC_TEXT |  | TRIP EXTERNO BANCO DE CAPACITORES | e172ad8a-be3b-4a57-91fb-4f492a646890 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_BC_TEXT |  | FWB_DS_00793 | 20260416 | Status |  |  | SingleBit | 829 | FALSE
FWB_TRF1_24-1_CCFL |  | FALTA VCC | 1a81bd9b-81a4-48d0-9671-04a6c6d7a527 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_TRF1_24-1_CCFL |  | FWB_DS_00779 | 20260416 | Status |  |  | SingleBit | 815 | FALSE
FWB_TRF1_24-1_50F |  | 50 - SOBRECORRENTE INSTANTANEA FASE | 6275487a-10c2-4de3-b74e-89b786446f56 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_PROT_50F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_50F |  | FWB_DS_00801 | 20260416 | Status |  |  | SingleBit | 837 | FALSE
FWB_TRF1_24-1_CCMO |  | FALTA VCC MOTOR | c5a6f818-b874-4dba-a5c3-95704968bff9 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_CCMO |  | FWB_DS_00770 | 20260416 | Status |  |  | SingleBit | 806 | FALSE
FWB_TRF1_24-1_51F |  | 51 - SOBRECORRENTE TEMPORIZADA FASE | 05c05ba3-e89e-437a-bedb-e474cdc04653 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_51F |  | FWB_DS_00802 | 20260416 | Status |  |  | SingleBit | 838 | FALSE
FWB_AL25_52-25_DR |  | DEFEITO RELE | fa24dda0-2296-491d-bf14-c8738893ad57 | Status | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL25_52-25_DR |  | 83d2a6b8-f1f6-4f82-8537-54a8590b3d2f | 20260416 | Status |  |  | SingleBit | 2340 | FALSE
FWB_TRF1_24-1_50N |  | 50 - SOBRECORRENTE INSTANTANEA NEUTRO | 5cbd3f27-93c5-49e6-9bcc-4fcc48355318 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_PROT_50N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_50N |  | FWB_DS_00803 | 20260416 | Status |  |  | SingleBit | 839 | FALSE
FWB_TRF1_24-1_51N1 |  | 51 - SOBRECORRENTE TEMPORIZADA NEUTRO | 0739edce-16b2-4444-b5cb-df3cf94de2b4 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_51N1 |  | FWB_DS_00804 | 20260416 | Status |  |  | SingleBit | 840 | FALSE
FWB_TRF1_24-1_BBAB |  | BOBINA ABERTURA | c43ec766-b67b-4b2a-bf0f-72e19fed0d7a | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_BBAB |  | FWB_DS_00778 | 20260416 | Status |  |  | SingleBit | 814 | FALSE
FWB_TRF1_24-1_62BF |  | 62 - FALHA DISJUNTOR BLOQUEIO | 5d474822-072e-42a3-801d-e4cc19b38fdc | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_62BF |  | FWB_DS_00800 | 20260416 | Status |  |  | SingleBit | 836 | FALSE
FWB_TRF1_24-1_27_T |  | 27 - SUBTENSAO | 114dc026-85a1-4f63-9ba7-12f2c691ae13 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_PROT_27_T |  | Enabled | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_27_T |  | FWB_DS_00806 | 20260416 | Status |  |  | SingleBit | 842 | FALSE
FWB_TRF1_24-1_59 |  | 59 - SOBRETENSAO | d2b2f7c9-be9b-491d-a303-a7adf705d806 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_PROT_59 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_59 |  | FWB_DS_00807 | 20260416 | Status |  |  | SingleBit | 843 | FALSE
FWB_TRF1_24-1_79OK |  | 79 - RELIGAMENTO COM SUCESSO | 3ace09a5-53cc-47eb-a786-6e032e682758 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_79OK |  | FWB_DS_00810 | 20260416 | Status |  |  | SingleBit | 846 | FALSE
FWB_TRF1_24-1_79_1 |  | 79 - PARTIDA RELIGAMENTO | e6842e15-3481-4200-a13d-ab4aaaf16860 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_79_1 |  | FWB_DS_00809 | 20260416 | Status |  |  | SingleBit | 845 | FALSE
FWB_TRF1_24-1_FSIH |  | FALHA SINCRONISMO HORA | ca4778cf-2fe1-4f86-ada8-eba3e698bea2 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_FSIH |  | FWB_DS_00812 | 20260416 | Status |  |  | SingleBit | 849 | FALSE
FWB_TRF1_24-1_81SU |  | 81 - TRIP SUB FREQUENCIA | 742a2d2c-04f9-46b1-b771-e535522fa079 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_PROT_81SU |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_81SU |  | FWB_DS_00808 | 20260416 | Status |  |  | SingleBit | 844 | FALSE
FWB_TRF1_24-1_FLK1 |  | FALHA LINK 1 | cf896de5-41c9-4749-924d-948fce2ac502 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_FLK1 |  | FWB_DS_00813 | 20260416 | Status |  |  | SingleBit | 850 | FALSE
FWB_TRF1_24-1_FLK2 |  | FALHA LINK 2 | da811018-e368-4fce-97b5-4228d3b71f07 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_FLK2 |  | FWB_DS_00814 | 20260416 | Status |  |  | SingleBit | 851 | FALSE
FWB_TRF1_24-1_FCOM |  | FALHA COMUNICACAO | 590edfea-6580-49ce-8d6e-b9eca960a6cf | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_FCOM |  | FWB_DS_00815 | 20260416 | Status |  |  | SingleBit | 852 | FALSE
FWB_TRF1_24-1_DR |  | DEFEITO RELE | b2ac568c-c3e1-43d2-9ae4-580a62b0c633 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_DR |  | 34d7bd31-e8a9-4225-a247-5ba69f466f33 | 20260416 | Status |  |  | SingleBit | 2330 | FALSE
FWB_TRF1_24-1_TOED |  | 26 49 - TRIP TEMPERATURA | 4a7168f4-c6e3-450e-b377-e287278e779c | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_TOED |  | FWB_DS_00816 | 20260416 | Status |  |  | SingleBit | 853 | FALSE
FWB_TRF2_24-2_43TC |  | 43 - CHAVE TELECOMANDO | cdfae083-4f06-4aee-b49c-cd94db54630a | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_43TC |  | FWB_DS_00818 | 20260416 | Status |  |  | SingleBit | 900 | FALSE
FWB_TRF2_24-2_SF6A |  | ALARME BAIXA PRESSAO SF6 | 3ce4bede-9bc3-45a8-8f40-b7887318f206 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_SF6A |  | FWB_DS_00819 | 20260416 | Status |  |  | SingleBit | 904 | FALSE
FWB_TRF1_24-1_79LO |  | 79 - RELIGAMENTO BLOQUEADO | b6b26740-d1e8-4b89-9dce-c2751add4c3e | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_79LO |  | FWB_DS_00811 | 20260416 | Status |  |  | SingleBit | 847 | FALSE
FWB_TRF1_24-1_MOLA |  | MOLA | 4f797960-2153-4ba3-b9ea-cb7e28dfaae5 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_MOLA |  | FWB_DS_00771 | 20260416 | Status |  |  | SingleBit | 807 | FALSE
FWB_TRF1_24-1_SF6B |  | BLOQUEIO BAIXA PRESSAO SF6 | e454fa5c-039f-4fe3-85fd-6b8d02dccc42 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_SF6B |  | FWB_DS_00769 | 20260416 | Status |  |  | SingleBit | 805 | FALSE
FWB_TRF1_24-1_CCAB |  | FALTA VCC CIRCUITO ABERTURA | 35e16fdf-26da-4e97-9e9d-a23227555f9b | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_CCAB |  | FWB_DS_00774 | 20260416 | Status |  |  | SingleBit | 810 | FALSE
FWB_TRF2_24-2_MOLA |  | MOLA | b22f3489-7b41-445f-be97-3d99b2554700 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_MOLA |  | FWB_DS_00822 | 20260416 | Status |  |  | SingleBit | 907 | FALSE
FWB_TRF2_24-2_43LR |  | 43 - CHAVE LOCAL REMOTO | 75edcecd-08a1-4b4c-9574-24e23e860ce5 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_43LR |  | FWB_DS_00826 | 20260416 | Status |  |  | SingleBit | 911 | FALSE
FWB_TRF2_24-2_CCAB |  | FALTA VCC CIRCUITO ABERTURA | 2ab16a5b-4b1c-4bf2-b6ac-aa814d75cc1c | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_CCAB |  | FWB_DS_00825 | 20260416 | Status |  |  | SingleBit | 910 | FALSE
FWB_TRF2_24-2_BBFC |  | BOBINA FECHAMENTO | e7178c52-641d-47c4-88a1-732791116d92 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_BBFC |  | FWB_DS_00827 | 20260416 | Status |  |  | SingleBit | 912 | FALSE
FWB_AL24_52-24_DR |  | DEFEITO RELE | a7f7d5aa-48d1-42e5-8d06-b8dc7b891306 | Status | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL24_52-24_DR |  | f336eacc-808c-4bf3-9575-5ceb3657327d | 20260416 | Status |  |  | SingleBit | 2339 | FALSE
FWB_TRF2_24-2_CCFL |  | FALTA VCC | 8dd63b78-2415-47b2-9a85-cd679cfaac0f | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_TRF2_24-2_CCFL |  | FWB_DS_00830 | 20260416 | Status |  |  | SingleBit | 915 | FALSE
FWB_TRF2_24-2_BC_TEXT |  | TRIP EXTERNO BANCO DE CAPACITORES | e6e0c333-1473-41c4-a618-6d532a832438 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_BC_TEXT |  | FWB_DS_00844 | 20260416 | Status |  |  | SingleBit | 929 | FALSE
FWB_TRF2_24-2_BBAB |  | BOBINA ABERTURA | 7f95d400-5623-4a12-b906-d188281aed7d | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_BBAB |  | FWB_DS_00829 | 20260416 | Status |  |  | SingleBit | 914 | FALSE
FWB_AL21_52-21_DR |  | DEFEITO RELE | 33f39bad-528d-4dae-bb20-9c5e00d7f61c | Status | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL21_52-21_DR |  | 96ec823c-aca2-4d83-9c5b-5afea653cd7d | 20260416 | Status |  |  | SingleBit | 2335 | FALSE
FWB_TRF2_24-2_G4_TEXT |  | TRIP EXTERNO G4 | ce0a70ee-b1b5-4f0e-b9f9-a9ee3400ed10 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_G4_TEXT |  | FWB_DS_00846 | 20260416 | Status |  |  | SingleBit | 931 | FALSE
FWB_TRF1_24-1_TEXT |  | TRIP EXTERNO | 27ca6e26-39a2-4119-b4ac-f6777e408b95 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_TEXT |  | FWB_DS_00777 | 20260416 | Status |  |  | SingleBit | 813 | FALSE
FWB_TRF2_24-2_CAFL |  | FALTA VCA | a0658430-f2c1-4704-ad9e-fda8e1917514 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_TRF2_24-2_CAFL |  | FWB_DS_00823 | 20260416 | Status |  |  | SingleBit | 908 | FALSE
FWB_TRF2_24-2_INTR |  | 20 63 87 - PROTECOES INTRINSECAS | b1ed8211-378d-418d-bd30-c60c76e6f5e4 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_INTR |  | FWB_DS_00847 | 20260416 | Status |  |  | SingleBit | 932 | FALSE
FWB_TRF2_24-2_62BF |  | 62 - FALHA DISJUNTOR BLOQUEIO | 0730456b-98c2-4443-a043-c7990215d89d | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_62BF |  | FWB_DS_00851 | 20260416 | Status |  |  | SingleBit | 936 | FALSE
FWB_TRF2_24-2_50F |  | 50 - SOBRECORRENTE INSTANTANEA FASE | fcf72558-093b-4daf-a47d-3f79f8d66efc | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_PROT_50F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_50F |  | FWB_DS_00852 | 20260416 | Status |  |  | SingleBit | 937 | FALSE
FWB_TRF1_24-1_B5M |  | BLOQUEIO 5 MINUTOS | 135a6cfd-8bda-46d7-9bee-9f8d05b24347 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_B5M |  | FWB_DS_00797 | 20260416 | Status |  |  | SingleBit | 833 | FALSE
FWB_TRF2_24-2_50N |  | 50 - SOBRECORRENTE INSTANTANEA NEUTRO | 5e7f582a-b066-4fb5-8463-2cdfa2115c54 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_PROT_50N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_50N |  | FWB_DS_00854 | 20260416 | Status |  |  | SingleBit | 939 | FALSE
FWB_TRF2_24-2_27_T |  | 27 - SUBTENSAO | fb11c490-70cd-46b9-83ac-59380af31264 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_PROT_27_T |  | Enabled | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_27_T |  | FWB_DS_00857 | 20260416 | Status |  |  | SingleBit | 942 | FALSE
FWB_TRF2_24-2_SGFT |  | TRIP SGF | a1b876f5-fdf4-49e3-9ba3-d5aba807ece8 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_PROT_SGFT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_SGFT |  | FWB_DS_00856 | 20260416 | Status |  |  | SingleBit | 941 | FALSE
FWB_TRF2_24-2_51N1 |  | 51 - SOBRECORRENTE TEMPORIZADA NEUTRO | 3055fcad-fabe-405c-9c3e-bf4a35319782 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_51N1 |  | FWB_DS_00855 | 20260416 | Status |  |  | SingleBit | 940 | FALSE
FWB_TRF2_24-2_B5M |  | BLOQUEIO 5 MINUTOS | cd5447fe-8a56-451f-8746-1d2a0d7e31d8 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_B5M |  | FWB_DS_00848 | 20260416 | Status |  |  | SingleBit | 933 | FALSE
FWB_TRF2_24-2_79OK |  | 79 - RELIGAMENTO COM SUCESSO | 3519c65a-d699-4733-83ef-744e52992e81 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_79OK |  | FWB_DS_00861 | 20260416 | Status |  |  | SingleBit | 946 | FALSE
FWB_TRF2_24-2_79LO |  | 79 - RELIGAMENTO BLOQUEADO | 823f9f59-5a0c-439e-8038-3b9503ba154a | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_79LO |  | FWB_DS_00862 | 20260416 | Status |  |  | SingleBit | 947 | FALSE
FWB_TRF2_24-2_59 |  | 59 - SOBRETENSAO | 2c8a107e-9b1a-4c5d-89f9-b0d1df0301fb | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_PROT_59 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_59 |  | FWB_DS_00858 | 20260416 | Status |  |  | SingleBit | 943 | FALSE
FWB_TRF2_24-2_FSIH |  | FALHA SINCRONISMO HORA | 2a795f6d-11d8-49f0-88ea-0e60e2178964 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_FSIH |  | FWB_DS_00863 | 20260416 | Status |  |  | SingleBit | 949 | FALSE
FWB_TRF2_24-2_CCMO |  | FALTA VCC MOTOR | 871e116c-4d73-4fa0-ae97-d3ddf71f5c08 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_CCMO |  | FWB_DS_00821 | 20260416 | Status |  |  | SingleBit | 906 | FALSE
FWB_TRF2_24-2_FLK2 |  | FALHA LINK 2 | 883777dd-3602-4d86-bce6-6d094f9f3601 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_FLK2 |  | FWB_DS_00865 | 20260416 | Status |  |  | SingleBit | 951 | FALSE
FWB_TRF2_24-2_FLK1 |  | FALHA LINK 1 | f12d22f0-5eba-4a05-a56a-ddaf4ffa8032 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_FLK1 |  | FWB_DS_00864 | 20260416 | Status |  |  | SingleBit | 950 | FALSE
FWB_TRF2_24-2_TOED |  | 26 49 - TRIP TEMPERATURA | 2da5830b-695b-457b-b61e-da6cc8778ec0 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_TOED |  | FWB_DS_00867 | 20260416 | Status |  |  | SingleBit | 953 | FALSE
FWB_TRF2_24-2_FCOM |  | FALHA COMUNICACAO | 3479e8f7-afd9-4094-b8d1-4c9260b298e1 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_FCOM |  | FWB_DS_00866 | 20260416 | Status |  |  | SingleBit | 952 | FALSE
FWB_TRF2_24-2_81SU |  | 81 - TRIP SUB FREQUENCIA | c5d57bfc-9606-4abd-9823-511b8b2e9f8a | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_PROT_81SU |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_81SU |  | FWB_DS_00859 | 20260416 | Status |  |  | SingleBit | 944 | FALSE
FWB_TRF2_24-2_TEXT |  | TRIP EXTERNO | bd61692e-c594-430f-9c10-bd39da565a6a | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_TEXT |  | FWB_DS_00828 | 20260416 | Status |  |  | SingleBit | 913 | FALSE
FWB_TRF2_24-2_CCCO |  | FALTA VCC COMANDO | 3bd9e701-eefd-4452-bb66-3c85d11485d6 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_CCCO |  | FWB_DS_00824 | 20260416 | Status |  |  | SingleBit | 909 | FALSE
FWB_TRF2_24-2_TR_TEXT |  | TRIP EXTERNO TRANSFORMADOR | 693639a1-7411-47c9-b7c5-7dc5c8b533d4 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_TR_TEXT |  | FWB_DS_00845 | 20260416 | Status |  |  | SingleBit | 930 | FALSE
FWB_TRF2_24-2_51F |  | 51 - SOBRECORRENTE TEMPORIZADA FASE | f51be66c-e04e-4572-a243-084d0b22dc9a | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_51F |  | FWB_DS_00853 | 20260416 | Status |  |  | SingleBit | 938 | FALSE
FWB_TRF1_24-1_TR_TEXT |  | TRIP EXTERNO TRANSFORMADOR | a8470a2d-878f-4213-a70a-dbfe4f117154 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_TR_TEXT |  | FWB_DS_00794 | 20260416 | Status |  |  | SingleBit | 830 | FALSE
FWB_TRF1_24-1_BBFC |  | BOBINA FECHAMENTO | 3f401e55-ade2-4ca7-a86d-fcd514271038 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_BBFC |  | FWB_DS_00776 | 20260416 | Status |  |  | SingleBit | 812 | FALSE
FWB_TRF1_24-1_CCCO |  | FALTA VCC COMANDO | 4d1c7926-88bf-4e16-b747-1c8ec8b900fc | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_CCCO |  | FWB_DS_00773 | 20260416 | Status |  |  | SingleBit | 809 | FALSE
FWB_TRF1_24-1_SGFT |  | TRIP SGF | d8210b52-d104-4413-9f22-5366f903c481 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_PROT_SGFT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_SGFT |  | FWB_DS_00805 | 20260416 | Status |  |  | SingleBit | 841 | FALSE
FWB_TRF1_24-1_SF6A |  | ALARME BAIXA PRESSAO SF6 | dfc083de-90db-43fa-9fd2-e57b25523b6c | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_SF6A |  | FWB_DS_00768 | 20260416 | Status |  |  | SingleBit | 804 | FALSE
FWB_TRF1_24-1_G4_TEXT |  | TRIP EXTERNO G4 | 3ec95d9e-ca6e-4027-86a9-db028e5eaaa5 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_G4_TEXT |  | FWB_DS_00795 | 20260416 | Status |  |  | SingleBit | 831 | FALSE
FWB_TRF2_24-2_SF6B |  | BLOQUEIO BAIXA PRESSAO SF6 | cd0ffa0e-ec3c-4d10-88e7-6b4583e9dc13 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_SF6B |  | FWB_DS_00820 | 20260416 | Status |  |  | SingleBit | 905 | FALSE
FWB_TRF1_24-1_43LR |  | 43 - CHAVE LOCAL REMOTO | 86c3883b-4eb7-4383-b6f3-a35ae92239dc | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_43LR |  | FWB_DS_00775 | 20260416 | Status |  |  | SingleBit | 811 | FALSE
FWB_TRF1_24-1_INTR |  | 20 63 87 - PROTECOES INTRINSECAS | e1fcc643-25db-46ee-94cb-d0227363227a | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_INTR |  | FWB_DS_00796 | 20260416 | Status |  |  | SingleBit | 832 | FALSE
FWB_TRF2_24-2_79_1 |  | 79 - PARTIDA RELIGAMENTO | afbf920d-efb8-4293-bae6-f2395a1c366c | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_79_1 |  | FWB_DS_00860 | 20260416 | Status |  |  | SingleBit | 945 | FALSE
FWB_AL15_52-15_DR |  | DEFEITO RELE | 4397c270-293d-45a4-ab9e-31f5bdfc7b48 | Status | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL15_52-15_DR |  | 08a48443-f5d6-4f84-a16a-cb09809cbde3 | 20260416 | Status |  |  | SingleBit | 2332 | FALSE
FWB_AL22_52-22_DR |  | DEFEITO RELE | 77d093ca-4ee4-478b-ba1b-7c4417c63420 | Status | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_AL22_52-22_DR |  | 87ec53d5-57f2-430a-8bb7-0ab1486d6429 | 20260416 | Status |  |  | SingleBit | 2336 | FALSE
FWB_TRF1_24-1_79 |  | 79 - FUNCAO RELIGAMENTO | c47f7e94-cc21-4f96-961b-d40283df4f5b | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_TRF1_24-1_79 |  | FWB_DS_00780 | 20260416 | Status | 30 | DirectOperate | SingleBit | 816 | FALSE | FALSE | 5 | SingleCoord | 162;162 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_TRF1_24-1_51N |  | 51N | e5ec1b44-ce9a-4651-9093-ed3661b4284a | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_TRF1_24-1_51N |  | FWB_DS_00782 | 20260416 | Status | 30 | DirectOperate | SingleBit | 818 | FALSE | FALSE | 5 | SingleCoord | 163;163 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TRF1_24-1_81U1 |  | AJUSTE PARA 81 E1 | 9220f772-09dd-4379-80f8-1612e2523911 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_81U1 |  | FWB_DS_00783 | 20260416 | Status | 30 | DirectOperate | SingleBit | 819 | FALSE | FALSE | 5 | SingleCoord | 165 | ClosePulseOn | 0.25
FWB_TRF1_24-1_AJG2 |  | AJUSTE PARA GRUPO 2 | a59f5e44-2941-48e7-bf7c-cd6073dae31f | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_TRF1_24-1_AJG2 |  | FWB_DS_00790 | 20260416 | Status | 30 | DirectOperate | SingleBit | 826 | FALSE | FALSE | 5 | SingleCoord | 168 | ClosePulseOn | 0.25
FWB_TRF1_24-1_81U3 |  | AJUSTE PARA 81 E3 | 25ca3bbf-3ea1-44ba-90b8-e7cd433f2330 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_81U3 |  | FWB_DS_00785 | 20260416 | Status | 30 | DirectOperate | SingleBit | 821 | FALSE | FALSE | 5 | SingleCoord | 169 | ClosePulseOn | 0.25
FWB_TRF2_24-2_81U5 |  | AJUSTE PARA 81 E5 | 47f3acc9-0c0c-4e71-b53f-f5c5219e77e6 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_81U5 |  | FWB_DS_00838 | 20260416 | Status | 30 | DirectOperate | SingleBit | 923 | FALSE | FALSE | 5 | SingleCoord | 193 | ClosePulseOn | 0.25
FWB_TRF2_24-2_79 |  | 79 - FUNCAO RELIGAMENTO | 71b3552f-7076-4afa-8e2d-368f8f707096 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_TRF2_24-2_79 |  | FWB_DS_00831 | 20260416 | Status | 30 | DirectOperate | SingleBit | 916 | FALSE | FALSE | 5 | SingleCoord | 182;182 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_TRF2_24-2_81U1 |  | AJUSTE PARA 81 E1 | 406e4d10-6613-4238-8464-dfd63e0b33d1 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_81U1 |  | FWB_DS_00834 | 20260416 | Status | 30 | DirectOperate | SingleBit | 919 | FALSE | FALSE | 5 | SingleCoord | 185 | ClosePulseOn | 0.25
FWB_TRF2_24-2_81U2 |  | AJUSTE PARA 81 E2 | cdf240eb-e47b-4913-b2cf-521675c70bbc | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_81U2 |  | FWB_DS_00835 | 20260416 | Status | 30 | DirectOperate | SingleBit | 920 | FALSE | FALSE | 5 | SingleCoord | 187 | ClosePulseOn | 0.25
FWB_TRF2_24-2_AJG1 |  | AJUSTE PARA GRUPO 1 | 20770458-62d3-4e94-8767-8014d37d76d8 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_TRF2_24-2_AJG1 |  | FWB_DS_00840 | 20260416 | Status | 30 | DirectOperate | SingleBit | 925 | FALSE | FALSE | 5 | SingleCoord | 186 | ClosePulseOn | 0.25
FWB_TRF2_24-2_AJG3 |  | AJUSTE PARA GRUPO 3 | 67540240-b1a1-43e3-8c79-7138a6666344 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_TRF2_24-2_AJG3 |  | FWB_DS_00842 | 20260416 | Status | 30 | DirectOperate | SingleBit | 927 | FALSE | FALSE | 5 | SingleCoord | 190 | ClosePulseOn | 0.25
FWB_TRF1_24-1_81 |  | 81 - FUNCAO SUB/SOB FREQUENCIA | 5ecac07c-7a09-4b76-a4f5-c4bdbbaaf8a4 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_TRF1_24-1_81 |  | FWB_DS_00788 | 20260416 | Status | 30 | DirectOperate | SingleBit | 824 | FALSE | FALSE | 5 | SingleCoord | 174;174 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TRF1_24-1_AJG4 |  | AJUSTE PARA GRUPO 4 | 335e89a0-7375-4c87-87e2-928380ff3967 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_TRF1_24-1_AJG4 |  | FWB_DS_00792 | 20260416 | Status | 30 | DirectOperate | SingleBit | 828 | FALSE | FALSE | 5 | SingleCoord | 172 | ClosePulseOn | 0.25
FWB_TRF2_24-2_TR_86 |  | 86T - BLOQUEIO | 55440d68-6d52-48d8-8458-7c72096c1289 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | ReadWrite |  | REARMAR@null___NORMAL@ATUADO___Custom_S_TC_SA | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_TR_86 |  | FWB_DS_00849 | 20260416 | Status | 30 | DirectOperate | SingleBit | 934 | FALSE | FALSE | 5 | SingleCoord | 195 | ClosePulseOn | 0.25
FWB_TRF2_24-2_BC_86 |  | 86BC - BLOQUEIO | eeb3a02f-cb0e-48f8-97ec-c37a7e72f7bd | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | ReadWrite |  | REARMAR@null___NORMAL@ATUADO___Custom_S_TC_SA | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_BC_86 |  | FWB_DS_00850 | 20260416 | Status | 30 | DirectOperate | SingleBit | 935 | FALSE | FALSE | 5 | SingleCoord | 196 | ClosePulseOn | 0.25
FWB_TRF1_24-1_81U5 |  | AJUSTE PARA 81 E5 | 454bce1d-3630-4347-88cb-f3a47390a3e5 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_81U5 |  | FWB_DS_00787 | 20260416 | Status | 30 | DirectOperate | SingleBit | 823 | FALSE | FALSE | 5 | SingleCoord | 173 | ClosePulseOn | 0.25
FWB_TRF2_24-2_AJG4 |  | AJUSTE PARA GRUPO 4 | 6abc4f2d-928c-41ca-a3dd-a328a8ef151b | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_TRF2_24-2_AJG4 |  | FWB_DS_00843 | 20260416 | Status | 30 | DirectOperate | SingleBit | 928 | FALSE | FALSE | 5 | SingleCoord | 192 | ClosePulseOn | 0.25
FWB_TRF1_24-1_AJG3 |  | AJUSTE PARA GRUPO 3 | 6f43f5b6-9c7c-4b0a-b30e-73f9da2a5668 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_TRF1_24-1_AJG3 |  | FWB_DS_00791 | 20260416 | Status | 30 | DirectOperate | SingleBit | 827 | FALSE | FALSE | 5 | SingleCoord | 170 | ClosePulseOn | 0.25
FWB_TRF2_24-2_AJG2 |  | AJUSTE PARA GRUPO 2 | 9c997adf-8d77-49e5-b43d-97e6724db813 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_TRF2_24-2_AJG2 |  | FWB_DS_00841 | 20260416 | Status | 30 | DirectOperate | SingleBit | 926 | FALSE | FALSE | 5 | SingleCoord | 188 | ClosePulseOn | 0.25
FWB_TRF2_24-2_DJF1 |  | DISJUNTOR NF | 446867b2-6c69-40f3-86be-17029050698b | SwitchStatus | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_FWB_1 | FWB_TRF2_24-2_DJF1 |  | FWB_DS_00868 | 20260416 | Status | 30 | DirectOperate | MultiCoord | 901;902 | FALSE | FALSE | 15 | SingleCoord | 181;181 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TRF2_24-2_81 |  | 81 - FUNCAO SUB/SOB FREQUENCIA | e1b6db0d-7852-49fc-a96e-3e10830b494a | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_TRF2_24-2_81 |  | FWB_DS_00839 | 20260416 | Status | 30 | DirectOperate | SingleBit | 924 | FALSE | FALSE | 5 | SingleCoord | 194;194 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TRF2_24-2_81U3 |  | AJUSTE PARA 81 E3 | 99dd25b0-cc61-4d37-a2fe-0b0d63364d96 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_81U3 |  | FWB_DS_00836 | 20260416 | Status | 30 | DirectOperate | SingleBit | 921 | FALSE | FALSE | 5 | SingleCoord | 189 | ClosePulseOn | 0.25
FWB_TRF1_24-1_AJG1 |  | AJUSTE PARA GRUPO 1 | 6008c686-a8f0-461f-8d35-12b51b524543 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_TRF1_24-1_AJG1 |  | FWB_DS_00789 | 20260416 | Status | 30 | DirectOperate | SingleBit | 825 | FALSE | FALSE | 5 | SingleCoord | 166 | ClosePulseOn | 0.25
FWB_TRF1_24-1_2649 |  | 26 49 - FUNCAO TEMPERATURA | 263758cb-9102-4831-b603-eb0340913539 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_2649 |  | FWB_DS_00781 | 20260416 | Status | 30 | DirectOperate | SingleBit | 817 | FALSE | FALSE | 5 | SingleCoord | 164;164 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_TRF1_24-1_TR_86 |  | 86T - BLOQUEIO | 76264981-09e8-489d-b675-da6ab7304a45 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | ReadWrite |  | REARMAR@null___NORMAL@ATUADO___Custom_S_TC_SA | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_TR_86 |  | FWB_DS_00798 | 20260416 | Status | 30 | DirectOperate | SingleBit | 834 | FALSE | FALSE | 5 | SingleCoord | 175 | ClosePulseOn | 0.25
FWB_TRF2_24-2_2649 |  | 26 49 - FUNCAO TEMPERATURA | f4740c30-c6c5-4f7f-ba9b-fb45ddc9b945 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_2649 |  | FWB_DS_00832 | 20260416 | Status | 30 | DirectOperate | SingleBit | 917 | FALSE | FALSE | 5 | SingleCoord | 184;184 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_TRF2_24-2_81U4 |  | AJUSTE PARA 81 E4 | a5444459-53d9-4ae5-a5cb-41e86483a0a3 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_81U4 |  | FWB_DS_00837 | 20260416 | Status | 30 | DirectOperate | SingleBit | 922 | FALSE | FALSE | 5 | SingleCoord | 191 | ClosePulseOn | 0.25
FWB_TRF1_24-1_81U4 |  | AJUSTE PARA 81 E4 | 52b15339-b98b-415f-877e-f70a7525e188 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_81U4 |  | FWB_DS_00786 | 20260416 | Status | 30 | DirectOperate | SingleBit | 822 | FALSE | FALSE | 5 | SingleCoord | 171 | ClosePulseOn | 0.25
FWB_TRF1_24-1_BC_86 |  | 86BC - BLOQUEIO | 7adaf3f1-8aa9-4efa-aaf2-2184c6c40043 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | ReadWrite |  | REARMAR@null___NORMAL@ATUADO___Custom_S_TC_SA | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_BC_86 |  | FWB_DS_00799 | 20260416 | Status | 30 | DirectOperate | SingleBit | 835 | FALSE | FALSE | 5 | SingleCoord | 176 | ClosePulseOn | 0.25
FWB_TRF1_24-1_DJF1 |  | DISJUNTOR NF | 099575b8-ef4d-417e-91b4-70616f4ca04a | SwitchStatus | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_FWB_1 | FWB_TRF1_24-1_DJF1 |  | FWB_DS_00817 | 20260416 | Status | 30 | DirectOperate | MultiCoord | 801;802 | FALSE | FALSE | 15 | SingleCoord | 161;161 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TRF2_24-2_51N |  | 51N | 0a4f05f3-ab1f-4f05-adda-82f8a5200946 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_TRF2_24-2_51N |  | FWB_DS_00833 | 20260416 | Status | 30 | DirectOperate | SingleBit | 918 | FALSE | FALSE | 5 | SingleCoord | 183;183 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_TRF1_24-1_81U2 |  | AJUSTE PARA 81 E2 | 9a993907-65d5-4b06-bee1-63bad57f5234 | Status | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_TRF1_24-1_81U2 |  | FWB_DS_00784 | 20260416 | Status | 30 | DirectOperate | SingleBit | 820 | FALSE | FALSE | 5 | SingleCoord | 167 | ClosePulseOn | 0.25
FWB_IB_52-16_43TC |  | 43 - CHAVE TELECOMANDO | f6ccf700-c605-4c0e-9dbd-4f86ceea43af | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_IB_52-16_43TC |  | FWB_DS_00869 | 20260416 | Status |  |  | SingleBit | 1000 | FALSE
FWB_IB_52-16_SF6A |  | ALARME BAIXA PRESSAO SF6 | 516904f6-867d-49c9-8d96-6920b1326090 | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_IB_52-16_SF6A |  | FWB_DS_00870 | 20260416 | Status |  |  | SingleBit | 1004 | FALSE
FWB_IB_52-16_CCMO |  | FALTA VCC MOTOR | c19ab075-c255-4403-b440-cce740779188 | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_IB_52-16_CCMO |  | FWB_DS_00872 | 20260416 | Status |  |  | SingleBit | 1006 | FALSE
FWB_IB_52-16_CAFL |  | FALTA VCA | 69dd51fe-6f5f-43be-b5cb-14525ff86278 | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_IB_52-16_CAFL |  | FWB_DS_00874 | 20260416 | Status |  |  | SingleBit | 1008 | FALSE
FWB_IB_52-16_BBAB |  | BOBINA ABERTURA | 41634bfe-5ed6-4534-bd8e-413bb706be39 | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_IB_52-16_BBAB |  | FWB_DS_00880 | 20260416 | Status |  |  | SingleBit | 1014 | FALSE
FWB_IB_52-16_TEXT |  | TRIP EXTERNO | a32addbc-2945-4a44-ad02-8072088e4e6b | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_IB_52-16_TEXT |  | FWB_DS_00879 | 20260416 | Status |  |  | SingleBit | 1013 | FALSE
FWB_IB_52-16_TR2_PERP |  | PERMISSAO PARALELISMO | afa01181-c384-4dd6-85b6-38b0de00052b | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NÃO PERMITIDO@PERMITIDO___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_IB_52-16_TR2_PERP |  | FWB_DS_00887 | 20260416 | Status |  |  | SingleBit | 1026 | FALSE
FWB_IB_52-16_43LR |  | 43 - CHAVE LOCAL REMOTO | bd91b699-c831-4e2c-a5c0-67fc1930ff1d | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_IB_52-16_43LR |  | FWB_DS_00877 | 20260416 | Status |  |  | SingleBit | 1011 | FALSE
FWB_IB_52-16_FSIH |  | FALHA SINCRONISMO HORA | fc8ef1b6-983b-4dde-93ab-a48e713d951c | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_IB_52-16_FSIH |  | FWB_DS_00883 | 20260416 | Status |  |  | SingleBit | 1022 | FALSE
FWB_IB_52-16_DR |  | DEFEITO RELE | 897eb9d8-3792-4cbf-ad99-c2af504bb1c1 | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_IB_52-16_DR |  | ffee2523-0c48-4429-8e85-c9c98e215b06 | 20260416 | Status |  |  | SingleBit | 2333 | FALSE
FWB_IB_52-16_CCCO |  | FALTA VCC COMANDO | de26891e-79b3-49d8-a2f3-b5b77ad6811c | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_IB_52-16_CCCO |  | FWB_DS_00875 | 20260416 | Status |  |  | SingleBit | 1009 | FALSE
FWB_IB_52-16_BBFC |  | BOBINA FECHAMENTO | b66c0501-6eb1-4ded-9d67-d61e75e67f75 | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_IB_52-16_BBFC |  | FWB_DS_00878 | 20260416 | Status |  |  | SingleBit | 1012 | FALSE
FWB_IB_52-16_CCFL |  | FALTA VCC | b28654cc-0a12-4df1-926a-97a62761b53c | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_IB_52-16_CCFL |  | FWB_DS_00881 | 20260416 | Status |  |  | SingleBit | 1015 | FALSE
FWB_TRF2_24-2_DR |  | DEFEITO RELE | 6a7c515d-6d22-4dee-9201-32c6a8cace97 | Status | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_TRF2_24-2_DR |  | b0b939f4-3b7e-4bd0-95c2-b482c26a0bf1 | 20260416 | Status |  |  | SingleBit | 2337 | FALSE
FWB_IB_52-16_FCOM |  | FALHA COMUNICACAO | 2ef4219d-ff68-4025-aed2-5b149fe4d02b | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_IB_52-16_FCOM |  | FWB_DS_00888 | 20260416 | Status |  |  | SingleBit | 1027 | FALSE
FWB_IB_52-16_MOLA |  | MOLA | 2f62cada-9a61-45ab-87fe-df472ff8816f | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_IB_52-16_MOLA |  | FWB_DS_00873 | 20260416 | Status |  |  | SingleBit | 1007 | FALSE
FWB_IB_52-16_CCAB |  | FALTA VCC CIRCUITO ABERTURA | 4044d75a-7200-47d9-a5bf-97d8ab600feb | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_IB_52-16_CCAB |  | FWB_DS_00876 | 20260416 | Status |  |  | SingleBit | 1010 | FALSE
FWB_IB_52-16_FLK1 |  | FALHA LINK 1 | 439181e5-56b9-493b-af22-ecc1a58bb459 | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_IB_52-16_FLK1 |  | FWB_DS_00884 | 20260416 | Status |  |  | SingleBit | 1023 | FALSE
FWB_IB_52-16_SF6B |  | BLOQUEIO BAIXA PRESSAO SF6 | 2f4410e0-6718-407d-8b87-8e1acc4dc3b6 | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_IB_52-16_SF6B |  | FWB_DS_00871 | 20260416 | Status |  |  | SingleBit | 1005 | FALSE
FWB_IB_52-16_TR1_PERP |  | PERMISSAO PARALELISMO | 65ac7b8b-f677-4199-a798-3ddc42acf315 | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NÃO PERMITIDO@PERMITIDO___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_IB_52-16_TR1_PERP |  | FWB_DS_00886 | 20260416 | Status |  |  | SingleBit | 1025 | FALSE
FWB_IB_52-16_FLK2 |  | FALHA LINK 2 | 2735b2b6-baa6-4a83-94e4-119b635d9e80 | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_IB_52-16_FLK2 |  | FWB_DS_00885 | 20260416 | Status |  |  | SingleBit | 1024 | FALSE
FWB_IB_52-16_AJG2 |  | AJUSTE PARA GRUPO 2 | 747b0f21-0261-4171-860f-40aaa758442b | Status | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 2 |  | UTR_FWB_1 | FWB_IB_52-16_AJG2 |  | FWB_DS_00882 | 20260416 | Status | 30 | DirectOperate | SingleBit | 1020 | FALSE | FALSE | 15 | MultiCoord | 202;203 | ClosePulseOn;ClosePulseOn | 0.25;0.25
FWB_IB_52-16_DJF1 |  | DISJUNTOR NF | 1db9f4db-7470-4b16-b52e-dce01a11c4a5 | SwitchStatus | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 1 |  | UTR_FWB_1 | FWB_IB_52-16_DJF1 |  | FWB_DS_00889 | 20260416 | Status | 30 | DirectOperate | MultiCoord | 1001;1002 | FALSE | FALSE | 15 | SingleCoord | 201;201 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_BC1_52-10_43TC |  | 43 - CHAVE TELECOMANDO | 656cdb01-c988-4bc6-aa5a-a4fb9708d70f | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_43TC |  | FWB_DS_00890 | 20260416 | Status |  |  | SingleBit | 1500 | FALSE
FWB_BC1_52-10_B5M |  | BLOQUEIO 5 MINUTOS | 8d4ec53d-578e-4c81-868f-5163d163fc6d | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_B5M |  | FWB_DS_00891 | 20260416 | Status |  |  | SingleBit | 1504 | FALSE
FWB_BC1_52-10_SF6A |  | ALARME BAIXA PRESSAO SF6 | a3a2cc6a-aa9a-4db7-bb8f-49ee46154187 | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_SF6A |  | FWB_DS_00892 | 20260416 | Status |  |  | SingleBit | 1505 | FALSE
FWB_BC1_52-10_MOLA |  | MOLA | b2a824a0-aedd-4752-b3ff-61443c55f551 | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_MOLA |  | FWB_DS_00894 | 20260416 | Status |  |  | SingleBit | 1507 | FALSE
FWB_BC1_52-10_TEXT |  | TRIP EXTERNO | 7af99b60-8a7a-4df6-bfbf-c0e28855fe5e | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_TEXT |  | FWB_DS_00902 | 20260416 | Status |  |  | SingleBit | 1515 | FALSE
FWB_BC1_52-10_50N |  | 50 - SOBRECORRENTE INSTANTANEA NEUTRO | 9c865245-8b13-4d85-999f-e3ccafd0dfee | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_PROT_50N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_50N |  | FWB_DS_00908 | 20260416 | Status |  |  | SingleBit | 1521 | FALSE
FWB_BC1_52-10_FSIH |  | FALHA SINCRONISMO HORA | 06057024-d8c5-44a6-9fb5-a7ad221013e8 | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_FSIH |  | FWB_DS_00914 | 20260416 | Status |  |  | SingleBit | 1527 | FALSE
FWB_BC1_52-10_FCOM |  | FALHA COMUNICACAO | 8125f002-17f8-47a4-9fdf-20dd00b447a9 | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_FCOM |  | FWB_DS_00917 | 20260416 | Status |  |  | SingleBit | 1530 | FALSE
FWB_BC1_52-10_59 |  | 59 - SOBRETENSAO | 76e96df7-160e-47cc-98a6-a4d859e6ad79 | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_PROT_59 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_59 |  | FWB_DS_00911 | 20260416 | Status |  |  | SingleBit | 1524 | FALSE
FWB_BC1_52-10_FLK2 |  | FALHA LINK 2 | 2732b0dc-a852-4783-b622-58f78d8f67ce | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_FLK2 |  | FWB_DS_00916 | 20260416 | Status |  |  | SingleBit | 1529 | FALSE
FWB_BC1_52-10_43LR |  | 43 - CHAVE LOCAL REMOTO | 7b623a55-4e8b-430a-82eb-4e78d2f02cb6 | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_43LR |  | FWB_DS_00897 | 20260416 | Status |  |  | SingleBit | 1510 | FALSE
FWB_BC1_52-10_FLK1 |  | FALHA LINK 1 | 2a2cd1dd-8598-409a-9489-e9db96ed8040 | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_FLK1 |  | FWB_DS_00915 | 20260416 | Status |  |  | SingleBit | 1528 | FALSE
FWB_BC1_52-10_CCCO |  | FALTA VCC COMANDO | c0fef493-32fe-45c7-8264-d5d8dd2eb48d | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_CCCO |  | FWB_DS_00896 | 20260416 | Status |  |  | SingleBit | 1509 | FALSE
FWB_BC1_52-10_CCFL |  | FALTA VCC | b80a7bc2-7ab1-40c9-ab10-27a9374ec4a0 | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_BC1_52-10_CCFL |  | FWB_DS_00901 | 20260416 | Status |  |  | SingleBit | 1514 | FALSE
FWB_BC1_52-10_62BF |  | 62 - FALHA DISJUNTOR BLOQUEIO | b7dc6d25-7908-4d39-8e91-c63d372b010a | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_62BF |  | FWB_DS_00905 | 20260416 | Status |  |  | SingleBit | 1518 | FALSE
FWB_BC1_52-10_50F |  | 50 - SOBRECORRENTE INSTANTANEA FASE | 911ab0be-8248-4f31-93ce-8b559cdcf3d7 | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_PROT_50F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_50F |  | FWB_DS_00906 | 20260416 | Status |  |  | SingleBit | 1519 | FALSE
FWB_BC1_52-10_27_T |  | 27 - SUBTENSAO | 8bda442a-1872-4042-9194-11b19aa793e2 | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_PROT_27_T |  | Enabled | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_27_T |  | FWB_DS_00910 | 20260416 | Status |  |  | SingleBit | 1523 | FALSE
FWB_BC1_52-10_51F |  | 51 - SOBRECORRENTE TEMPORIZADA FASE | 436ab25c-cec5-4d38-ad60-16465202100c | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_51F |  | FWB_DS_00907 | 20260416 | Status |  |  | SingleBit | 1520 | FALSE
FWB_BC1_52-10_61 |  | 61 - DESEQUILIBRIO | d70fa5c6-9c81-4808-ba02-4f2bdd9d8dac | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_PROT_61 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_61 |  | FWB_DS_00912 | 20260416 | Status |  |  | SingleBit | 1525 | FALSE
FWB_BC1_52-10_CAFL |  | FALTA VCA | 55e8daea-e001-409c-a273-358594a24581 | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 | FWB_BC1_52-10_CAFL |  | FWB_DS_00895 | 20260416 | Status |  |  | SingleBit | 1508 | FALSE
FWB_BC1_52-10_BBAB |  | BOBINA ABERTURA | ffdff9ab-62dd-46bf-83d8-b124341c2048 | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_BBAB |  | FWB_DS_00898 | 20260416 | Status |  |  | SingleBit | 1512 | FALSE
FWB_BC1_52-10_CCAB |  | FALTA VCC CIRCUITO ABERTURA | 13a7a827-49d0-4e5b-9cc4-0efc06ebcf80 | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_CCAB |  | FWB_DS_00900 | 20260416 | Status |  |  | SingleBit | 1513 | FALSE
FWB_BC1_52-10_51N1 |  | 51 - SOBRECORRENTE TEMPORIZADA NEUTRO | 8989ad51-0de2-46d6-b2b3-5b0ef71bdef5 | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_51N1 |  | FWB_DS_00909 | 20260416 | Status |  |  | SingleBit | 1522 | FALSE
FWB_BC1_52-10_CCMO |  | FALTA VCC MOTOR | 752084d4-81ad-4b80-9740-4a53c8f1df65 | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_CCMO |  | FWB_DS_00904 | 20260416 | Status |  |  | SingleBit | 1517 | FALSE
FWB_BC1_52-10_SF6B |  | BLOQUEIO BAIXA PRESSAO SF6 | d135613a-d195-4b22-8e48-8151484f04b7 | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_SF6B |  | FWB_DS_00893 | 20260416 | Status |  |  | SingleBit | 1506 | FALSE
FWB_BC1_52-10_BBFC |  | BOBINA FECHAMENTO | 9da2d6e0-7e11-4ee9-9a0a-d61b4df4e7ae | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_BBFC |  | FWB_DS_00899 | 20260416 | Status |  |  | SingleBit | 1511 | FALSE
FWB_BC1_52-10_DR |  | DEFEITO RELE | 644e71f2-295f-4ddc-b40e-5d16c01b8304 | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_DR |  | 7974ec6f-a451-4b8b-abc8-d7e4b87f37b0 | 20260416 | Status |  |  | SingleBit | 2326 | FALSE
FWB_BC1_52-10_86 |  | 86 - BLOQUEIO | 945b2939-4c49-4943-8d14-1c58948e3f99 | Status | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | Custom | ABC | None | ReadWrite |  | REARMAR@null___NORMAL@ATUADO___Custom_S_TC_SA | 1 |  | UTR_FWB_1 | FWB_BC1_52-10_86 |  | FWB_DS_00903 | 20260416 | Status | 30 | DirectOperate | SingleBit | 1516 | FALSE | FALSE | 5 | SingleCoord | 282 | ClosePulseOn | 0.25
FWB_BC1_52-10_DJF1 |  | DISJUNTOR NF | 56aaedca-d865-47e9-85f7-89d7d8d4251f | SwitchStatus | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_FWB_1 | FWB_BC1_52-10_DJF1 |  | FWB_DS_00918 | 20260416 | Status | 30 | DirectOperate | MultiCoord | 1501;1502 | FALSE | FALSE | 15 | SingleCoord | 281;281 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_BP1_BP1_86CC |  | FALTA VCC CIRCUITO RELE 86 | 57ab7f75-fba8-45d1-9ff9-a2cec49e059d | Status | FWB Trans | [8 empty] | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_BP1_BP1_86CC |  | ddc561c9-5d15-4365-b825-cc572d22dd4e | 20260417 | Status |  |  | SingleBit | 1703 | FALSE
FWB_BP2_BP2_86CC |  | FALTA VCC CIRCUITO RELE 86 | 141346e0-f113-41da-85a7-a1a4e63cd663 | Status | FWB Trans | [8 empty] | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_BP2_BP2_86CC |  | 3360fe0c-f441-46fa-b86b-b8b5c0cf5013 | 20260417 | Status |  |  | SingleBit | 1803 | FALSE
FWB_BP1_87BAR_FLK2 |  | FALHA LINK 2 | 74156cf3-dee1-4086-aa10-8025c964c436 | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_BP1_87BAR_FLK2 |  | 7d5743bf-cf9e-450e-bf25-b108dcced265 | 20260417 | Status |  |  | SingleBit | 1706 | FALSE
FWB_BP1_87BAR_FSIN |  | FALHA IRIG B - SINCRONISMO | eb78bd0c-8443-44fe-bb52-427d1aa27ade | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_BP1_87BAR_FSIN |  | dbff7af0-cba3-4d46-a025-686610f300c2 | 20260417 | Status |  |  | SingleBit | 1704 | FALSE
FWB_BP2_87BAR_FSIN |  | FALHA IRIG B - SINCRONISMO | f2f30a4e-145a-4408-9913-7d285de13169 | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_BP2_87BAR_FSIN |  | 19af54b1-2056-4957-95aa-75607c05ed54 | 20260417 | Status |  |  | SingleBit | 1804 | FALSE
FWB_SE_SE_PREX |  | ALARME PREDIAL PRESENCA EXTERNA | 4510fc2b-14e0-4241-9d7b-73ede955ab92 | Status | FWB Trans | [8 empty] | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SP | 1 |  | UTR_FWB_1 | FWB_SE_SE_PREX |  | dc409ca7-89f8-4d7b-834e-2ac7db23dcb2 | 20260417 | Status |  |  | SingleBit | 2344 | FALSE
FWB_BP2_87BAR_87_T |  | 87 - TRIP DIFERENCIAL | 55d05696-2a99-4987-bb32-d4f4021a26bc | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT_87_T |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_BP2_87BAR_87_T |  | 578ed0fa-1039-446e-a138-bfc9ab12805a | 20260417 | Status |  |  | SingleBit | 1800 | FALSE
FWB_SE_RET1_DRET |  | DEFEITO RETIFICADOR | 52c1e92a-4dba-4b89-98be-1a7133593b0b | Status | FWB Trans | [6 empty] | SCD_SE_RET1_RET |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_SE_RET1_DRET |  | 540c2abd-308a-4c3a-a78b-262e5d2d6e0c | 20260417 | Status |  |  | SingleBit | 2342 | FALSE
FWB_BP2_87BAR_43TC |  | 43 - CHAVE TELECOMANDO | 99ed53a7-07d4-43fa-b5ae-5ef558a5da4a | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_BP2_87BAR_43TC |  | 4f4ed3fc-c01c-48bc-946a-958858abf56c | 20260417 | Status |  |  | SingleBit | 1817 | FALSE
FWB_BP1_87BAR_87_T |  | 87 - TRIP DIFERENCIAL | 79b90dce-8172-4e35-bcc7-6d4904769314 | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT_87_T |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 | FWB_BP1_87BAR_87_T |  | 8dc83111-720e-488b-9c95-32c6e6feed9c | 20260417 | Status |  |  | SingleBit | 1700 | FALSE
FWB_BP1_87BAR_FCOM |  | FALHA COMUNICACAO | 729fd80f-ce6c-4d7d-bb12-cfceb9830bed | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_BP1_87BAR_FCOM |  | 8121751d-ccc1-4ba0-b9ac-15af27a34023 | 20260417 | Status |  |  | SingleBit | 1718 | FALSE
FWB_BP2_87BAR_DR |  | DEFEITO RELE | d2a83165-5ace-4edf-8d36-f754d7a53fd3 | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_BP2_87BAR_DR |  | 59928f75-2582-4be2-bdf4-25a90ace8d90 | 20260417 | Status |  |  | SingleBit | 2324 | FALSE
FWB_SE_SACC_FGTE |  | FUGA TERRA | a3195a37-2d40-4186-8692-36b4fab7d6e7 | Status | FWB Trans | [6 empty] | SCD_SE_RET1_RET |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_SE_SACC_FGTE |  | 884f6766-1063-4dc9-a6d6-d9a69ee17118 | 20260417 | Status |  |  | SingleBit | 2341 | FALSE
FWB_SE_SE_FUMA |  | SENSOR FUMACA | 344f1fe5-9f86-4dad-b250-310fffa6ffe7 | Status | FWB Trans | [8 empty] | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SP | 1 |  | UTR_FWB_1 | FWB_SE_SE_FUMA |  | 04f6f2f2-9e6f-4a5a-b2f3-64685e4b07ae | 20260417 | Status |  |  | SingleBit | 2345 | FALSE
FWB_A8000_A8000_FCOM |  | FALHA COMUNICACAO | 4530f463-5903-47f4-a647-06d6270f4da9 | Status | FWB Trans | [8 empty] | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_A8000_A8000_FCOM |  | 09ee7d02-6716-48aa-b9de-c2bceda12048 | 20260417 | Status |  |  | SingleBit | 2364 | FALSE
FWB_BP1_87BAR_43TC |  | 43 - CHAVE TELECOMANDO | b0faeaff-79dd-43a9-9808-423afdfbbf94 | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_FWB_1 | FWB_BP1_87BAR_43TC |  | b30ca554-4b41-4b01-81b8-98a7c0ce871b | 20260417 | Status |  |  | SingleBit | 1717 | FALSE
FWB_BP2_87BAR_FCOM |  | FALHA COMUNICACAO | 50aa24d1-b61c-44f8-a120-57eb5f0d4306 | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_BP2_87BAR_FCOM |  | db031a7a-63e0-45db-9946-391660f91720 | 20260417 | Status |  |  | SingleBit | 1818 | FALSE
FWB_BP2_87BAR_FLK2 |  | FALHA LINK 2 | 35098748-07ae-4718-964e-9d5429c76ec9 | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_BP2_87BAR_FLK2 |  | 937c1bc8-ea65-40c8-922b-d0f3389d16a8 | 20260417 | Status |  |  | SingleBit | 1806 | FALSE
FWB_BP1_87BAR_DR |  | DEFEITO RELE | edcd26b8-f528-4d8b-8ba5-2474f2383ffe | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_BP1_87BAR_DR |  | bb36fc75-1210-4ead-82f7-c1ea0997726b | 20260417 | Status |  |  | SingleBit | 2322 | FALSE
FWB_BP1_87BAR_FLK1 |  | FALHA LINK 1 | bdc8a320-1c2e-4413-86c2-9b5b1ff67f86 | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_BP1_87BAR_FLK1 |  | 0f19e70c-bc67-4e7e-8393-7a449ec82cfd | 20260417 | Status |  |  | SingleBit | 1705 | FALSE
FWB_BP2_87BAR_FLK1 |  | FALHA LINK 1 | 7da922a1-6d29-43ac-9bfd-c4fb19ecf62d | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 | FWB_BP2_87BAR_FLK1 |  | e3abc7c2-87bc-4a65-a995-f45a06177793 | 20260417 | Status |  |  | SingleBit | 1805 | FALSE
FWB_SE_RET2_DRET |  | DEFEITO RETIFICADOR | 037390b8-1d99-4411-955b-0310d6df9035 | Status | FWB Trans | [6 empty] | FWB_SE_RET2_RET |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 | FWB_SE_RET2_DRET |  | 87d2b1ce-1633-45e7-a34a-f74582d3d524 | 20260417 | Status |  |  | SingleBit | 2343 | FALSE
FWB_BP1_87BAR_87 |  | 87 BARRA | 616c9253-b213-4ecc-bd43-dfd62c9f2e66 | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT_87 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_BP1_87BAR_87 |  | fae73dcc-4acb-4f0d-b4a5-02db0c656c4e | 20260417 | Status | 30 | DirectOperate | SingleBit | 1716 | FALSE | FALSE | 5 | SingleCoord | 330;330 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_BP1_87BAR_TR1_87 |  | 87 | a2116d9c-5cfe-4da6-acd6-98d17906d499 | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_BP1_87BAR_TR1_87 |  | 35ef5478-3103-452d-a321-011e2c6a2f3d | 20260417 | Status | 30 | DirectOperate | SingleBit | 1707 | FALSE | FALSE | 5 | SingleCoord | 321;321 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_BP1_87BAR_TRF1_87 |  | 87 | 19a927ef-8a4e-4e6a-8d0d-91107f9c6dc6 | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_BP1_87BAR_TRF1_87 |  | 1f912e51-f1d5-4097-bce6-e685c2c2b107 | 20260417 | Status | 30 | DirectOperate | SingleBit | 1714 | FALSE | FALSE | 5 | SingleCoord | 328;328 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_BP1_87BAR_AL13_87 |  | 87 | b0a91ba2-9d59-4d1b-b5a9-68f7c3601249 | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_BP1_87BAR_AL13_87 |  | c2f18d43-bd38-4291-aed8-099ac2c3c15d | 20260417 | Status | 30 | DirectOperate | SingleBit | 1711 | FALSE | FALSE | 5 | SingleCoord | 325;325 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_BP1_87BAR_AL12_87 |  | 87 | 1e294cca-5d48-489a-9a1f-30e734073d1a | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_BP1_87BAR_AL12_87 |  | 1c741192-8081-4943-b606-7cbeed5207b3 | 20260417 | Status | 30 | DirectOperate | SingleBit | 1710 | FALSE | FALSE | 5 | SingleCoord | 324;324 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_BP1_87BAR_BC1_87 |  | 87 | 41af6e2c-8a8d-4ac3-bbcf-dedbbfa9e1fc | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_BP1_87BAR_BC1_87 |  | feb4417c-4c1a-4780-bf27-db1b731b3671 | 20260417 | Status | 30 | DirectOperate | SingleBit | 1708 | FALSE | FALSE | 5 | SingleCoord | 322;322 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_BP2_87BAR_TRF2_87 |  | 87 | a3e2a1b0-2311-49d2-af73-6ec93d5939ff | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_BP2_87BAR_TRF2_87 |  | 48880239-0599-4bee-8bec-ddec5cf055a1 | 20260417 | Status | 30 | DirectOperate | SingleBit | 1814 | FALSE | FALSE | 5 | SingleCoord | 348;348 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_BP2_87BAR_AL24_87 |  | 87 | 5d6cf038-9d3a-468f-b53e-e97be4a651a7 | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_BP2_87BAR_AL24_87 |  | 19669fcb-43f4-442a-bd9b-97d4aef459e9 | 20260417 | Status | 30 | DirectOperate | SingleBit | 1812 | FALSE | FALSE | 5 | SingleCoord | 346;346 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_SE_SE_PRES |  | ALARME PREDIAL | 068c6294-2583-4d5b-afde-5d6a2a6ccdf6 | Status | FWB Trans | [8 empty] | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 2 |  | UTR_FWB_1 | FWB_SE_SE_PRES |  | f2245cc2-57f4-4790-9f29-3633635caa4d | 20260417 | Status | 30 | DirectOperate | SingleBit | 2363 | FALSE | FALSE | 5 | SingleCoord | 421;421 | TripPulseOn;ClosePulseOn | 0;0
FWB_BP2_87BAR_BC2_87 |  | 87 | 3a55dd44-a459-4dfb-bde9-1ac8dd0aec29 | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_BP2_87BAR_BC2_87 |  | 78aa494a-2802-4a8b-8fbe-8a5abb43b50d | 20260417 | Status | 30 | DirectOperate | SingleBit | 1808 | FALSE | FALSE | 5 | SingleCoord | 342;342 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_BP1_87BAR_AL11_87 |  | 87 | fd5218b5-5798-4890-8ad6-3938497f432f | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_BP1_87BAR_AL11_87 |  | c7444f93-ff87-4e93-9aa5-62ff57bda73d | 20260417 | Status | 30 | DirectOperate | SingleBit | 1709 | FALSE | FALSE | 5 | SingleCoord | 323;323 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_BP2_87BAR_AL22_87 |  | 87 | 40be1d70-90cb-46f3-aa37-7f7b54420e3d | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_BP2_87BAR_AL22_87 |  | 58d57409-195d-46fb-b4a4-359ac03d2a85 | 20260417 | Status | 30 | DirectOperate | SingleBit | 1810 | FALSE | FALSE | 5 | SingleCoord | 344;344 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_BP2_87BAR_87 |  | 87 BARRA | f4975288-42f0-44ba-a2bb-c1751c6bd989 | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT_87 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_BP2_87BAR_87 |  | 20601a49-8187-4f57-8c73-f8d8a6a66148 | 20260417 | Status | 30 | DirectOperate | SingleBit | 1816 | FALSE | FALSE | 5 | SingleCoord | 350;350 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_BP2_87BAR_AL23_87 |  | 87 | 12904a1e-7240-4831-922b-b69f1df359ae | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_BP2_87BAR_AL23_87 |  | 64e338a6-c61b-47cb-b576-1415bec2e876 | 20260417 | Status | 30 | DirectOperate | SingleBit | 1811 | FALSE | FALSE | 5 | SingleCoord | 345;345 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_BP2_87BAR_AL25_87 |  | 87 | 3ca5c682-4d7e-4882-a54c-27dcf0e1fe18 | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_BP2_87BAR_AL25_87 |  | 2f6e42ed-6cae-4151-bfb0-de4cce87a4ac | 20260417 | Status | 30 | DirectOperate | SingleBit | 1813 | FALSE | FALSE | 5 | SingleCoord | 347;347 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_BP1_87BAR_AL15_87 |  | 87 | 26d7700d-1ea4-4b4e-985b-70fb1a657e7b | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_BP1_87BAR_AL15_87 |  | abaf527a-19aa-4b64-b224-c96f809616a9 | 20260417 | Status | 30 | DirectOperate | SingleBit | 1713 | FALSE | FALSE | 5 | SingleCoord | 327;327 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_BP1_87BAR_AL14_87 |  | 87 | b1c08d0e-65a2-4f40-887e-e98bd4e651c1 | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_BP1_87BAR_AL14_87 |  | 0138f5b2-a9c2-47a1-b339-1aa61e3dcde2 | 20260417 | Status | 30 | DirectOperate | SingleBit | 1712 | FALSE | FALSE | 5 | SingleCoord | 326;326 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_BP2_87BAR_IB_87 |  | 87 | efa43b60-0f3f-43ea-91e2-3fcd7d8e9101 | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_BP2_87BAR_IB_87 |  | b681f776-f7a7-4825-b51a-513e29ded9f3 | 20260417 | Status | 30 | DirectOperate | SingleBit | 1815 | FALSE | FALSE | 5 | SingleCoord | 349;349 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_BP2_87BAR_TR2_87 |  | 87 | 64051293-7bd3-4527-8807-4e9bca165292 | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_BP2_87BAR_TR2_87 |  | b39a338b-258d-411d-8367-b24beab72e26 | 20260417 | Status | 30 | DirectOperate | SingleBit | 1807 | FALSE | FALSE | 5 | SingleCoord | 341;341 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_BP1_87BAR_IB_87 |  | 87 | 5e4e1db3-00a3-409d-a223-10b52b0ec5b2 | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_BP1_87BAR_IB_87 |  | 547075be-99e0-4f94-ae68-bee49ee29da7 | 20260417 | Status | 30 | DirectOperate | SingleBit | 1715 | FALSE | FALSE | 5 | SingleCoord | 329;329 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_BP2_87BAR_AL21_87 |  | 87 | 15fa3b79-8b78-4371-86ee-2e0ff9fa10be | Status | FWB Trans | [6 empty] | FWB_BP1_BP1_87_PROT |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 | FWB_BP2_87BAR_AL21_87 |  | 4bd5608a-544f-4219-af8e-1ba12001fc7e | 20260417 | Status | 30 | DirectOperate | SingleBit | 1809 | FALSE | FALSE | 5 | SingleCoord | 343;343 | TripPulseOn;ClosePulseOn | 0.25;0.25

## DNP3_AnalogSignals
Signal Details | [35 empty] | Remote Points
ASIGNAL | [26 empty] | ADVALMLIMITS | [8 empty] | REMOTEPOINT | [17 empty] | APROCESSING
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | MEASUREMENT_TYPE | IDOBJ_AORGROUP | SIGNAL_DEVICEMAPPING | [7 empty] | ASIGNAL_TYPE | MEASUREMENT_PHASE | MEASUREMENT_UNIT | MEASUREMENT_SIDE | SIGNAL_DIRECTION | SIGNAL_ANNUALSCH | ASIGNAL_FLOWDIRECTION | ASIGNAL_RATEDVALUE | ASIGNAL_MINSETPOINT | ASIGNAL_MAXSETPOINT | ASIGNAL_TRUST | ASIGNAL_ALARMLIMITS | MEASUREMENT_PSR | IDOBJ_NAME | ADVALMLIMITS_ROCALARMGROWTH | ADVALMLIMITS_ROCLIMITGROWTH | ADVALMLIMITS_ROCALARMDROP | ADVALMLIMITS_ROCLIMITDROP | ADVALMLIMITS_FLATLINEALARM | ADVALMLIMITS_FLATLINETIMEOUT | ADVALMLIMITS_CREEPALARM | ADVALMLIMITS_CREEPDEADBAND | IDOBJ_NAME | DELETE | IDOBJ_CUSTOMID | IDOBJ_ALIAS | REMOTEPOINT_TYPE | REMOTEPOINT_SCALING | REMOTEPOINT_INTERCEPT | REMOTEPOINT_ADCFAIL | REMOTEOUTPUT_CMDTIMEOUT | REMOTEOUTPUT_SBOMODE | REMOTEOUTPUT_SPTOL | REMOTEINPUTDNP3_INCOORDS¦REMOTEOUTPUTDNP3_INCOORDS | REMOTEINPUTDNP3_OUTREGISTER¦REMOTEOUTPUTDNP3_OUTREGISTER | AOUTPUTDNP3_OUTTYPE | REMOTEOUTPUTDNP3_OUTCOORDS | COUNTERDNP3_ENABLEROLLOVER | COUNTERDNP3_ROLLOVER | COUNTERDNP3_RESET | APROCESSING_LOCALDBCHECK | APROCESSING_USERELATIVEDB | APROCESSING_DEADBANDTYPE | APROCESSING_DEADBAND | APROCESSING_ZEROCLAMPINGDB | APROCESSING_LINEARFILTER | APROCESSING_LFFACTOR
Signal Name | Delete | Signal Alias | Signal Custom ID | Measurement Type | Signal AOR Group | Substation | Feeder | Feeder Object | Bank | Bay | Device | Device Mapping | Description | Signal Type | Phases | Display Unit | Side | Direction | Annual Schedule | Flow Direction | Rated Value | Min. Setpoint | Max. Setpoint | Trust Factor | Alarm Limits | Remote Unit | Advanced Alarms - Name | Advanced Alarms - Rate-Of-Growth Alarm | Advanced Alarms - Rate-Of-Growth Limit | Advanced Alarms - Rate-Of-Drop Alarm | Advanced Alarms - Rate-Of-Drop Limit | Advanced Alarm - Flatline Alarm | Advanced Alarm - Flatline Timeout [s] | Advanced Alarm - Creep Alarm | Advanced Alarm - Creep Deadband | Remote Point Name | Delete Remote Point | Remote Point Custom ID | Remote Point Alias | Remote Point Type | Scaling Factor | Intercept | ADC Fail | Command Timeout [s] | Commanding Mode | Setpoint Tolerance | Input Coordinates | Output Register | Output Data Type | Output Coordinates | Enable Rollover | Rollover Value | With Reset | Advanced Processing - Local Deadband Check | Advanced Processing - Use Relative Deadband | Deadband Type | Advanced Processing - Deadband | Advanced Processing - Zero Clamping Deadband | Advanced Processing - Apply Linear Filter | Advanced Processing - Linear Filter Factor
FWB_TR1AT_TR1AT_IA |  | CORRENTE FASE A | c60cc50c-b33d-48ba-9e58-c6299e66fc4d | Current | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_TC |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR1AT_TR1AT_IA |  | FWB_AS_00001 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 233 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1AT_TR1AT_IB |  | CORRENTE FASE B | ff21fa34-a356-460d-bb65-f7f1145b99ea | Current | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_TC |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR1AT_TR1AT_IB |  | FWB_AS_00002 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 234 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1AT_TR1AT_IC |  | CORRENTE FASE C | e4ca17cd-97db-4a7f-a1ac-e22a0c2983ea | Current | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_TC |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR1AT_TR1AT_IC |  | FWB_AS_00003 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 235 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1AT_TR1AT_IN |  | CORRENTE NEUTRO | a9abc6f8-9d9f-410e-a880-a665a8cc70fa | Current | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_TC |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR1AT_TR1AT_IN |  | FWB_AS_00004 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 236 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1AT_TR1AT_VAB |  | TENSAO FASE AB | e1b70457-e8ea-4c38-b408-cc28ff625937 | Voltage | FWB Trans | [6 empty] | FWB_TR1AT_52-2_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | VBC_144.9@143.52_131.1@124.2_Trans | UTR_FWB_1 | [9 empty] | FWB_TR1AT_TR1AT_VAB |  | FWB_AS_00005 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 221 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1AT_TR1AT_VBC |  | TENSAO FASE BC | 7c409c7c-dffa-42b6-a685-e91976a7eda2 | Voltage | FWB Trans | [6 empty] | FWB_TR1AT_52-2_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR1AT_TR1AT_VBC |  | FWB_AS_00006 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 222 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1AT_TR1AT_VCA |  | TENSAO FASE CA | 20ec6bc1-13d7-433c-ab79-68a07923caaa | Voltage | FWB Trans | [6 empty] | FWB_TR1AT_52-2_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR1AT_TR1AT_VCA |  | FWB_AS_00007 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 223 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1AT_TR1AT_P |  | POTENCIA ATIVA | 470efd53-a5bd-4718-85ff-41242707f4ca | ActivePower | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_TC |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR1AT_TR1AT_P |  | FWB_AS_00008 | 20260410 | Analog | 1000 | 0 | FALSE |  |  |  | 224 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1AT_TR1AT_Q |  | POTENCIA REATIVA | a5fbca3e-2869-47c1-9c13-8949884c73dd | ReactivePower | FWB Trans | [6 empty] | FWB_TR1AT_TR1AT_TC |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR1AT_TR1AT_Q |  | FWB_AS_00009 | 20260410 | Analog | 1000 | 0 | FALSE |  |  |  | 225 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1AT_TR1AT_FREQ |  | FREQUENCIA | b4140e61-8ed4-4225-99a4-d52d80d4eebe | Frequency | FWB Trans | [6 empty] | FWB_TR1AT_52-2_DJ |  | MeasuredValue | ABC | Hz | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR1AT_TR1AT_FREQ |  | FWB_AS_00010 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 226 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1BT_TR1BT_IA |  | CORRENTE FASE A | 0612dfdd-acf0-422b-9703-9201fd91d61f | Current | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_TC |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR1BT_TR1BT_IA |  | FWB_AS_00011 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 237 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1BT_TR1BT_IB |  | CORRENTE FASE B | add6174a-757c-4b4a-b223-d4bf9b6150d2 | Current | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_TC |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR1BT_TR1BT_IB |  | FWB_AS_00012 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 238 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1BT_TR1BT_IC |  | CORRENTE FASE C | bbea55b7-6aea-422b-95a6-0f2e883dfdd4 | Current | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_TC |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR1BT_TR1BT_IC |  | FWB_AS_00013 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 239 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1BT_TR1BT_IN |  | CORRENTE NEUTRO | ab0ea89c-5cbd-4d7a-8e95-f0944d0727d5 | Current | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_TC |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR1BT_TR1BT_IN |  | FWB_AS_00014 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 240 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1BT_TR1BT_VAB |  | TENSAO FASE AB | 319b509d-b94c-48a9-a8d4-ed90ade7403a | Voltage | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | V_24.2@23.9_21.9@21.6_Trans | UTR_FWB_1 | [9 empty] | FWB_TR1BT_TR1BT_VAB |  | FWB_AS_00015 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 227 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1BT_TR1BT_VBC |  | TENSAO FASE BC | 7e05d4ca-f8e4-46ae-bb52-6d564e6ef927 | Voltage | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR1BT_TR1BT_VBC |  | FWB_AS_00016 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 228 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1BT_TR1BT_VCA |  | TENSAO FASE CA | 08851326-4eec-48c9-b07a-c3a448dfe414 | Voltage | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR1BT_TR1BT_VCA |  | FWB_AS_00017 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 229 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1BT_TR1BT_P |  | POTENCIA ATIVA | 67baa7df-883d-4cc0-aabe-db613dbae83f | ActivePower | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_TC |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR1BT_TR1BT_P |  | FWB_AS_00018 | 20260410 | Analog | 1000 | 0 | FALSE |  |  |  | 230 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1BT_TR1BT_Q |  | POTENCIA REATIVA | a50b92d1-578a-41dc-b972-c4feaf0b4a72 | ReactivePower | FWB Trans | [6 empty] | FWB_TR1BT_TR1BT_TC |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR1BT_TR1BT_Q |  | FWB_AS_00019 | 20260410 | Analog | 1000 | 0 | FALSE |  |  |  | 231 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1BT_TR1BT_FREQ |  | FREQUENCIA | 123f192f-e616-4afa-bfd4-84e972a0d036 | Frequency | FWB Trans | [6 empty] | FWB_TR1BT_52-6_DJ |  | MeasuredValue | ABC | Hz | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR1BT_TR1BT_FREQ |  | FWB_AS_00020 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 232 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1_TR1_TOLE |  | TEMPERATURA OLEO | 90f0e2ba-aa4f-4360-8992-7cab734de29c | Temperature | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | C | None | Read |  | Undirected | 0 | 0 | 100 | -1 | TOLE_95@85_0@0_Trans | UTR_FWB_1 | [9 empty] | FWB_TR1_TR1_TOLE |  | FWB_AS_00021 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 440 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1AT_TR1AT_TENR |  | TEMPERATURA ENROLAMENTO | 9ff088a8-0c60-4ddb-aa7a-4dee90d3ded2 | Temperature | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | C | None | Read |  | Undirected | 0 | 0 | 100 | -1 | TENR_105@95_0@0_Trans | UTR_FWB_1 | [9 empty] | FWB_TR1AT_TR1AT_TENR |  | FWB_AS_00022 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 441 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1BT_TR1BT_TENR |  | TEMPERATURA ENROLAMENTO | f8d197b7-fcf7-4aac-b935-deedbd00cd17 | Temperature | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | C | None | Read |  | Undirected | 0 | 0 | 100 | -1 | TENR_105@95_0@0_Trans | UTR_FWB_1 | [9 empty] | FWB_TR1BT_TR1BT_TENR |  | FWB_AS_00023 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 442 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR1_CDC_TOLE |  | TEMPERATURA OLEO | 07316e4a-056c-42db-9828-5317e8d1589e | Temperature | FWB Trans | [6 empty] | FWB_TR1_TR1_TR |  | Custom | ABC | C | None | Read |  | Undirected | 0 | 0 | 100 | -1 | TOLE_95@85_0@0_Trans | UTR_FWB_1 | [9 empty] | FWB_TR1_CDC_TOLE |  | FWB_AS_00024 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 443 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL12_52-12_IA |  | IA | 27d483ed-f9a8-4051-9bd5-e5a72b931d0e | Current | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL12_52-12_IA |  | FWB_AS_00049 | 20260415 | Analog | 1 | 0 | FALSE |  |  |  | 21 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL12_52-12_ICCC |  | IC DESARME | c34f705b-b4cd-4ddb-9755-6e846e1aff23 | Current | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | MeasuredValue | AC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL12_52-12_ICCC |  | FWB_AS_00060 | 20260415 | Analog | 1 | 0 | FALSE |  |  |  | 32 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL12_52-12_Q |  | Q | f68e8184-a042-49ce-9c9c-4e3311ea53a1 | ReactivePower | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL12_52-12_Q |  | FWB_AS_00057 | 20260415 | Analog | 1 | 0 | FALSE |  |  |  | 29 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2AT_TR2AT_IA |  | CORRENTE FASE A | 22aeb5ee-d36c-4618-be0c-fde11f464bd3 | Current | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_TC |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR2AT_TR2AT_IA |  | FWB_AS_00025 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 263 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2AT_TR2AT_VAB |  | TENSAO FASE AB | 4f22d29a-a872-4844-818d-45aed50b973a | Voltage | FWB Trans | [6 empty] | FWB_TR2AT_52-3_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | VBC_144.9@143.52_131.1@124.2_Trans | UTR_FWB_1 | [9 empty] | FWB_TR2AT_TR2AT_VAB |  | FWB_AS_00029 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 251 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2AT_TR2AT_P |  | POTENCIA ATIVA | be90120d-6487-4c19-9c66-8bb79351cf8d | ActivePower | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_TC |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR2AT_TR2AT_P |  | FWB_AS_00032 | 20260414 | Analog | 1000 | 0 | FALSE |  |  |  | 254 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2AT_TR2AT_VBC |  | TENSAO FASE BC | f93be954-ac0d-450c-8892-1049a341df52 | Voltage | FWB Trans | [6 empty] | FWB_TR2AT_52-3_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR2AT_TR2AT_VBC |  | FWB_AS_00030 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 252 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2BT_TR2BT_VAB |  | TENSAO FASE AB | 24397d1f-3027-4ce4-bfc8-91e6c7237a61 | Voltage | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | V_24.2@23.9_21.9@21.6_Trans | UTR_FWB_1 | [9 empty] | FWB_TR2BT_TR2BT_VAB |  | FWB_AS_00039 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 257 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2BT_TR2BT_IA |  | CORRENTE FASE A | 097857a9-da4b-4970-843a-70525ec179c1 | Current | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_TC |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR2BT_TR2BT_IA |  | FWB_AS_00035 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 267 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2BT_TR2BT_TENR |  | TEMPERATURA ENROLAMENTO | c78af3c1-fca1-42ad-a2c4-9382fcb634d2 | Temperature | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | C | None | Read |  | Undirected | 0 | 0 | 100 | -1 | TENR_105@95_0@0_Trans | UTR_FWB_1 | [9 empty] | FWB_TR2BT_TR2BT_TENR |  | FWB_AS_00047 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 462 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2AT_TR2AT_IC |  | CORRENTE FASE C | ceecb8e3-be43-48ac-b8dc-fb923143c143 | Current | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_TC |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR2AT_TR2AT_IC |  | FWB_AS_00027 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 265 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2AT_TR2AT_Q |  | POTENCIA REATIVA | 731e0f8b-26e8-4503-88e5-beedd7e4edc4 | ReactivePower | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_TC |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR2AT_TR2AT_Q |  | FWB_AS_00033 | 20260414 | Analog | 1000 | 0 | FALSE |  |  |  | 255 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2BT_TR2BT_IC |  | CORRENTE FASE C | b27123d9-609c-47a9-b5b0-ddfe16e3a9d8 | Current | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_TC |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR2BT_TR2BT_IC |  | FWB_AS_00037 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 269 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2BT_TR2BT_VBC |  | TENSAO FASE BC | 04b3badd-da99-430d-85ec-9d78b00808e0 | Voltage | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR2BT_TR2BT_VBC |  | FWB_AS_00040 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 258 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2AT_TR2AT_TENR |  | TEMPERATURA ENROLAMENTO | 842fbc1a-a59a-45f1-b10e-2cdfa6947bdc | Temperature | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | C | None | Read |  | Undirected | 0 | 0 | 100 | -1 | TENR_105@95_0@0_Trans | UTR_FWB_1 | [9 empty] | FWB_TR2AT_TR2AT_TENR |  | FWB_AS_00046 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 461 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2_CDC_TOLE |  | TEMPERATURA OLEO | 40ffbeed-1f54-4e6c-8b17-fc1f32e66cb9 | Temperature | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | C | None | Read |  | Undirected | 0 | 0 | 100 | -1 | TOLE_95@85_0@0_Trans | UTR_FWB_1 | [9 empty] | FWB_TR2_CDC_TOLE |  | FWB_AS_00048 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 463 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2BT_TR2BT_VCA |  | TENSAO FASE CA | 504d9bb2-0166-460b-b199-4e051a0c809f | Voltage | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR2BT_TR2BT_VCA |  | FWB_AS_00041 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 259 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2AT_TR2AT_IB |  | CORRENTE FASE B | d3441fb9-8845-4049-91c1-7dc8ee30c924 | Current | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_TC |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR2AT_TR2AT_IB |  | FWB_AS_00026 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 264 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2AT_TR2AT_IN |  | CORRENTE NEUTRO | 0c75be3c-1cf7-4c14-aef4-095f01a38e6d | Current | FWB Trans | [6 empty] | FWB_TR2AT_TR2AT_TC |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR2AT_TR2AT_IN |  | FWB_AS_00028 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 266 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2AT_TR2AT_FREQ |  | FREQUENCIA | cb57471e-3511-439a-b5ca-92f7f60cc06b | Frequency | FWB Trans | [6 empty] | FWB_TR2AT_52-3_DJ |  | MeasuredValue | ABC | Hz | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR2AT_TR2AT_FREQ |  | FWB_AS_00034 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 256 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2BT_TR2BT_IN |  | CORRENTE NEUTRO | 7aca998d-d2db-4875-aa9c-b36686d6b1f3 | Current | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_TC |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR2BT_TR2BT_IN |  | FWB_AS_00038 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 270 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2BT_TR2BT_P |  | POTENCIA ATIVA | 089b026e-b8a0-4985-8def-1c0c5c06b919 | ActivePower | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_TC |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR2BT_TR2BT_P |  | FWB_AS_00042 | 20260414 | Analog | 1000 | 0 | FALSE |  |  |  | 260 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2BT_TR2BT_Q |  | POTENCIA REATIVA | 6334f45d-e23c-4dfb-938f-167946b1726d | ReactivePower | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_TC |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR2BT_TR2BT_Q |  | FWB_AS_00043 | 20260414 | Analog | 1000 | 0 | FALSE |  |  |  | 261 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2AT_TR2AT_VCA |  | TENSAO FASE CA | 02f9a4bd-03e1-4bac-96cc-c9875916f2a9 | Voltage | FWB Trans | [6 empty] | FWB_TR2AT_52-3_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR2AT_TR2AT_VCA |  | FWB_AS_00031 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 253 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2BT_TR2BT_FREQ |  | FREQUENCIA | eca492ed-f292-4b08-b6b1-bf817e406c44 | Frequency | FWB Trans | [6 empty] | FWB_TR2BT_52-07_DJ |  | MeasuredValue | ABC | Hz | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR2BT_TR2BT_FREQ |  | FWB_AS_00044 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 262 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2BT_TR2BT_IB |  | CORRENTE FASE B | dacda0d2-4238-4a6d-a306-cff656465764 | Current | FWB Trans | [6 empty] | FWB_TR2BT_TR2BT_TC |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TR2BT_TR2BT_IB |  | FWB_AS_00036 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 268 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2_TR2_TOLE |  | TEMPERATURA OLEO | 4980faec-2bf2-4f9e-a309-821d4dd230b6 | Temperature | FWB Trans | [6 empty] | FWB_TR2_TR2_TR |  | Custom | ABC | C | None | Read |  | Undirected | 0 | 0 | 100 | -1 | TOLE_95@85_0@0_Trans | UTR_FWB_1 | [9 empty] | FWB_TR2_TR2_TOLE |  | FWB_AS_00045 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 460 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL12_52-12_IB |  | IB | 7e4b7d98-13e8-44fc-9e3e-ad020d5cbfdd | Current | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL12_52-12_IB |  | FWB_AS_00050 | 20260415 | Analog | 1 | 0 | FALSE |  |  |  | 22 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL12_52-12_IN |  | IN | 6c95ecc7-8eae-49e7-8be4-317b2c324afc | Current | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL12_52-12_IN |  | FWB_AS_00052 | 20260415 | Analog | 1 | 0 | FALSE |  |  |  | 24 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL12_52-12_P |  | P | 838fea38-2c6c-4594-a312-632023b83ec2 | ActivePower | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL12_52-12_P |  | FWB_AS_00056 | 20260415 | Analog | 1 | 0 | FALSE |  |  |  | 28 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL12_52-12_VBC |  | VBC | 64863225-3915-4e3d-ac81-6fb8e1d97421 | Voltage | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL12_52-12_VBC |  | FWB_AS_00054 | 20260415 | Analog | 1 | 0 | FALSE |  |  |  | 26 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL12_52-12_INCC |  | IN DESARME | 1a92e6b5-94c4-4801-873e-79b5e02c36bc | Current | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | MeasuredValue | ABCN | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL12_52-12_INCC |  | FWB_AS_00061 | 20260415 | Analog | 1 | 0 | FALSE |  |  |  | 33 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL12_52-12_IC |  | IC | 143f07e6-c71d-4b5b-bdaf-a50c22e01d8c | Current | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL12_52-12_IC |  | FWB_AS_00051 | 20260415 | Analog | 1 | 0 | FALSE |  |  |  | 23 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL12_52-12_VCA |  | VCA | ec841a22-e75d-4f35-be49-0d40c4be0d48 | Voltage | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL12_52-12_VCA |  | FWB_AS_00055 | 20260415 | Analog | 1 | 0 | FALSE |  |  |  | 27 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL12_52-12_IBCC |  | IB DESARME | 9c7527e9-08aa-42d7-9456-694b68215add | Current | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | MeasuredValue | BC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL12_52-12_IBCC |  | FWB_AS_00059 | 20260415 | Analog | 1 | 0 | FALSE |  |  |  | 31 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL12_52-12_VAB |  | VAB | 8e986014-e97b-458d-8cf5-74407caaef41 | Voltage | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | V_24.2@23.9_21.9@21.6_Trans | UTR_FWB_1 | [9 empty] | FWB_AL12_52-12_VAB |  | FWB_AS_00053 | 20260415 | Analog | 1 | 0 | FALSE |  |  |  | 25 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL12_52-12_IACC |  | IA DESARME | 31008cd0-0fd2-49d4-8680-dbb0268a6792 | Current | FWB Distr | [6 empty] | FWB_AL12_52-12_DJ |  | MeasuredValue | AB | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL12_52-12_IACC |  | FWB_AS_00058 | 20260415 | Analog | 1 | 0 | FALSE |  |  |  | 30 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_VBC |  | VBC | 375c89fc-e3b0-495f-a323-3736edd39b7e | Voltage | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL13_52-13_VBC |  | FWB_AS_00067 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 46 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_IN |  | IN | 8bc878dd-06e3-4234-8e76-0c17775bc82c | Current | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL13_52-13_IN |  | FWB_AS_00065 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 44 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_INCC |  | IN DESARME | 5e88f91a-cafc-4f22-ad30-da3b7cd3d810 | Current | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | ABCN | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL13_52-13_INCC |  | FWB_AS_00074 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 53 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL14_52-14_IB |  | IB | 2e0f5e05-99e8-4337-a6a3-93cfb56c4799 | Current | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL14_52-14_IB |  | FWB_AS_00076 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 62 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_IA |  | IA | 2c2aae1e-2837-4b77-b81f-32fb6c74afbd | Current | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL13_52-13_IA |  | FWB_AS_00062 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 41 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_VAB |  | VAB | 2cae4437-836c-4b3c-b30f-f3305dfea126 | Voltage | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | V_24.2@23.9_21.9@21.6_Trans | UTR_FWB_1 | [9 empty] | FWB_AL13_52-13_VAB |  | FWB_AS_00066 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 45 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL14_52-14_ICCC |  | IC DESARME | a30064ab-5ad2-4637-a122-ea1a8402f59b | Current | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | MeasuredValue | AC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL14_52-14_ICCC |  | FWB_AS_00086 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 72 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_Q |  | Q | 07c62f6e-56ff-4ce3-9229-3efc7c5cf1cd | ReactivePower | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL13_52-13_Q |  | FWB_AS_00070 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 49 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_IBCC |  | IB DESARME | c2d8276f-d5a2-47db-98f6-f737d145bd93 | Current | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | BC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL13_52-13_IBCC |  | FWB_AS_00072 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 51 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL21_52-21_IA |  | IA | 589ecb24-47a7-41a6-bf5c-7f2121d771dc | Current | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL21_52-21_IA |  | FWB_AS_00101 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 101 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL14_52-14_IN |  | IN | 6f64c619-b149-4e74-b5a0-0a912669180e | Current | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL14_52-14_IN |  | FWB_AS_00078 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 64 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_VCA |  | VCA | 87a0dbd7-e11c-4d9b-9639-76cab61e82bb | Voltage | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL13_52-13_VCA |  | FWB_AS_00068 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 47 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL21_52-21_VAB |  | VAB | 35dae730-9a9c-4992-b9c5-acf676bcbd40 | Voltage | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | V_24.2@23.9_21.9@21.6_Trans | UTR_FWB_1 | [9 empty] | FWB_AL21_52-21_VAB |  | FWB_AS_00105 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 105 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL21_52-21_VBC |  | VBC | a2db9f0f-db8d-4fd5-8046-846afe0d7a26 | Voltage | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL21_52-21_VBC |  | FWB_AS_00106 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 106 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL21_52-21_IN |  | IN | 06d24d88-5978-4b98-920c-14caab01e76e | Current | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL21_52-21_IN |  | FWB_AS_00104 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 104 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL21_52-21_VCA |  | VCA | fce9f7d0-74da-443b-b8c1-f4d50df94560 | Voltage | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL21_52-21_VCA |  | FWB_AS_00107 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 107 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL21_52-21_Q |  | Q | f76dcc79-3b76-4aa6-966a-5e9be48575d7 | ReactivePower | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL21_52-21_Q |  | FWB_AS_00109 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 109 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL21_52-21_IACC |  | IA DESARME | 8b159aa6-9ced-47a1-8063-a4b81fc26172 | Current | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | MeasuredValue | AB | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL21_52-21_IACC |  | FWB_AS_00110 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 110 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL21_52-21_IBCC |  | IB DESARME | d61ea4fd-604e-4eeb-9bfd-263c65dcc544 | Current | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | MeasuredValue | BC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL21_52-21_IBCC |  | FWB_AS_00111 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 111 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL21_52-21_P |  | P | f58bad06-b6bd-4aa2-a1a0-d90e1381f906 | ActivePower | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL21_52-21_P |  | FWB_AS_00108 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 108 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL21_52-21_IB |  | IB | 223320c9-3fa3-4dcf-b687-d570df0addfa | Current | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL21_52-21_IB |  | FWB_AS_00102 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 102 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL21_52-21_INCC |  | IN DESARME | 199d298f-e585-45f6-8177-4fa4001c620b | Current | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | MeasuredValue | ABCN | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL21_52-21_INCC |  | FWB_AS_00113 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 113 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL22_52-22_IB |  | IB | 5229a34b-108b-49db-aea6-af80f83706f1 | Current | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL22_52-22_IB |  | FWB_AS_00115 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 122 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL22_52-22_IC |  | IC | 23d7e4d2-a7db-43aa-a0d4-7707a51b587c | Current | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL22_52-22_IC |  | FWB_AS_00116 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 123 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL22_52-22_IN |  | IN | fd6f8373-a20d-4d71-b8e3-bdfd466ac16d | Current | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL22_52-22_IN |  | FWB_AS_00117 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 124 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL22_52-22_VCA |  | VCA | 57804640-1590-48ea-b69c-4b13f90295eb | Voltage | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL22_52-22_VCA |  | FWB_AS_00120 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 127 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_P |  | P | 47ac438b-cfd0-4d64-91f9-47cc96f806e1 | ActivePower | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL13_52-13_P |  | FWB_AS_00069 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 48 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL22_52-22_P |  | P | 488c4b41-42c6-424c-adc7-36c12c0b35df | ActivePower | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL22_52-22_P |  | FWB_AS_00121 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 128 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL21_52-21_ICCC |  | IC DESARME | 985ac8cc-71ce-4822-95e5-356d46e0e5ef | Current | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | MeasuredValue | AC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL21_52-21_ICCC |  | FWB_AS_00112 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 112 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL22_52-22_VBC |  | VBC | 9bd5f23c-e75c-49ed-ba2d-29465b72b94b | Voltage | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL22_52-22_VBC |  | FWB_AS_00119 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 126 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL22_52-22_IACC |  | IA DESARME | e03c39af-60d0-40d6-b306-c72704f104a2 | Current | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | MeasuredValue | AB | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL22_52-22_IACC |  | FWB_AS_00123 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 130 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL22_52-22_ICCC |  | IC DESARME | a08835c3-1140-4584-9ffb-5d592f02bdd9 | Current | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | MeasuredValue | AC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL22_52-22_ICCC |  | FWB_AS_00125 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 132 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL22_52-22_Q |  | Q | dd32e61f-eafe-41b0-8cd4-8243e69f2fc5 | ReactivePower | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL22_52-22_Q |  | FWB_AS_00122 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 129 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL22_52-22_INCC |  | IN DESARME | b3d05201-0fd7-4f6c-aee9-972e73ecc759 | Current | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | MeasuredValue | ABCN | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL22_52-22_INCC |  | FWB_AS_00126 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 133 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL15_52-15_IC |  | IC | b2aaf43a-b054-4239-a048-307f9e3c6d61 | Current | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL15_52-15_IC |  | FWB_AS_00090 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 83 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL14_52-14_Q |  | Q | be5b2dfc-a327-47f7-ae1f-53aacc28072f | ReactivePower | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL14_52-14_Q |  | FWB_AS_00083 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 69 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL15_52-15_IA |  | IA | c3919821-e98b-4d7d-bd79-61cb2d5adca8 | Current | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL15_52-15_IA |  | FWB_AS_00088 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 81 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL15_52-15_IN |  | IN | da502133-a520-4141-9a38-b7e13191e90c | Current | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL15_52-15_IN |  | FWB_AS_00091 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 84 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL15_52-15_VAB |  | VAB | 9194728c-bf7b-4e1b-a1ef-ce7e2441552a | Voltage | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | V_24.2@23.9_21.9@21.6_Trans | UTR_FWB_1 | [9 empty] | FWB_AL15_52-15_VAB |  | FWB_AS_00092 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 85 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL15_52-15_VCA |  | VCA | 4cf0f202-e7f6-4cbd-8c47-9a81b7c92934 | Voltage | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL15_52-15_VCA |  | FWB_AS_00094 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 87 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL15_52-15_VBC |  | VBC | f79b14cc-e585-4bb1-91d7-89d80e8878d6 | Voltage | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL15_52-15_VBC |  | FWB_AS_00093 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 86 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL15_52-15_Q |  | Q | cc96ef88-de7c-409d-8110-15d8136cb4f9 | ReactivePower | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL15_52-15_Q |  | FWB_AS_00096 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 89 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL14_52-14_P |  | P | 40bc673f-11fb-4bf9-bdce-e32f57f157d4 | ActivePower | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL14_52-14_P |  | FWB_AS_00082 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 68 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL15_52-15_IBCC |  | IB DESARME | 43ffee6f-b8d8-41fa-87e4-612415477294 | Current | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | MeasuredValue | BC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL15_52-15_IBCC |  | FWB_AS_00098 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 91 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL15_52-15_IACC |  | IA DESARME | 7f240f17-2b90-47b7-b564-e9fc77c8d73a | Current | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | MeasuredValue | AB | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL15_52-15_IACC |  | FWB_AS_00097 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 90 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL15_52-15_ICCC |  | IC DESARME | 5fa3e140-aea2-454f-b49f-b7b33b703160 | Current | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | MeasuredValue | AC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL15_52-15_ICCC |  | FWB_AS_00099 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 92 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL24_52-24_IB |  | IB | 12f8f18b-1ce9-4793-a162-20d062d7aabc | Current | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL24_52-24_IB |  | FWB_AS_00141 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 362 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL24_52-24_IC |  | IC | 7bf53d0d-72df-495b-8020-14528f49a929 | Current | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL24_52-24_IC |  | FWB_AS_00142 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 363 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL24_52-24_IA |  | IA | 5f237fb1-3340-4a23-86e6-6365090bb89e | Current | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL24_52-24_IA |  | FWB_AS_00140 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 361 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL15_52-15_P |  | P | 4269d190-9151-447a-94df-5a18a740c02e | ActivePower | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL15_52-15_P |  | FWB_AS_00095 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 88 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL24_52-24_IN |  | IN | ba8c0436-983c-4575-80d1-1fea874e4a31 | Current | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL24_52-24_IN |  | FWB_AS_00143 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 364 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_IC |  | IC | abede076-17be-4459-aa3b-e64d8b9a1842 | Current | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL13_52-13_IC |  | FWB_AS_00064 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 43 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL24_52-24_VAB |  | VAB | 02a2fc16-7b63-4bff-9273-25aae746b245 | Voltage | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | V_24.2@23.9_21.9@21.6_Trans | UTR_FWB_1 | [9 empty] | FWB_AL24_52-24_VAB |  | FWB_AS_00144 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 365 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL24_52-24_VBC |  | VBC | f9bb7ea1-7f54-4847-8903-cf85c1e058c7 | Voltage | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL24_52-24_VBC |  | FWB_AS_00145 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 366 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL24_52-24_VCA |  | VCA | ed8590e8-9c73-4d36-8e19-9099017e22e8 | Voltage | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL24_52-24_VCA |  | FWB_AS_00146 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 367 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL24_52-24_IACC |  | IA DESARME | 0c7b79c9-74b8-4d00-8cb5-b49a0457c6c3 | Current | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | MeasuredValue | AB | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL24_52-24_IACC |  | FWB_AS_00149 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 370 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL24_52-24_IBCC |  | IB DESARME | 35f8c0f4-d04f-4bca-b5d3-bedb7bb6c7e1 | Current | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | MeasuredValue | BC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL24_52-24_IBCC |  | FWB_AS_00150 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 371 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL24_52-24_ICCC |  | IC DESARME | 1775a15e-1f18-4f78-881a-8ddd868aa9ba | Current | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | MeasuredValue | AC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL24_52-24_ICCC |  | FWB_AS_00151 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 372 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL22_52-22_IBCC |  | IB DESARME | aaf6532d-4fd3-486b-826f-4bd5fda8de50 | Current | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | MeasuredValue | BC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL22_52-22_IBCC |  | FWB_AS_00124 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 131 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL24_52-24_INCC |  | IN DESARME | f8ed3e01-4621-4dc0-91ef-33ac48a40f88 | Current | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | MeasuredValue | ABCN | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL24_52-24_INCC |  | FWB_AS_00152 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 373 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL25_52-25_IA |  | IA | fbbeabc6-cb23-4e46-bf22-a2c66956e025 | Current | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL25_52-25_IA |  | FWB_AS_00153 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 381 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL25_52-25_IB |  | IB | 5ee19963-0b5c-4993-96b5-e6c5e48bf271 | Current | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL25_52-25_IB |  | FWB_AS_00154 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 382 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL15_52-15_IB |  | IB | 5f47ba1d-9c7c-40e8-823b-9c9fba29cffb | Current | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL15_52-15_IB |  | FWB_AS_00089 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 82 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL25_52-25_IN |  | IN | 8ad22ce4-fcbc-4ac1-8535-92987c71ba8f | Current | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL25_52-25_IN |  | FWB_AS_00156 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 384 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL24_52-24_Q |  | Q | d1e7cb99-1f60-4ee6-abab-6b213b67d12e | ReactivePower | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL24_52-24_Q |  | FWB_AS_00148 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 369 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL25_52-25_VBC |  | VBC | 1bb3af65-31c5-4e3f-abc8-24deb534f172 | Voltage | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL25_52-25_VBC |  | FWB_AS_00158 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 386 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL25_52-25_VCA |  | VCA | f9a7d211-2fcd-4a70-aa5a-13afb761d480 | Voltage | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL25_52-25_VCA |  | FWB_AS_00159 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 387 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL25_52-25_P |  | P | acc137b3-b182-4771-b9d2-0a5bcc68818a | ActivePower | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL25_52-25_P |  | FWB_AS_00160 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 388 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL25_52-25_Q |  | Q | 5d78bff7-d1e2-41da-9aa4-f725748fc0e1 | ReactivePower | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL25_52-25_Q |  | FWB_AS_00161 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 389 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL25_52-25_IACC |  | IA DESARME | 2cff367a-07c4-434b-8143-f9e540f32210 | Current | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | MeasuredValue | AB | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL25_52-25_IACC |  | FWB_AS_00162 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 390 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL25_52-25_IBCC |  | IB DESARME | ac30cfd9-f5ef-4789-ac9c-e659c8f4f653 | Current | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | MeasuredValue | BC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL25_52-25_IBCC |  | FWB_AS_00163 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 391 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL25_52-25_ICCC |  | IC DESARME | 1adc89fb-4a2c-4c29-b00c-08677bd4878a | Current | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | MeasuredValue | AC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL25_52-25_ICCC |  | FWB_AS_00164 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 392 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL25_52-25_INCC |  | IN DESARME | c0f238b9-6525-4528-b9b3-e7aae658b6b6 | Current | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | MeasuredValue | ABCN | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL25_52-25_INCC |  | FWB_AS_00165 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 393 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL15_52-15_INCC |  | IN DESARME | 53f465ff-e74a-411f-9027-8e89b9e14845 | Current | FWB Distr | [6 empty] | FWB_AL15_52-15_DJ |  | MeasuredValue | ABCN | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL15_52-15_INCC |  | FWB_AS_00100 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 93 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL25_52-25_VAB |  | VAB | f8bb3455-3f2c-4177-a637-490867fd51a4 | Voltage | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | V_24.2@23.9_21.9@21.6_Trans | UTR_FWB_1 | [9 empty] | FWB_AL25_52-25_VAB |  | FWB_AS_00157 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 385 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL24_52-24_P |  | P | 79d360d2-c207-40fc-a72c-c331838e10dc | ActivePower | FWB Distr | [6 empty] | FWB_AL24_52-24_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL24_52-24_P |  | FWB_AS_00147 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 368 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_IACC |  | IA DESARME | bc7cc5a9-45cd-4477-a759-be4b7c46e332 | Current | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | AB | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL13_52-13_IACC |  | FWB_AS_00071 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 50 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_ICCC |  | IC DESARME | 33f70dde-6983-4700-99ea-3182a3c8d7ea | Current | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | AC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL13_52-13_ICCC |  | FWB_AS_00073 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 52 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL14_52-14_VAB |  | VAB | 07b769a2-995f-430f-b857-b8c295eb22fe | Voltage | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | V_24.2@23.9_21.9@21.6_Trans | UTR_FWB_1 | [9 empty] | FWB_AL14_52-14_VAB |  | FWB_AS_00079 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 65 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL22_52-22_IA |  | IA | e8d4f005-c97f-4d61-a1fd-be3dbe801f9a | Current | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL22_52-22_IA |  | FWB_AS_00114 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 121 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL25_52-25_IC |  | IC | d0713bfe-35ae-40b1-b41f-3b021da9c0ba | Current | FWB Distr | [6 empty] | FWB_AL25_52-25_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL25_52-25_IC |  | FWB_AS_00155 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 383 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL14_52-14_IBCC |  | IB DESARME | 2a0bf78d-a1a5-426d-9c08-e671486d4558 | Current | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | MeasuredValue | BC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL14_52-14_IBCC |  | FWB_AS_00085 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 71 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL14_52-14_INCC |  | IN DESARME | f5e9b2e7-cdaf-4bb2-ac78-ca11da429cdd | Current | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | MeasuredValue | ABCN | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL14_52-14_INCC |  | FWB_AS_00087 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 73 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL21_52-21_IC |  | IC | e8910244-ef17-4698-8d25-017d21961a3b | Current | FWB Distr | [6 empty] | FWB_AL21_52-21_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL21_52-21_IC |  | FWB_AS_00103 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 103 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL14_52-14_IC |  | IC | 45b9c3b1-549d-4b90-9d64-88abdc64122b | Current | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL14_52-14_IC |  | FWB_AS_00077 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 63 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL14_52-14_VCA |  | VCA | 46798657-2b62-4086-b53f-5dc3a3780284 | Voltage | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL14_52-14_VCA |  | FWB_AS_00081 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 67 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL14_52-14_VBC |  | VBC | d815066a-6fb8-4bf1-a62e-6ffcafae6101 | Voltage | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_AL14_52-14_VBC |  | FWB_AS_00080 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 66 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL14_52-14_IA |  | IA | 2dbe8d26-4f11-45b4-9b7e-606ff8a46372 | Current | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL14_52-14_IA |  | FWB_AS_00075 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 61 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL14_52-14_IACC |  | IA DESARME | d873f2a2-d082-4f6d-9c47-14ccb984a45f | Current | FWB Distr | [6 empty] | FWB_AL14_52-14_DJ |  | MeasuredValue | AB | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL14_52-14_IACC |  | FWB_AS_00084 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 70 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL22_52-22_VAB |  | VAB | 73c9d5d2-c27c-4e0f-83c3-6c4cbbce1ccb | Voltage | FWB Distr | [6 empty] | FWB_AL22_52-22_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | V_24.2@23.9_21.9@21.6_Trans | UTR_FWB_1 | [9 empty] | FWB_AL22_52-22_VAB |  | FWB_AS_00118 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 125 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_IB |  | IB | 1bd361df-c81b-47de-85e6-aa8ae8484470 | Current | FWB Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_AL13_52-13_IB |  | FWB_AS_00063 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 42 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF1_24-1_IA |  | IA | e1353706-a3d5-46d7-87ac-e290ca70cb85 | Current | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_TRF1_24-1_IA |  | FWB_AS_00166 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 161 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF1_24-1_IB |  | IB | 26eb2554-68d1-4494-9a6d-824d59197640 | Current | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_TRF1_24-1_IB |  | FWB_AS_00167 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 162 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF1_24-1_IC |  | IC | 83dcff96-1316-4ab5-9405-32b1a63f9dd6 | Current | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_TRF1_24-1_IC |  | FWB_AS_00168 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 163 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF1_24-1_P |  | P | d75dd7f8-e749-4aab-93b9-1ded9ae12211 | ActivePower | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TRF1_24-1_P |  | FWB_AS_00173 | 20260416 | Analog | 1000 | 0 | FALSE |  |  |  | 168 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF1_24-1_Q |  | Q | 1da1d228-0b92-4ddd-814e-1f26d848baa6 | ReactivePower | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TRF1_24-1_Q |  | FWB_AS_00174 | 20260416 | Analog | 1000 | 0 | FALSE |  |  |  | 169 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF1_24-1_IBCC |  | IB DESARME | 273f3f1a-c7e1-474c-97d4-e22014421307 | Current | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | MeasuredValue | BC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_TRF1_24-1_IBCC |  | FWB_AS_00176 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 171 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF2_24-2_IC |  | IC | 9b6822f2-c258-48d0-99dc-674328aa8587 | Current | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_TRF2_24-2_IC |  | FWB_AS_00181 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 183 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF2_24-2_IN |  | IN | c6e55bcd-b9cf-4915-be6d-3e3a03da08b4 | Current | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_TRF2_24-2_IN |  | FWB_AS_00182 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 184 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF2_24-2_IA |  | IA | d577108e-e050-4e78-a563-46daf715c49d | Current | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_TRF2_24-2_IA |  | FWB_AS_00179 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 181 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF1_24-1_VCA |  | VCA | da4f63a0-99e4-4a57-85c8-d4c5894d976d | Voltage | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TRF1_24-1_VCA |  | FWB_AS_00172 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 167 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF2_24-2_ICCC |  | IC DESARME | d53e2d32-a310-442c-aa98-0e4848a0f67f | Current | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | MeasuredValue | AC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_TRF2_24-2_ICCC |  | FWB_AS_00190 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 192 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF2_24-2_Q |  | Q | e2004b13-8dd4-49e2-b903-f8dfb7da19dd | ReactivePower | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TRF2_24-2_Q |  | FWB_AS_00187 | 20260416 | Analog | 1000 | 0 | FALSE |  |  |  | 189 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF2_24-2_IACC |  | IA DESARME | b9719e84-61d0-4100-806b-1a417928abb8 | Current | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | MeasuredValue | AB | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_TRF2_24-2_IACC |  | FWB_AS_00188 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 190 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF2_24-2_VCA |  | VCA | cff3bd17-d993-493d-8856-96d15ef89041 | Voltage | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TRF2_24-2_VCA |  | FWB_AS_00185 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 187 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF1_24-1_VBC |  | VBC | cc5bfcf7-ab6d-4870-89b1-9ca47c53c971 | Voltage | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TRF1_24-1_VBC |  | FWB_AS_00171 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 166 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF1_24-1_IACC |  | IA DESARME | 15f55e41-6ac8-41a8-a591-18c4997c79e2 | Current | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | MeasuredValue | AB | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_TRF1_24-1_IACC |  | FWB_AS_00175 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 170 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF2_24-2_INCC |  | IN DESARME | e6f628e0-f855-438a-8381-28b479ca64a2 | Current | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | MeasuredValue | ABCN | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_TRF2_24-2_INCC |  | FWB_AS_00191 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 193 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF2_24-2_VBC |  | VBC | 125b90bc-35ec-48b9-bea4-9206b6884b5e | Voltage | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TRF2_24-2_VBC |  | FWB_AS_00184 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 186 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF2_24-2_P |  | P | cf4e8d38-6474-4c05-ae75-972b4cae58ec | ActivePower | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_TRF2_24-2_P |  | FWB_AS_00186 | 20260416 | Analog | 1000 | 0 | FALSE |  |  |  | 188 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF1_24-1_IN |  | IN | e8c62ce9-eacf-41a9-8d2d-b70d4233d019 | Current | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_TRF1_24-1_IN |  | FWB_AS_00169 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 164 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF1_24-1_VAB |  | VAB | d4ecf29a-1877-42f8-9cb6-cf0852e3e191 | Voltage | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | V_24.2@23.9_21.9@21.6_Trans | UTR_FWB_1 | [9 empty] | FWB_TRF1_24-1_VAB |  | FWB_AS_00170 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 165 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF1_24-1_ICCC |  | IC DESARME | 4dd0a802-ded3-4d21-88e1-c65ef27f943a | Current | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | MeasuredValue | AC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_TRF1_24-1_ICCC |  | FWB_AS_00177 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 172 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF2_24-2_IB |  | IB | d6507ffb-ab3d-413a-bf42-9fc62512d8c5 | Current | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_TRF2_24-2_IB |  | FWB_AS_00180 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 182 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF2_24-2_IBCC |  | IB DESARME | 63296f07-406a-425c-8bc2-19dda26fbab7 | Current | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | MeasuredValue | BC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_TRF2_24-2_IBCC |  | FWB_AS_00189 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 191 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF2_24-2_VAB |  | VAB | 9fda831c-34d5-4927-a8a7-2ca5846c5264 | Voltage | FWB Distr | [6 empty] | FWB_TRF2_24-2_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | V_24.2@23.9_21.9@21.6_Trans | UTR_FWB_1 | [9 empty] | FWB_TRF2_24-2_VAB |  | FWB_AS_00183 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 185 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TRF1_24-1_INCC |  | IN DESARME | 03f6d24f-d02d-4e62-9004-5364dc6f4f68 | Current | FWB Distr | [6 empty] | FWB_TRF1_24-1_DJ |  | MeasuredValue | ABCN | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_TRF1_24-1_INCC |  | FWB_AS_00178 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 173 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_IB_52-16_IA |  | IA | b5c546e0-23e6-4a5b-9f69-f2c34072bb5d | Current | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_IB_52-16_IA |  | FWB_AS_00192 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 201 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_IB_52-16_IB |  | IB | 43e6229c-c0e0-4fe0-aaec-fe750c214125 | Current | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_IB_52-16_IB |  | FWB_AS_00193 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 202 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_IB_52-16_P |  | P | 81be000b-ddba-43cd-8c92-2ea6cf050264 | ActivePower | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_IB_52-16_P |  | FWB_AS_00199 | 20260416 | Analog | 1000 | 0 | FALSE |  |  |  | 208 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_IB_52-16_INCC |  | IN DESARME | c28e9564-cd6a-4fea-b553-2616b3e682d7 | Current | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | MeasuredValue | ABCN | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_IB_52-16_INCC |  | FWB_AS_00204 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 213 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_IB_52-16_IACC |  | IA DESARME | 18874a3d-bbc6-432f-a863-42d903309443 | Current | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | MeasuredValue | AB | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_IB_52-16_IACC |  | FWB_AS_00201 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 210 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_IB_52-16_IBCC |  | IB DESARME | 6bf25f7e-6cce-4168-b696-1e558215a4e0 | Current | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | MeasuredValue | BC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_IB_52-16_IBCC |  | FWB_AS_00202 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 211 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_IB_52-16_IN |  | IN | 1f3db5ee-4431-44f9-9755-c87c654dae60 | Current | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_IB_52-16_IN |  | FWB_AS_00195 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 204 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_IB_52-16_VBC |  | VBC | 2f28953a-83fc-43c8-a5de-d81766303af1 | Voltage | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_IB_52-16_VBC |  | FWB_AS_00197 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 206 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_IB_52-16_IC |  | IC | d23525c6-48fa-48cb-b115-8bbcbab4db47 | Current | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_IB_52-16_IC |  | FWB_AS_00194 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 203 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_IB_52-16_VCA |  | VCA | 2bb08fcd-f979-4eb8-8187-258abab721b4 | Voltage | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_IB_52-16_VCA |  | FWB_AS_00198 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 207 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_IB_52-16_ICCC |  | IC DESARME | d6113106-9237-401c-a192-b64b8ffab75f | Current | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | MeasuredValue | AC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_IB_52-16_ICCC |  | FWB_AS_00203 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 212 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_IB_52-16_Q |  | Q | 5322c90a-06d6-46e4-bc31-5d22c79c8b52 | ReactivePower | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_IB_52-16_Q |  | FWB_AS_00200 | 20260416 | Analog | 1000 | 0 | FALSE |  |  |  | 209 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_IB_52-16_VAB |  | VAB | c096957f-4591-4e0a-97f2-ebe8c4d0dce0 | Voltage | FWB Trans | [6 empty] | FWB_IB_52-16_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | V_24.2@23.9_21.9@21.6_Trans | UTR_FWB_1 | [9 empty] | FWB_IB_52-16_VAB |  | FWB_AS_00196 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 205 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_BC1_52-10_IA |  | IA | a4910490-4507-4abf-b5c6-91048fe388bd | Current | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_BC1_52-10_IA |  | FWB_AS_00205 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 281 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_BC1_52-10_IB |  | IB | edfb92a8-a540-401e-a8d5-d1347d96f56f | Current | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_BC1_52-10_IB |  | FWB_AS_00206 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 282 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_BC1_52-10_VAB |  | VAB | 8fb93dc0-c0ff-4b68-95f4-a16e8f25c499 | Voltage | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | V_24.2@23.9_21.9@21.6_Trans | UTR_FWB_1 | [9 empty] | FWB_BC1_52-10_VAB |  | FWB_AS_00209 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 285 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_BC1_52-10_IN |  | IN | bc5f9457-e6ba-42d7-a5d0-2cb57d1e8305 | Current | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_BC1_52-10_IN |  | FWB_AS_00208 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 284 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_BC1_52-10_IACC |  | IA DESARME | 1cb2185e-23e6-4bfe-8e00-db1d5856ea68 | Current | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | MeasuredValue | AB | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_BC1_52-10_IACC |  | FWB_AS_00214 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 290 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_BC1_52-10_ICCC |  | IC DESARME | 9c570e75-ec37-46db-96d3-7d55e4efea2b | Current | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | MeasuredValue | AC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_BC1_52-10_ICCC |  | FWB_AS_00216 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 292 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_BC1_52-10_P |  | P | 6f8a8d87-7f6d-4938-9949-e8617161eecb | ActivePower | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_BC1_52-10_P |  | FWB_AS_00212 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 288 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_SE_BARR_VCC |  | VCC | bb8dde62-071e-49f1-94bb-a94bc84a3aff | Unitless | FWB Trans | [6 empty] | SCD_SE_RET1_RET |  | Custom | ABC | Default | None | Read |  | Undirected | 0 | -3.4028e+38 | 3.4028e+38 | -1 | VCC_142@138_115@110_Trans | UTR_FWB_1 | [9 empty] | FWB_SE_BARR_VCC |  | cf6e91bb-c1ef-4811-a84b-6db368891663 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 420 | FALSE
FWB_LTPNT_LTPNT_VB |  | TENSAO FASE B | 7afe7850-25c1-4c59-bdaa-5506fa642024 | Voltage | FWB Trans | [6 empty] | FWB_LTPNT_LTPNT_TP |  | MeasuredValue | B | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_LTPNT_LTPNT_VB |  | 5694f106-6412-428d-850c-7cd1d1b381bf | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 423 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_BC1_52-10_Q |  | Q | 495debd1-823f-4f4e-80ef-ac25f6d36631 | ReactivePower | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_BC1_52-10_Q |  | FWB_AS_00213 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 289 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_SE_RET1_VCC |  | VCC | 36200f84-76ca-4236-b942-9c5360826265 | Unitless | FWB Trans | [6 empty] | SCD_SE_RET1_RET |  | Custom | ABC | Default | None | Read |  | Undirected | 0 | -3.4028e+38 | 3.4028e+38 | -1 | VCC_142@138_115@110_Trans | UTR_FWB_1 | [9 empty] | FWB_SE_RET1_VCC |  | 7ae82a5e-a02e-4dab-8a05-ac73bbd2cef5 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 421 | FALSE
FWB_BC1_52-10_VBC |  | VBC | f0a2464b-8dc4-4df2-a67d-810d1f3a6c1d | Voltage | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_BC1_52-10_VBC |  | FWB_AS_00210 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 286 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_BC1_52-10_VCA |  | VCA | 4ccd4d56-4757-4235-b89a-277e55400167 | Voltage | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [9 empty] | FWB_BC1_52-10_VCA |  | FWB_AS_00211 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 287 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_BC1_52-10_INCC |  | IN DESARME | 05f1afc7-ac64-4da1-9afc-d99c06d4bfd8 | Current | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | MeasuredValue | ABCN | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_BC1_52-10_INCC |  | FWB_AS_00217 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 293 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_SE_RET2_VCC |  | VCC | 24a246d8-bcab-4f5e-b71f-23ed882fedc4 | Unitless | FWB Trans | [6 empty] | FWB_SE_RET2_RET |  | Custom | ABC | Default | None | Read |  | Undirected | 0 | -3.4028e+38 | 3.4028e+38 | -1 | VCC_142@138_115@110_Trans | UTR_FWB_1 | [9 empty] | FWB_SE_RET2_VCC |  | 17f59e4b-c5f1-40ee-8881-f0b892c39075 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 422 | FALSE
FWB_BC1_52-10_IBCC |  | IB DESARME | f9f52050-66f2-4e10-a7dd-778eee357745 | Current | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | MeasuredValue | BC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_BC1_52-10_IBCC |  | FWB_AS_00215 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 291 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_BC1_52-10_IC |  | IC | abf1d191-040c-4e26-9b24-083f5bdbf926 | Current | FWB Trans | [6 empty] | FWB_BC1_52-17_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [9 empty] | FWB_BC1_52-10_IC |  | FWB_AS_00207 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 283 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0

## DNP3_DiscreteAnalog
Signal Details | [22 empty] | Remote Points
DSIGNAL | [22 empty] | REMOTEPOINT | [17 empty] | APROCESSING
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | MEASUREMENT_TYPE | IDOBJ_AORGROUP | SIGNAL_DEVICEMAPPING | [7 empty] | DSIGNAL_TYPE | MEASUREMENT_PHASE | MEASUREMENT_SIDE | SIGNAL_DIRECTION | SIGNAL_ANNUALSCH | DSIGNAL_NORMALVALUE | DSIGNAL_MAPPING | DSIGNAL_DOMCATALOG | MEASUREMENT_PSR | IDOBJ_NAME | DELETE | IDOBJ_CUSTOMID | IDOBJ_ALIAS | REMOTEPOINT_TYPE | REMOTEPOINT_SCALING | REMOTEPOINT_INTERCEPT | REMOTEPOINT_ADCFAIL | REMOTEOUTPUT_CMDTIMEOUT | REMOTEOUTPUT_SBOMODE | REMOTEOUTPUT_SPTOL | REMOTEINPUTDNP3_INCOORDS¦REMOTEOUTPUTDNP3_INCOORDS | REMOTEINPUTDNP3_OUTREGISTER¦REMOTEOUTPUTDNP3_OUTREGISTER | AOUTPUTDNP3_OUTTYPE | REMOTEOUTPUTDNP3_OUTCOORDS | COUNTERDNP3_ENABLEROLLOVER | COUNTERDNP3_ROLLOVER | COUNTERDNP3_RESET | APROCESSING_LOCALDBCHECK | APROCESSING_USERELATIVEDB | APROCESSING_DEADBANDTYPE | APROCESSING_DEADBAND | APROCESSING_ZEROCLAMPINGDB | APROCESSING_LINEARFILTER | APROCESSING_LFFACTOR
Signal Name | Delete | Signal Alias | Signal Custom ID | Measurement Type | Signal AOR Group | Substation | Feeder | Feeder Object | Bank | Bay | Device | Device Mapping | Description | Signal Type | Phases | Side | Direction | Annual Schedule | Normal Value | Message Mapping | DOM Catalog | Remote Unit | Remote Point Name | Delete Remote Point | Remote Point Custom ID | Remote Point Alias | Remote Point Type | Scaling Factor | Intercept | ADC Fail | Command Timeout [s] | Commanding Mode | Setpoint Tolerance | Input Coordinates | Output Register | Output Data Type | Output Coordinates | Enable Rollover | Rollover Value | With Reset | Advanced Processing - Local Deadband Check | Advanced Processing - Use Relative Deadband | Deadband Type | Advanced Processing - Deadband | Advanced Processing - Zero Clamping Deadband | Advanced Processing - Apply Linear Filter | Advanced Processing - Linear Filter Factor
FWB_TR1_TR1_TAP |  | TAP | ca87615c-f020-45ef-a889-66b7fab6912f | Discrete | FWB Trans | [6 empty] | FWB_TR1_TR1_COMTAP |  | TapPosition | ABC | None | Read |  | 9 |  |  | UTR_FWB_1 | FWB_TR1_TR1_TAP |  | FWB_DA_00001 | 20260410 | Analog | 1 | 0 | FALSE |  |  |  | 400 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_TR2_TR2_TAP |  | TAP | 5ef69482-83be-4956-b478-2a1c4b60d421 | Discrete | FWB Trans | [6 empty] | FWB_TR2_TR2_COMTAP |  | TapPosition | ABC | None | Read |  | 9 |  |  | UTR_FWB_1 | FWB_TR2_TR2_TAP |  | FWB_DA_00002 | 20260414 | Analog | 1 | 0 | FALSE |  |  |  | 401 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0

## CalculationCode
Calculation Code
CALCCODE
IDOBJ_NAME | DELETE | PSR_LOCATION | CALCCODE_SHARED | CALCCODE_ROUTINE
Name | Delete | Description | Shared | Code

## CalculationParameter
Calculation Parameters
CALCPARAM
IDOBJ_NAME | CALCARG_PARAMTYPE | CALCARG_ISOUTPUT | CALCARG_CALCULATION
Name | Data Type | Output | Calculation

## Calculations
Calculation
CALCULATION
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_AORGROUP | EQUIPMENT_CONT |  | CALCULATION_TIMEOUT | CALCULATION_CODE | CALCULATION_SCHEDULE
Name | Delete | Alias | AOR Group | Container Name | Container Custom ID | Execution Timeout [s] | Code Name | Schedule

## ConstantCalculationArgument
Calculation Arguments
CALCCONSTARG
CALCARG_CALCULATION | CALCARG_PARAM | CALCCONSTARG_STRING
Calculation | Calculation Parameter | Value

## SignalCalculationArgument
Signal Calculation Arguments
CALCSIGNALARG
CALCARG_CALCULATION | CALCARG_PARAM | CALCSIGNALARG_SIGNAL | CALCSIGNALARG_INPUTTRIGGER | CALCSIGNALARG_DEADBAND
Calculation | Calculation Parameter | Signal Custom ID | Input Trigger | Deadband