## Info
File name: | Telemetry Data Template File
File created: | 06/26/2026 10:16:49
User: | rgeprod\rafael.weber
Location(s):
Document Number:
Revision:
Legend
DMSMatchingTemplateInfo | Sheet containing supported ADMS types and attributes
RTUs | Configuration of Remote Terminal Units, Terminal Servers and Modem Banks
CommLInks | Configuration of TCP/IP based communication links
Modem | Modem configuration
ModemLinks | Configuration of Modem Links
DiscreteSignals | Configuration of discrete signals attached to a discrete type of remote points
AnalolgSignals | Configuration of analog signals attached to analog or rate (accumulator) type of remote points
Discrete-AnalogSignalTypes | Configuration of discrete signals attached to a analog or rate (accumulator) point type of remote poins (e.g. tap position signal types)
ScanGroups | Scan group configuration typical for serial based protocols (DNP3, VanComm, Series5...)
ICCP_RemoteControlCenters | Configuration of ICCP Remote Control Centers
ICCP_DataSetTransferSet | Configuration of ICCP Data Sets Transfer Sets
ICCP_NetworkConfigurationInfo | Configuration of network and security parameters for communication with the RCC
ServerDiscreteSignals | List of discrete signals served to the remote control center or SCADA master
ServerAnalogSignals | List of analog signals served to the remote control center or SCADA master
Note Catalog | Configuration of applicable types of note cataogs
Alarm Catalog | Configuration of Alarm catalog e.g. alarm text, alarm cause, priority (severity)
Event Catalog | Configuration of Event catalog e.g. event text, priority (severity)
Alarm Limits | Configuration of Alarm Limits for a specific measurement type, including reasonability checks and references to return-to-normal and high/low alarm limit catalogs
Limit Sets | Configuration of applicable limit sets and deadbands associated with an Alarm Limit
Tag Catalog | Configuration of applicable types of tags within the utility
Message Mappings | Message Mapping configuration - mapping of each possible discrete signal value (state) to a text message and alarm catalog associated with the state
DOM Catalog | Device operation monitoring - specifies criteria for alarm generation based on monitoring of cumulative switchgear operations

## DMSMatchingTemplateInfo (hidden)
YesNo | TrueFalse | AlarmEventCause | AlarmSeverity | MeasurementType | TagSemantics | DMSType | DiscreteSignalType | AbnormalState | PhaseCode | WindingType | SignalDirection | AnalogSignalType | UnitSymbol | FlowDirection | RemoteUnitType | TimeZone | RedundancyBehaviorType | SOEGroup | ProtocolTypeConitel | ScanTypeConitel | RemotePointType | OperateType | DiscreteInputTypeConitel | SectionConitel | DiscreteOutputDataTypeConitel | CommandTypeConitel | FunctionCodeConitel | AnalogInputTypeConitel | DeadbandDataType | DNP3Scan | TimeSyncMode |  | DNP3ConfirmMode | DNP3ObjectGroup | DNP3InputType | DNP3OutputType | ControlCode | DNP3Variation | DNP3SlaveEvent | DNP3SlaveDiscreteInputDataType | DNP3SlaveClassData | DNP3SlaveAnalogInputDataType | DNP3SlaveCounterDataType | IccpVersion | IccpBlocks | ConnectionRole | ServiceRole | AuthenticationMode | DstsType | IccpScope | IccpDataValueType | IECCounterInterrogationType | IECClockSyncMode | OctetSize | IEC101LinkMode | IEC101ConfirmMode | ModemCallType | ModemCommandType | BaudRate | IECDiscreteType | IECCommandQualifier | CommandState | IECAnalogType | IECRateType | ScanTypeMD3 | DiscreteInputModuleTypeMD3 | DiscreteInputDataTypeMD3 | DiscreteOutputTypeMD3 | DiscreteOutputDataTypeMD3 | CmdTypeMD3 | AnalogInputModuleTypeMD3 | AnalogInputDataTypeMD3 | AnalogOutputTypeMD3 | ModbusByteOrder | ModbusTransmissionMode | ModbusRegisterType | ModbusDiscreteOutputType | ModbusAnalogType | SecurityCodeSeries5 | ScanTypeSeries5 | DiscreteTypeSeries5 | ScanTypeVanComm | DiscreteInputTypeVanComm | DiscreteOutputTypeVanComm | AnalogTypeVanComm | CalculationParamType | InputTriggerType | RemoteUnitType | OperateType | RemotePointType | RemotePointType | RemotePointType | SignalDirection | MeasurementType | RemotePointType | OperateType | DNP3InputType | RemotePointType | OperateType | RemotePointType | SignalDirection | OperateType | MeasurementType | RemotePointType | OperateType | RemotePointType | OperateType | RemoteUnitType | RemoteUnitType | RemotePointType | IccpDataValueType | RemotePointType | IccpDataValueType | RemotePointType | SignalDirection | IccpDataValueType | MeasurementType | IccpDataValueType | IccpDataValueType | RemoteUnitType | OctetSize | OctetSize | OctetSize | OctetSize | BaudRate | OctetSize | RemotePointType | IECDiscreteType | IECDiscreteType | RemotePointType | IECAnalogType | RemotePointType | SignalDirection | MeasurementType | IECAnalogType | RemotePointType | IECDiscreteType | IECDiscreteType | RemotePointType | IECAnalogType | RemoteUnitType | OctetSize | RemoteUnitType | RemotePointType | IECDiscreteType | IECDiscreteType | RemotePointType | IECAnalogType | IECAnalogType | RemotePointType | SignalDirection | IECAnalogType | IECAnalogType | MeasurementType | RemotePointType | RemotePointType | RemotePointType | SignalDirection | MeasurementType | RemotePointType | RemotePointType | ModbusRegisterType | RemotePointType | SignalDirection | ModbusRegisterType | MeasurementType | RemotePointType | RemotePointType | RemotePointType | SignalDirection | MeasurementType | RemotePointType | RemotePointType | RemotePointType | SignalDirection | MeasurementType | CalculationParamType
No | TRUE | ApplicationAlarm | Severidade 16 | Unitless | DoNotOperatorClose | SUBSTATION | Custom | Normal | Unknown | None | Read | Custom | Default | Undirected | RTU | (UTC-12:00) International Date Line West | PrioritizeCostFactor | Group07 | Conitel2025 | Scan | Analog | DirectOperate | SingleBit | SectionA | SingleCoord | TripClose | Trip | TwelveBitSignedMagnitude | Int32 | Class0 | LAN | None | Never | BinaryInput | SingleBit | SingleCoord | Nul | Empty | WithoutTime | BinaryInputPackedFormat | Class1 | Int32WithFlag | Int32WithFlag | Version1996 | Block1 | Outgoing | Client | None | ManualRBE | Vcc | Unknown | CounterRead | SyncOnly | OneOctet | Unbalanced | Sometimes | DialOut | BaudRate | B100 | IECNone | UseDefault | On | IECShortNormalized | IECRateTimestamp | AnalogUnconditional | DigitalInputModuleDCM | SingleBit | RaiseLower | SingleCoord | Trip | AnalogInputModule | TwelveBitSignedMagnitude | AOMType | LittleEndian | TCP | Coil | SingleCoord | Short | LRC8bit | ExceptionScan | SingleCoord | AnalogScan | MomentaryStatus | SingleCoord | Signed | Bool | None | RTU | DirectOperate | Status | Analog | Analog | Read | Discrete | Status | DirectOperate | SingleBit | Analog | DirectOperate | Analog | Read | DirectOperate | Discrete | Status | DirectOperate | Analog | DirectOperate | ControlCenter | ControlCenter | Status | State | Analog | Real | Analog | Read | Real | Discrete | State | Real | RTU | OneOctet | OneOctet | OneOctet | OneOctet | B9600 | OneOctet | Status | IECSingleBit | IECSingleBit | Analog | IECShortNormalized | Analog | Read | Discrete | IECShortNormalized | Status | IECSingleBit | IECSingleBit | Analog | IECShortNormalized | RTU | OneOctet | RTU | Status | IECSingleBit | IECSingleBit | Analog | IECShortNormalized | IECShortNormalized | Analog | Read | IECShortNormalized | IECShortNormalized | Discrete | Status | Analog | Analog | Read | Discrete | Status | Analog | Coil | Analog | Read | Coil | Discrete | Status | Analog | Analog | Read | Discrete | Status | Analog | Analog | Read | Discrete | Bool
Yes | FALSE | DiscreteState | Severidade 15 | Voltage | DoNotOperatorOpen | BAY | SwitchStatus | Abnormal | N | Primary | Write | MeasuredValue | kV | Forward | SubstationControlSystem | (UTC-11:00) Coordinated Universal Time-11 | SwitchOnFirstRTUFailure | Group8F | Baker | SOEScan | Status | SelectWithValue | SingleBitMCDA | SectionB | TwoCoord | RaiseLower | Close | TwelveBitSignedTwoComplement | Int16 | Class0123 | Serial | Diagnostic | Sometimes | BinaryInputEvent | DoubleBit | MultiCoord | PulseOn | Int32 | WithAbsoluteTime | BinaryInputWithFlags | Class2 | Int16WithFlag | Int16WithFlag | Version2000 | Block2 | Incoming | Server | Mace | ManualInterval | Icc | Real | CounterFreezeWithReset | LoadDelay | TwoOctets | Balanced | Always | DialIn | TelephoneNumber | B200 | IECSingleBit | ShortPulse | Off | IECShortScaled | IECRateShortTimestamp | AnalogDeltaScan | DigitalInputModule | MultiBit | POMType | TwoCoord | Close | FloatingPointModule | TwelveBitSignedTwoComplement | InputPointControl | BigEndian | ASCII | DiscreteInput | TwoCoords | UShort | CRC16bit | StatusScan | DoubleCoord | AllStatusScan | MemoryStatus | DoubleCoord | Unsigned | Int | Value | TerminalServer | AutoSelectWithValue |  | Counter | Counter |  |  |  | AutoSelectWithValue | DoubleBit | Counter | AutoSelectWithValue | Counter |  | AutoSelectWithValue |  |  | AutoSelectWithValue | Counter | AutoSelectWithValue | DSTS | DSTS |  | Discrete | Counter | RealQuality | Counter |  | RealQuality |  | Discrete | RealQuality | ModemBank | TwoOctets | TwoOctets | TwoOctets | TwoOctets |  | TwoOctets |  | IECDoubleBit | IECDoubleBit | Counter | IECShortScaled | Counter |  |  | IECShortScaled |  | IECDoubleBit | IECDoubleBit | Counter | IECShortScaled |  | TwoOctets |  |  | IECDoubleBit | IECDoubleBit | Counter | IECShortScaled | IECShortScaled | Counter |  | IECShortScaled | IECShortScaled |  |  | Counter | Counter |  |  |  | Counter | HoldingRegister | Counter |  | HoldingRegister |  |  | Counter | Counter |  |  |  | Counter | Counter |  |  | Int
|  | AnalogHigh | Severidade 14 | Current | DoNotAutoClose | BASEVOLTAGE | Local | Auto | C | Secondary | ReadWrite | ControlSetValue | V | Reverse | ControlCenter | (UTC-10:00) Aleutian Islands | SwitchOnAllRTUFailure |  |  |  | Counter | SelectWithoutValue | MultiBit |  | MultiCoord |  | Raise | SixBitUnsigned | Float | ScanTable |  | Type2 | Always | DoubleBinaryInput | MultiCoord |  | PulseOff | Int16 | WithRelativeTime | DoubleBitBinaryInputPackedFormat | Class3 | Int32WithoutFlag | Int32WithoutFlag |  | Block3 |  | Peer | SSL | AutoAll |  | State | CounterFreezeWithoutReset | DelayAcq | ThreeOctets |  | Never |  | Command | B300 | IECDoubleBit | LongPulse |  | IECFloat | IECRate | DigitalCOSTimeTagged |  | MultiBitBCD | DOMType | MultiCoord | Raise | AnalogInputModuleDCM | TwelveBitUnsigned | FloatingPointOP |  | RTU | InputRegister | MultiCoord | Int32 |  | AnalogScan | MultiCoord | MomentaryStatusScan | LatchingStatus | MultiCoord |  | Double | Flags | [8 empty] | DirectNoAck | MultiCoord |  | DirectNoAck |  |  | DirectNoAck |  |  | DirectNoAck |  | DirectNoAck |  |  |  | StateSupp |  | RealQualityTimeTag |  |  | RealQualityTimeTag |  | StateSupp | RealQualityTimeTag | TerminalServer |  |  |  | Undefined |  | Undefined |  | IECStepPosition | IECStepPosition |  | IECFloat |  |  |  | IECFloat |  | IECStepPosition | IECStepPosition |  | IECFloat |  |  |  |  | IECStepPosition | IECStepPosition |  | IECFloat | IECFloat |  |  | IECFloat | IECFloat | [23 empty] | Double
|  | AnalogLow | Severidade 13 | ActivePower | DoNotAutoOpen | NETWORKINFO | OperationCount |  | CN | Tertiary |  | ControlBandwidth | mV |  | IED | (UTC-10:00) Hawaii | CostFactorWithAvailabilityCheck |  |  |  | SmartMeter | AutoSelectWithValue | MultiBitBCD |  |  |  | Lower | TwelveBitUnsigned |  |  |  | Type1 |  | DoubleBinaryInputEvent | MultiCoordBCD |  | LatchOn | Float |  | DoubleBitBinaryInputWithFlags | None | Int16WithoutFlag | Int16WithoutFlag |  | Block4 |  |  |  | AutoReal |  | Discrete | CounterReset |  | Undefined |  |  |  | Delay | B600 | IECStepPosition | Persistent |  | IECShortNormalizedTimestamp |  | DigitalUnconditional |  |  | InputPointControl |  | Lower |  | FloatingPoint |  |  |  | HoldingRegister |  | UInt32 |  | SetpointScan |  | MemoryStatusScan | Multibit | RaiseLower |  | String | Timestamp | [23 empty] | StateQuality |  | RealExtended |  |  | RealExtended |  | StateQuality | RealExtended | [8 empty] | IECBitstring | IECBitstring | [7 empty] | IECBitstring | IECBitstring | [6 empty] | IECBitstring | IECBitstring |  | IECShortNormalizedTimestamp | IECShortNormalizedTimestamp |  |  | IECShortNormalizedTimestamp | IECShortNormalizedTimestamp | [23 empty] | String
|  | AnalogCreep | Severidade 12 | ReactivePower | WarnOnOpen | FAULTINDICATORC | TapPosition |  | B |  |  | ControlDelay | A |  | SmartMeter | (UTC-09:30) Marquesas Islands | [5 empty] | AutoSelectWithoutValue | SingleBitMCDB |  |  |  |  | RemoteStatusByte | [5 empty] | BinaryOutput |  |  | LatchOff | Double |  |  |  | FloatWithFlag |  |  | Block5 |  |  |  | AutoDiscrete |  | StateSupp | [7 empty] | B1200 | IECBitstring |  |  | IECShortScaledTimestamp |  | FloatingPointUnconditional |  |  |  |  | PointOff |  | FifteenBitSignedMagnitude | [5 empty] | Float |  |  |  | LatchingStatusScan |  |  |  | ASignal | AlarmLimit | [23 empty] | DiscreteQuality |  | RealQualityTimeTagExtended |  |  | RealQualityTimeTagExtended |  | DiscreteQuality | RealQualityTimeTagExtended | [8 empty] | IECMultiBit | IECMultiBit | [7 empty] | IECMultiBit | IECMultiBit | [6 empty] | IECMultiBit | IECMultiBit |  | IECShortScaledTimestamp | IECShortScaledTimestamp |  |  | IECShortScaledTimestamp | IECShortScaledTimestamp | [23 empty] | ASignal
|  | AnalogGrowth | Severidade 11 | CosPhi | WarnOnClose | POWERTRC2W | TapIncrement |  | BN |  |  | ControlSubDelay | kA |  | ModemBank | (UTC-09:00) Alaska | [5 empty] | DirectNoAck | SingleBitMCDC | [10 empty] | BinaryOutputEvent |  |  | ClosePulseOn |  |  |  |  | DoubleWithFlag | [6 empty] | AutoState |  | RealQuality | [7 empty] | B2400 | IECMultiBit |  |  | IECFloatTimestamp |  | FloatingPointDelta |  |  |  |  | PointOn |  | FifteenBitSignedTwoComplement | [9 empty] | StatusExceptionScan |  |  |  | DSignal | [24 empty] | StateSuppQuality | [6 empty] | StateSuppQuality | [10 empty] | IECSingleBitTimestamp | [7 empty] | IECSingleBitTimestamp | [7 empty] | IECSingleBitTimestamp | IECSingleBitTimestamp |  | IECFloatTimestamp | IECFloatTimestamp |  |  | IECFloatTimestamp | IECFloatTimestamp | [23 empty] | DSignal
|  | AnalogFlatline | Severidade 10 | Frequency | Predicted | POWERTRC3W | Enabled |  | BC |  |  | ControlLimitHigh | mA |  | DSTS | (UTC-09:00) Coordinated Universal Time-09 | [6 empty] | DoubleBitMCDA | [10 empty] | BinaryCounter |  |  | TripPulseOn | [13 empty] | StateQuality | [7 empty] | B4800 | IECSingleBitTimestamp |  |  | IECShortNormalizedNoQuality |  | FloatingPointCOSTimeTagged |  |  |  |  | SinglePoleOperate |  | FifteenBitUnsigned | [9 empty] | ReadInternalStatus |  |  |  | BoolArray | [24 empty] | StateQualityTimeTag | [6 empty] | StateQualityTimeTag | [10 empty] | IECDoubleBitTimestamp | [7 empty] | IECDoubleBitTimestamp | [7 empty] | IECDoubleBitTimestamp | IECDoubleBitTimestamp |  | IECShortNormalizedNoQuality | IECShortNormalizedNoQuality |  |  | IECShortNormalizedNoQuality | IECShortNormalizedNoQuality | [23 empty] | ASignalArray
|  | AnalogDrop | Severidade 9 | Temperature | Confirmed | SYNCMACHINEC | LoadBonus |  | BCN |  |  | ControlLimitLow | kW |  | TerminalServer | (UTC-08:00) Baja California | [6 empty] | DoubleBitMCDB | [10 empty] | FrozenCounter |  |  | ClosePulseOff | [13 empty] | DiscreteQuality | [7 empty] | B9600 | IECDoubleBitTimestamp |  |  | IECShortNormalizedShortTimestamp | [6 empty] | CustomPayload0 | [11 empty] | ClearInternalStatus |  |  |  | IntArray | [24 empty] | DiscreteQualityTimeTag | [6 empty] | DiscreteQualityTimeTag | [10 empty] | IECStepPositionTimestamp | [7 empty] | IECStepPositionTimestamp | [7 empty] | IECStepPositionTimestamp | IECStepPositionTimestamp | [30 empty] | DSignalArray
|  | AnalogRTN | Severidade 8 | ActiveEnergy | OutOfOrder | CAPACITORC | ReclosingEnabled |  | A |  |  | ControlSlopeReal | MW |  |  | (UTC-08:00) Coordinated Universal Time-08 | [6 empty] | DoubleBitMCDC | [10 empty] | CounterEvent |  |  | TripPulseOff | [13 empty] | StateSuppQuality | [7 empty] | B19200 | IECStepPositionTimestamp |  |  | IECShortScaledShortTimestamp | [6 empty] | CustomPayload1 | [11 empty] | StatusAcknowledge |  |  |  | DoubleArray | [24 empty] | StateSuppQualityTimeTag | [6 empty] | StateSuppQualityTimeTag | [10 empty] | IECBitstringTimestamp | [7 empty] | IECBitstringTimestamp | [7 empty] | IECBitstringTimestamp | IECBitstringTimestamp
|  | TransformerOverload | Severidade 7 | ReactiveEnergy | Malfunctioning | PETERSENCOILC | ControlActiveSetting |  | AN |  |  | ControlSlopeImag | W |  |  | (UTC-08:00) Pacific Time (US & Canada) | [17 empty] | FrozenCounterEvent |  |  | CloseLatchOn | [13 empty] | RealQualityTimeTag | [7 empty] | B38400 | IECBitstringTimestamp |  |  | IECFloatShortTimestamp | [6 empty] | CustomPayload32 | [15 empty] | StringArray | [24 empty] | StateExtended | [6 empty] | StateExtended | [10 empty] | IECMultiBitTimestamp | [7 empty] | IECMultiBitTimestamp | [7 empty] | IECMultiBitTimestamp | IECMultiBitTimestamp
|  | LineOverload | Severidade 6 | ApparentPower | AlarmInhibit | JUMPERC | Refresh |  | AC |  |  | FaultRecorder | kVAr |  |  | (UTC-07:00) Arizona | [17 empty] | AnalogInput |  |  | TripLatchOn | [13 empty] | StateQualityTimeTag | [7 empty] | B56000 | IECMultiBitTimestamp | [25 empty] | ASignalArray | [24 empty] | DiscreteExtended | [6 empty] | DiscreteExtended | [10 empty] | IECSingleBitShortTimestamp | [7 empty] | IECSingleBitShortTimestamp
|  | AnalogReasonability | Severidade 5 | VoltageAngle | AlarmAudioInhibit | DISCONNECTORC | VoltageIndex1 |  | ACN |  |  | WeatherData | MVAr |  |  | (UTC-07:00) La Paz, Mazatlan | [17 empty] | FrozenAnalogInput |  |  | CloseLatchOff | [13 empty] | DiscreteQualityTimeTag | [7 empty] | B64000 | IECSingleBitShortTimestamp | [25 empty] | DSignalArray | [24 empty] | StateSuppExtended | [6 empty] | StateSuppExtended | [10 empty] | IECDoubleBitShortTimestamp | [7 empty] | IECDoubleBitShortTimestamp
|  | SystemAlarm | Severidade 4 | Status | StopProcessing | SECTIONALIZERC | VoltageIndex2 |  | AB |  |  | BellwetherMeter | VAr |  |  | (UTC-07:00) Mountain Time (US & Canada) | [17 empty] | AnalogInputEvent |  |  | TripLatchOff | [13 empty] | StateSuppQualityTimeTag | [8 empty] | IECDoubleBitShortTimestamp | [50 empty] | StateQualityTimeTagExtended | [6 empty] | StateQualityTimeTagExtended | [10 empty] | IECStepPositionShortTimestamp | [7 empty] | IECStepPositionShortTimestamp
|  | DOMAlarm | Severidade 3 | Discrete | PointTest | LOADBREAKERC | LoadFlowEnabled |  | ABN |  |  | RecloseDelay | Hz |  |  | (UTC-07:00) Yukon | [17 empty] | FrozenAnalogInputEvent | [16 empty] | RealExtended | [8 empty] | IECStepPositionShortTimestamp | [50 empty] | DiscreteQualityTimeTagExtended | [6 empty] | DiscreteQualityTimeTagExtended | [10 empty] | IECBitstringShortTimestamp | [7 empty] | IECBitstringShortTimestamp
|  |  | Severidade 2 | SwitchStatus | DOMInhibit | FUSEC | FaultStatus |  | ABC |  |  | FaultCurrentSub | Hz_s |  |  | (UTC-06:00) Central America | [17 empty] | AnalogOutputStatus | [16 empty] | StateExtended | [8 empty] | IECBitstringShortTimestamp | [50 empty] | StateSuppQualityTimeTagExtended | [6 empty] | StateSuppQualityTimeTagExtended | [10 empty] | IECMultiBitShortTimestamp | [7 empty] | IECMultiBitShortTimestamp
|  |  | Severidade 1 | Time |  | BREAKERC | RecloserLockout |  | ABCN |  |  | FaultAngleSub | C |  |  | (UTC-06:00) Central Time (US & Canada) | [17 empty] | AnalogOutputEvent | [16 empty] | DiscreteExtended | [8 empty] | IECMultiBitShortTimestamp
|  |  |  | Humidity |  | CONNODE | FanStatus |  |  |  |  | FaultCurrentTrans | F |  |  | (UTC-06:00) Easter Island | [17 empty] | ClassObjects | [16 empty] | StateSuppExtended
|  |  |  | WindSpeed |  | BUSNODE | OilPumpStatus |  |  |  |  | FaultAngleTrans | kWh |  |  | (UTC-06:00) Guadalajara, Mexico City, Monterrey | [17 empty] | Authentication | [16 empty] | RealQualityTimeTagExtended
|  |  |  | FeelsLike |  | POTENTIALTR | HotLineTag |  |  |  |  | DeltaVoltage | MWh |  |  | (UTC-06:00) Saskatchewan | [17 empty] | SecureDNP3Statistics | [16 empty] | StateQualityTimeTagExtended
|  |  |  | SunshineMinutes |  | SURGEPROTECTOR | MaxOpCount |  |  |  |  | MaxRampUp | kVArh |  |  | (UTC-05:00) Bogota, Lima, Quito, Rio Branco | [17 empty] | SecureDNP3StatisticsEvent | [16 empty] | DiscreteQualityTimeTagExtended
|  |  |  | SkyCover |  | GNDIMPEDANCE | HourlyOpCount |  |  |  |  | MaxRampDown | MVArh |  |  | (UTC-05:00) Chetumal | [34 empty] | StateSuppQualityTimeTagExtended
|  |  |  | Length |  | CONSUMER | DailyOpCount |  |  |  |  | Charged | kVA |  |  | (UTC-05:00) Eastern Time (US & Canada)
|  |  |  | CrossSection |  | SOURCE | MonthlyOpCount |  |  |  |  | EnergyPrice | MVA |  |  | (UTC-05:00) Haiti
|  |  |  | Impedance |  | CAPACITOR | UnderFrequencyAlarm |  |  |  |  | GenerationPrice | VA |  |  | (UTC-05:00) Havana
|  |  |  | Admittance |  | SYNCMACHINE | Forward |  |  |  |  | PInjectedReal | deg |  |  | (UTC-05:00) Indiana (East)
|  |  |  | ImpedancePerLength |  | CURRENTTR | RelayTrip |  |  |  |  | QInjectedReal | dms |  |  | (UTC-05:00) Turks and Caicos
|  |  |  | AdmittancePerLength |  | INDUCTOR | ReverseMode |  |  |  |  | PInjectedEq | sec |  |  | (UTC-04:00) Atlantic Time (Canada)
|  |  |  | Percent |  | FAULTINDICATOR | SourceStatus |  |  |  |  | QInjectedEq | min |  |  | (UTC-04:00) Caracas
|  |  |  | Money |  | SECTION | Parallel |  |  |  |  | CalculatedVoltage | hour |  |  | (UTC-04:00) Cuiaba
|  |  |  | RelativeVoltage |  | TAPCHANGER | PowerOn |  |  |  |  | PMin | km_h |  |  | (UTC-04:00) Georgetown, La Paz, Manaus, San Juan
|  |  |  | Insolation |  | POWERTR2W | Manageable |  |  |  |  | PMax | mph |  |  | (UTC-04:00) Santiago
|  |  |  | CurrentAngle |  | POWERTR3W | Malfunctioning |  |  |  |  | QMin | m_s |  |  | (UTC-03:30) Newfoundland
|  |  |  | RotationSpeed |  | ASIGNAL | WeightingFactor |  |  |  |  | QMax | m |  |  | (UTC-03:00) Araguaina
|  |  |  | Mass |  | DSIGNAL | TemporaryFault |  |  |  |  | SShortCircuit | km |  |  | (UTC-03:00) Asuncion
|  |  |  | FailureRate |  | GROUNDNODE | GroupStatus |  |  |  |  | X1R1Ratio | ft |  |  | (UTC-03:00) Brasilia
|  |  |  | SoilTemperature |  | REMOTEPOINT | Custom1 |  |  |  |  | RWard | yd |  |  | (UTC-03:00) Cayenne, Fortaleza
|  |  |  | OilTemperature |  | CURVE | Custom2 |  |  |  |  | XWard | mi |  |  | (UTC-03:00) City of Buenos Aires
|  |  |  | HotSpotTemperature |  | PETERSENCOIL | Custom3 |  |  |  |  | R1ShortCircuit | mm2 |  |  | (UTC-03:00) Montevideo
|  |  |  | AbsoluteDateTime |  | COMPSWITCH | Custom4 |  |  |  |  | X1ShortCircuit | kcmil |  |  | (UTC-03:00) Punta Arenas
|  |  |  | LatLong |  | PCELL | Custom5 |  |  |  |  | R2ShortCircuit | AWG |  |  | (UTC-03:00) Saint Pierre and Miquelon
|  |  |  | Date |  | REGCTRL | Custom6 |  |  |  |  | X2ShortCircuit | Ohm |  |  | (UTC-03:00) Salvador
|  |  |  | LongDistanceLength |  | CTRLLIMIT | Custom7 |  |  |  |  | R0ShortCircuit | S |  |  | (UTC-02:00) Coordinated Universal Time-02
|  |  |  | Precipitation |  | DAYTYPE | Custom8 |  |  |  |  | X0ShortCircuit | mS |  |  | (UTC-02:00) Greenland
|  |  |  | WindDirection |  | SEASON | Custom9 |  |  |  |  | Custom1 | uS |  |  | (UTC-02:00) Mid-Atlantic - Old
|  |  |  | ThermalPower |  | LOADRSPCHAR | Custom10 |  |  |  |  | Custom2 | Ohm_km |  |  | (UTC-01:00) Azores
|  |  |  | Emission |  | LOADPICKUPCHAR | [5 empty] | Custom3 | Ohm_m |  |  | (UTC-01:00) Cabo Verde Is.
[6 empty] | LOADGROUP | [5 empty] | Custom4 | Ohm_kft |  |  | (UTC) Coordinated Universal Time
[6 empty] | SECTIONALIZER | [5 empty] | Custom5 | Ohm_mi |  |  | (UTC+00:00) Dublin, Edinburgh, Lisbon, London
[6 empty] | RECLSTAGE | [6 empty] | S_km |  |  | (UTC+00:00) Monrovia, Reykjavik
[6 empty] | PROTECTEQP | [6 empty] | S_m |  |  | (UTC+00:00) Sao Tome
[6 empty] | RELSTAGE | [6 empty] | S_kft |  |  | (UTC+01:00) Casablanca
[6 empty] | RTUC | [6 empty] | S_mi |  |  | (UTC+01:00) Amsterdam, Berlin, Bern, Rome, Stockholm, Vienna
[6 empty] | REGION | [6 empty] | uS_km |  |  | (UTC+01:00) Belgrade, Bratislava, Budapest, Ljubljana, Prague
[6 empty] | SUBREGION | [6 empty] | uS_m |  |  | (UTC+01:00) Brussels, Copenhagen, Madrid, Paris
[6 empty] | FEEDER | [6 empty] | uS_kft |  |  | (UTC+01:00) Sarajevo, Skopje, Warsaw, Zagreb
[6 empty] | FEEDEROBJECT | [6 empty] | uS_mi |  |  | (UTC+01:00) West Central Africa
[6 empty] | ASYNCMACHINE | [6 empty] | Percent |  |  | (UTC+02:00) Athens, Bucharest
[6 empty] | ASYNCMACHINEC | [6 empty] | pu |  |  | (UTC+02:00) Beirut
[6 empty] | WIREC | [6 empty] | base120 |  |  | (UTC+02:00) Cairo
[6 empty] | CABLEC | [6 empty] | currency |  |  | (UTC+02:00) Chisinau
[6 empty] | LINEGEOMETRYC | [6 empty] | W_m2 |  |  | (UTC+02:00) Gaza, Hebron
[6 empty] | WEATHERREGION | [6 empty] | rpm |  |  | (UTC+02:00) Harare, Pretoria
[6 empty] | TRANSFORMERAREA | [6 empty] | kg |  |  | (UTC+02:00) Helsinki, Kyiv, Riga, Sofia, Tallinn, Vilnius
[6 empty] | CONSUMERCONTRACT | [6 empty] | ton |  |  | (UTC+02:00) Jerusalem
[6 empty] | JUMPER | [6 empty] | lb |  |  | (UTC+02:00) Juba
[6 empty] | LOADBREAKSWITCH | [6 empty] | perYear |  |  | (UTC+02:00) Kaliningrad
[6 empty] | BREAKER | [6 empty] | mm_h |  |  | (UTC+02:00) Khartoum
[6 empty] | CBLTHERMMODEL | [6 empty] | in_h |  |  | (UTC+02:00) Tripoli
[6 empty] | ARRAYSIGNAL | [6 empty] | MBTU_h |  |  | (UTC+02:00) Windhoek
[6 empty] | INTERLOCKINGITEM | [6 empty] | kcal_h |  |  | (UTC+03:00) Amman
[6 empty] | INTERLOCKINGSCHEME | [6 empty] | kJ_h |  |  | (UTC+03:00) Baghdad
[6 empty] | CTRLSETT | [6 empty] | MJ_h |  |  | (UTC+03:00) Damascus
[6 empty] | FEEDERSEGMENT | [6 empty] | khour |  |  | (UTC+03:00) Istanbul
[6 empty] | FUSE | [6 empty] | kg_h |  |  | (UTC+03:00) Kuwait, Riyadh
[6 empty] | DISCONNECTOR | [6 empty] | g_h |  |  | (UTC+03:00) Minsk
[6 empty] | TAGC | [9 empty] | (UTC+03:00) Moscow, St. Petersburg
[6 empty] | MOBILEOBJECT | [9 empty] | (UTC+03:00) Nairobi
[6 empty] | AORGROUP | [9 empty] | (UTC+03:00) Volgograd
[6 empty] | CUSTOMGROUP | [9 empty] | (UTC+03:30) Tehran
[6 empty] | INTSCHEDULE | [9 empty] | (UTC+04:00) Abu Dhabi, Muscat
[6 empty] | ANNUALSCHEDULE | [9 empty] | (UTC+04:00) Astrakhan, Ulyanovsk
[6 empty] | LVNETWORK | [9 empty] | (UTC+04:00) Baku
[6 empty] | LVFEEDER | [9 empty] | (UTC+04:00) Izhevsk, Samara
[6 empty] | TEMPSCHEDULE | [9 empty] | (UTC+04:00) Port Louis
[6 empty] | CURRENTTRC | [9 empty] | (UTC+04:00) Saratov
[6 empty] | POTENTIALTRC | [9 empty] | (UTC+04:00) Tbilisi
[6 empty] | MESSAGEMAPPING | [9 empty] | (UTC+04:00) Yerevan
[6 empty] | SEASONDAYSCH | [9 empty] | (UTC+04:30) Kabul
[6 empty] | CUSTOMTYPE | [9 empty] | (UTC+05:00) Ashgabat, Tashkent
[6 empty] | GENCONTRACT | [9 empty] | (UTC+05:00) Astana
[6 empty] | DISTGEN | [9 empty] | (UTC+05:00) Ekaterinburg
[6 empty] | PWRPLANT | [9 empty] | (UTC+05:00) Islamabad, Karachi
[6 empty] | SRVDELIVERYPOINT | [9 empty] | (UTC+05:30) Chennai, Kolkata, Mumbai, New Delhi
[6 empty] | SRVLOCATION | [9 empty] | (UTC+05:30) Sri Jayawardenepura
[6 empty] | BUSBAR | [9 empty] | (UTC+05:45) Kathmandu
[6 empty] | NOTEC | [9 empty] | (UTC+06:00) Bishkek
[6 empty] | DYNAMICLINERATING | [9 empty] | (UTC+06:00) Dhaka
[6 empty] | DYNAMICPWTRATING | [9 empty] | (UTC+06:00) Omsk
[6 empty] | RELSETTS | [9 empty] | (UTC+06:30) Yangon (Rangoon)
[6 empty] | DISTRELSETTS | [9 empty] | (UTC+07:00) Bangkok, Hanoi, Jakarta
[6 empty] | DISTRELSTAGE | [9 empty] | (UTC+07:00) Barnaul, Gorno-Altaysk
[6 empty] | RELCONDITION | [9 empty] | (UTC+07:00) Hovd
[6 empty] | REGCTRLGROUP | [9 empty] | (UTC+07:00) Krasnoyarsk
[6 empty] | TRBANK | [9 empty] | (UTC+07:00) Novosibirsk
[6 empty] | CAPBANK | [9 empty] | (UTC+07:00) Tomsk
[6 empty] | PROTGROUP | [9 empty] | (UTC+08:00) Beijing, Chongqing, Hong Kong, Urumqi
[6 empty] | TRANSMISSION | [9 empty] | (UTC+08:00) Irkutsk
[6 empty] | METERC | [9 empty] | (UTC+08:00) Kuala Lumpur, Singapore
[6 empty] | LOGICALNODE | [9 empty] | (UTC+08:00) Perth
[6 empty] | CUSTOMEQP | [9 empty] | (UTC+08:00) Taipei
[6 empty] | CUSTOMBRANCH | [9 empty] | (UTC+08:00) Ulaanbaatar
[6 empty] | CUSTOMSHUNT | [9 empty] | (UTC+08:45) Eucla
[6 empty] | CUSTOMSWITCH | [9 empty] | (UTC+09:00) Chita
[6 empty] | FLEXIBLELOAD | [9 empty] | (UTC+09:00) Osaka, Sapporo, Tokyo
[6 empty] | LIMITSET | [9 empty] | (UTC+09:00) Pyongyang
[6 empty] | ALARMEVENTC | [9 empty] | (UTC+09:00) Seoul
[6 empty] | SIGNALVALUEALARM | [9 empty] | (UTC+09:00) Yakutsk
[6 empty] | ANALOGALARMLIMITS | [9 empty] | (UTC+09:30) Adelaide
[6 empty] | ADVALMLIMITS | [9 empty] | (UTC+09:30) Darwin
[6 empty] | STORAGE | [9 empty] | (UTC+10:00) Brisbane
[6 empty] | METERCMEAS | [9 empty] | (UTC+10:00) Canberra, Melbourne, Sydney
[6 empty] | PHASETAPCHANGER | [9 empty] | (UTC+10:00) Guam, Port Moresby
[6 empty] | SVC | [9 empty] | (UTC+10:00) Hobart
[6 empty] | COUNTERIEC | [9 empty] | (UTC+10:00) Vladivostok
[6 empty] | AINPUTIEC | [9 empty] | (UTC+10:30) Lord Howe Island
[6 empty] | DINPUTIEC | [9 empty] | (UTC+11:00) Bougainville Island
[6 empty] | AOUTPUTIEC | [9 empty] | (UTC+11:00) Chokurdakh
[6 empty] | DOUTPUTIEC | [9 empty] | (UTC+11:00) Magadan
[6 empty] | SUBRTUIEC104 | [9 empty] | (UTC+11:00) Norfolk Island
[6 empty] | RTUIEC104 | [9 empty] | (UTC+11:00) Sakhalin
[6 empty] | COMMLINKIEC104 | [9 empty] | (UTC+11:00) Solomon Is., New Caledonia
[6 empty] | COMMCHANNELIEC104 | [9 empty] | (UTC+12:00) Anadyr, Petropavlovsk-Kamchatsky
[6 empty] | AINPUTDNP3 | [9 empty] | (UTC+12:00) Auckland, Wellington
[6 empty] | DINPUTDNP3 | [9 empty] | (UTC+12:00) Coordinated Universal Time+12
[6 empty] | AOUTPUTDNP3 | [9 empty] | (UTC+12:00) Fiji
[6 empty] | DOUTPUTDNP3 | [9 empty] | (UTC+12:00) Petropavlovsk-Kamchatsky - Old
[6 empty] | RTUDNP3 | [9 empty] | (UTC+12:45) Chatham Islands
[6 empty] | COMMLINKDNP3 | [9 empty] | (UTC+13:00) Coordinated Universal Time+13
[6 empty] | COMMCHANNELDNP3 | [9 empty] | (UTC+13:00) Nuku'alofa
[6 empty] | COUNTERDNP3 | [9 empty] | (UTC+13:00) Samoa
[6 empty] | REMOTEINPUTICCP | [9 empty] | (UTC+14:00) Kiritimati Island
REMOTEOUTPUTICCP
DSTSICCP
RCCICCP
APPREFICCP
ASSOCIATIONICCP
APROCESSING
DERGROUP
TERMINALSERVER
RTUIEC101
COMMLINKIEC101
COMMCHANNELIEC101
SERIALLINK
TCPIPLINK
CALCCONSTARG
CALCSIGNALARG
CALCPARAM
CALCULATION
CALCCODE
AINPUTADMS
DINPUTADMS
AINPUTMODBUS
DINPUTMODBUS
AOUTPUTMODBUS
DOUTPUTMODBUS
RTUMODBUS
COMMLINKMODBUS
COMMCHANNELMODBUS
MODEM
MODEMBANK
MODEMLINK
SCANGROUPDNP3
NETCONFIGICCP
AINPUT2179
DINPUT2179
RPOINT2179
AOUTPUT2179
DOUTPUT2179
RTU2179
COMMLINK2179
COMMCHANNEL2179
SCANGROUP2179
SUBRTU2179
AINPUTCUSTOM1
DINPUTCUSTOM1
AOUTPUTCUSTOM1
DOUTPUTCUSTOM1
COMMCHANNELCUSTOM1
RTUCUSTOM1
COMMLINKCUSTOM1
AINPUTCUSTOM2
DINPUTCUSTOM2
AOUTPUTCUSTOM2
DOUTPUTCUSTOM2
COMMCHANNELCUSTOM2
RTUCUSTOM2
COMMLINKCUSTOM2
AINPUTCUSTOM3
DINPUTCUSTOM3
AOUTPUTCUSTOM3
DOUTPUTCUSTOM3
COMMCHANNELCUSTOM3
RTUCUSTOM3
COMMLINKCUSTOM3
AINPUT61850
DINPUT61850
AOUTPUT61850
DOUTPUT61850
COMMCHANNEL61850
RTU61850
COMMLINK61850
AINPUTDNP3SLAVE
DINPUTDNP3SLAVE
AOUTPUTDNP3SLAVE
DOUTPUTDNP3SLAVE
COMMCHANNELDNP3SLAVE
RTUDNP3SLAVE
COMMLINKDNP3SLAVE
COUNTERDNP3SLAVE
AINPUTS5
DINPUTS5
AOUTPUTS5
DOUTPUTS5
RTUS5
COMMLINKS5
COMMCHANNELS5
SCANGROUPS5
CONDITIONALSCHM
DOMCATALOG
TEMPLATE
AINPUTMETER
DINPUTMETER
RTUVCOM
COMMLINKVCOM
COMMCHANNELVCOM
SCANGROUPVCOM
AINPUTVCOM
AOUTPUTVCOM
DINPUTVCOM
DOUTPUTVCOM
RTUMD3
COMMLINKMD3
COMMCHANNELMD3
SCANGROUPMD3
AINPUTMD3
AOUTPUTMD3
DINPUTMD3
DOUTPUTMD3
RTUCONITEL
COMMLINKCONITEL
COMMCHANNELCONITEL
SCANGROUPCONITEL
AINPUTCONITEL
AOUTPUTCONITEL
DINPUTCONITEL
DOUTPUTCONITEL
SECUREDNP3
TEMPLATEINSTANCE
TMPMOBILEOBJECT
TMPCUT
TMPGENERATOR
TMPGROUNDING
TMPJUMPER
TMPSWITCH
FAULT
TMPLOAD
CHATTERPROCESSING
EVENTSCHEDULE
AINPUTIECSLAVE
DINPUTIECSLAVE
COUNTERIECSLAVE
AOUTPUTIECSLAVE
DOUTPUTIECSLAVE
RTUIECSLAVE
COMMCHANNELIEC101SLAVE
COMMLINKIEC101SLAVE
UDPLINK
TLS

## AlarmCatalog
Alarm Catalog
ALARMEVENTC
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | ALARMEVENTC_DOALARM | ALARMEVENTC_TEXT | ALARMEVENTC_INFO | ALARMEVENTC_DELAY | ALARMEVENTC_ESCALATION | ALARMEVENTC_CAUSE | ALARMEVENTC_SEVERITY | ALARMEVENTC_ESCALATEDSEVERITY | ALARMEVENTC_AUTOACKRTN
Name | Delete | Alias | Custom ID | Do alarm | Text | Alarm Information | Delay [s] | Escalation Timeout [s] | Cause | Severity | Escalated Severity | Auto Acknowledge RTN
Alarme de Estado em Ponto Telessinalizado SB |  | ALESTS SB | 1f59c83d-ed50-4c30-b78c-f6a7bf4fc419 | TRUE | ALESTS - {1} [] | Alarme de Estado em Ponto Telessinalizado SB | 0 | 0 | DiscreteState | Severidade 7 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telessinalizado SA |  | ALESTS SA | ea37e1f4-2f6f-4890-bff5-f26ef60861bc | TRUE | ALESTS - {1} [] | Alarme de Estado em Ponto Telessinalizado SA | 0 | 0 | DiscreteState | Severidade 4 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telessinalizado SI |  | ALESTS SI | 8f25ca55-4b1e-4922-9939-22adf675a896 | TRUE | ALESTS - {1} [] | Alarme de Estado em Ponto Telessinalizado SI | 0 | 0 | DiscreteState | Severidade 3 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telecontrolado SS |  | ALESTC SS | 86dfd195-09a3-4de8-8a16-4e75477b0a6d | TRUE | ALESTC - {1} [] | Alarme de Estado em Ponto Telecontrolado SS | 0 | 0 | DiscreteState | Severidade 8 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telessinalizado SB sem temporizacao |  | ALESTS SB sem temporizado | 25f438c3-fe49-4b9e-a52f-39ee48ce83cf | TRUE | ALESTS - {1} [] | Alarme de Estado em Ponto Telessinalizado SB nao Temporizado | 0 | 0 | DiscreteState | Severidade 7 | Severidade 16 | FALSE
Retorno do Dado do Limite sem Alarme |  | LIRLIM | bfa467a2-0504-4148-93cd-22ceb2c7b90b | FALSE | LIRLIM - Retorno de limite {0:G} {1} {2} [] | Retorno do Dado do Limite Superior / Inferior | 0 | 0 | AnalogRTN | Severidade 12 | Severidade 16 | FALSE
Alarme Prioritario de Dado a 90% do Limite Superior com Temporização |  | ALI90 | 4bfc2d6b-ef89-419d-a340-43a7e4fae649 | TRUE | ALI90 - Valor {0:G} {1} (limite = {3:0.00}) {4} [] | Alarme Prioritario de Dado a 90% do Limite Superior com Temporização | 180 | 0 | AnalogHigh | Severidade 12 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telessinalizado SS |  | ALESTS SS | 67432746-cf34-4050-b437-ce71f5c97687 | TRUE | ALESTS - {1} [] | Alarme de Estado em Ponto Telessinalizado SS | 0 | 0 | DiscreteState | Severidade 8 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telecontrolado SE |  | ALESTC SE | 79db9ae6-f5fa-48d7-a106-e844ad4cffd1 | TRUE | ALESTC - {1} [] | Alarme de Estado em Ponto Telecontrolado SE | 0 | 0 | DiscreteState | Severidade 2 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telessinalizado SO |  | ALESTS SO | 824112f7-80f9-44d3-b23f-a5dd759a8089 | TRUE | ALESTS - {1} [] | Alarme de Estado em Ponto Telessinalizado SO | 0 | 0 | DiscreteState | Severidade 6 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telecontrolado SO |  | ALESTC SO | f61778cb-e93a-4585-a157-96927f8984dd | TRUE | ALESTC - {1} [] | Alarme de Estado em Ponto Telecontrolado SO | 0 | 0 | DiscreteState | Severidade 6 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telecontrolado SV |  | ALESTC SV | a0074a11-62cf-49d4-bf2d-845b23e10823 | TRUE | ALESTC - {1} [] | Alarme de Estado em Ponto Telecontrolado SV | 0 | 0 | DiscreteState | Severidade 5 | Severidade 16 | FALSE
Alarme de Dado em Limite Inferior 1 |  | ALIINF OPER | c7ece8f5-c6e7-487b-b037-1203bc485f3a | TRUE | ALIINF OPER - Valor {0:G} {1} (limite = {3:0.00}) {4} [] | Alarme de Dado em Limite Inferior - Nivel 1 | 0 | 0 | AnalogLow | Severidade 11 | Severidade 16 | FALSE
Alarme de Dado em Limite Inferior 2 |  | ALIINF EMERG | be48ca90-c6b7-41ba-8ee9-c8e438a1d7b9 | TRUE | ALIINF EMERG - Valor {0:G} {1} (limite = {3:0.00}) {4} [] | Alarme de Dado em Limite Inferior - Nivel 2 | 0 | 0 | AnalogLow | Severidade 10 | Severidade 16 | FALSE
Alarme de Dado em Limite Superior 1 |  | ALISUP OPER | ff1d090d-cb13-4917-9eb3-e0fa2d86d7c6 | TRUE | ALISUP OPER - Valor {0:G} {1} (limite = {3:0.00}) {4} [] | Alarme de Dado em Limite Superior - Nivel 1 | 0 | 0 | AnalogHigh | Severidade 11 | Severidade 16 | FALSE
Alarme de Dado em Limite Superior 2 |  | ALISUP EMERG | 7f78107b-a539-488b-947c-5208b1b636a7 | TRUE | ALISUP EMERG - Valor {0:G} {1} (limite = {3:0.00}) {4} [] | Alarme de Dado em Limite Superior - Nivel 2 | 0 | 0 | AnalogHigh | Severidade 10 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telecontrolado SC |  | ALESTC SC | 00b6a6e5-f6f1-43d7-93a4-6e8a0903ed9b | TRUE | ALESTC - {1} [] | Alarme de Estado em Ponto Telecontrolado SC | 0 | 0 | DiscreteState | Severidade 6 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telecontrolado SA |  | ALESTC SA | ca6bf4fd-884a-4c87-a290-9f6e0c688ba8 | TRUE | ALESTC - {1} [] | Alarme de Estado em Ponto Telecontrolado SA | 0 | 0 | DiscreteState | Severidade 4 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telessinalizado SP |  | ALESTS SP | 9081b1ae-4a23-44c1-9bbf-ede74195045f | TRUE | ALESTS - {1} [] | Alarme de Estado em Ponto Telessinalizado SP | 0 | 0 | DiscreteState | Severidade 5 | Severidade 16 | FALSE
Alarme de Estado em Ponto Telessinalizado |  | ALESTS | c44e4e88-54bf-42e8-9855-195297dff8bb | TRUE | ALESTS - {1} [] | Alarme de Estado em Ponto Telessinalizado | 0 | 0 | DiscreteState | Severidade 4 | Severidade 16 | FALSE

## AlarmLimits
Alarm Limits
ANALOGALARMLIMITS | [6 empty] | SIGNALVALUEALARM
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | ANALOGALMLIMITS_MEASTYPE | ANALOGALMLIMITS_MINEGU | ANALOGALMLIMITS_MAXEGU | SIGNALVALUEALARM_USEDINCREEP | SIGNALVALUEALARM_USEDINFLATLINE | SIGNALVALUEALARM_USEDIN2 | SIGNALVALUEALARM_USEDIN1
Name | Delete | Alias | Custom ID | Measurement Type | Min. Reasonable Value | Max. Reasonable Value | Reasonability Check Alarm Catalog | Return-To-Normal Alarm Catalog | Low Limit Catalog | High Limit Catalog
I_403.2@null_null@null_Distr |  |  | 002d0a43-c094-4cc4-a82c-defc8f98a753 | Current | -3.4028e+38 | 3.4028e+38 |  | Retorno do Dado do Limite sem Alarme |  | Alarme Prioritario de Dado a 90% do Limite Superior com Temporização
VBC_144.9@143.52_131.1@124.2_Trans |  |  | 52c8833e-40da-45a1-b805-c0b427dd8ec3 | Voltage | -3.4028e+38 | 3.4028e+38 |  | Retorno do Dado do Limite sem Alarme | Alarme de Dado em Limite Inferior 1;Alarme de Dado em Limite Inferior 2 | Alarme de Dado em Limite Superior 1;Alarme de Dado em Limite Superior 2
V_24.2@23.9_21.9@21.6_Trans |  |  | 8b30a88d-9f7e-4eb0-bc1a-dd6c8f1dadb3 | Voltage | -3.4028e+38 | 3.4028e+38 |  | Retorno do Dado do Limite sem Alarme | Alarme de Dado em Limite Inferior 1;Alarme de Dado em Limite Inferior 2 | Alarme de Dado em Limite Superior 1;Alarme de Dado em Limite Superior 2
TENR_105@95_0@0_Trans |  |  | b3ec273e-e399-4b6f-a12b-94cc6dd8eb02 | Temperature | -3.4028e+38 | 3.4028e+38 |  | Retorno do Dado do Limite sem Alarme | Alarme de Dado em Limite Inferior 1;Alarme de Dado em Limite Inferior 2 | Alarme de Dado em Limite Superior 1;Alarme de Dado em Limite Superior 2
TOLE_95@85_0@0_Trans |  |  | cb6dae5a-aac1-4f05-af90-c9e27fa5c830 | Temperature | -3.4028e+38 | 3.4028e+38 |  | Retorno do Dado do Limite sem Alarme | Alarme de Dado em Limite Inferior 1;Alarme de Dado em Limite Inferior 2 | Alarme de Dado em Limite Superior 1;Alarme de Dado em Limite Superior 2
VAB_253@237.6_202.4@187_Trans |  |  | 17f842d3-5c32-4710-b8fe-941af325ebbb | Voltage | -3.4028e+38 | 3.4028e+38 |  | Retorno do Dado do Limite sem Alarme | Alarme de Dado em Limite Inferior 1;Alarme de Dado em Limite Inferior 2 | Alarme de Dado em Limite Superior 1;Alarme de Dado em Limite Superior 2
VAB_24.15@23.92_22.54@22.31_Trans |  |  | eae52cc0-15f4-46b5-be66-a51f9e730d1e | Voltage | -3.4028e+38 | 3.4028e+38 |  | Retorno do Dado do Limite sem Alarme | Alarme de Dado em Limite Inferior 1;Alarme de Dado em Limite Inferior 2 | Alarme de Dado em Limite Superior 1;Alarme de Dado em Limite Superior 2

## LimitSets
Limit Set
LIMITSET
LIMITSET_DYNAMICRATING | IDOBJ_NAME | LIMITSET_LOWLIMITVALUES | LIMITSET_LOWDEADBAND | LIMITSET_LIMITVALUES | LIMITSET_HIGHDEADBAND
Alarm Limit | Name | Low Limits | Low Limit Deadbands | High Limits | High Limit Deadbands
I_403.2@null_null@null_Distr | Default |  |  | 403.2 | 0.2016
VBC_144.9@143.52_131.1@124.2_Trans | Default | 131.1;124.2 | 2.484;4.14 | 143.52;144.9 | 1.37;1.37
V_24.2@23.9_21.9@21.6_Trans | Default | 21.9;21.6 | 0.12;0.12 | 23.9;24.2 | 0.09;0.09
TENR_105@95_0@0_Trans | Default | 1;0 | 0.5;0.5 | 95;105 | 4.75;5.25
TOLE_95@85_0@0_Trans | Default | 1;0 | 0.5;0.5 | 85;95 | 4.25;4.75
VAB_253@237.6_202.4@187_Trans | Default | 0.2024;0.187 | 0.00704;0.0132 | 0.2376;0.253 | 0.00704;0.0132
VAB_24.15@23.92_22.54@22.31_Trans | Default | 22.54;22.31 | 0.22;0.22 | 23.92;24.15 | 0.22;0.22

## MessageMappings
Message Mapping
MESSAGEMAPPING | [10 empty] | SIGNALVALUEALARM
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | MESSAGEMAPPING_MESSAGES | MESSAGEMAPPING_VALUES | MESSAGEMAPPING_SCADAVALUES | MESSAGEMAPPING_CMDMESSAGES | MESSAGEMAPPING_COLORS | MESSAGEMAPPING_ABNORMAL | MESSAGEMAPPING_OVERRIDABLE | SIGNALVALUEALARM_USEDIN1
Name | Delete | Alias | Custom ID | Messages | Values | SCADA Values | Commanding Messages | Colors | Abnormal Status | Overridable | Alarm Catalog
null@null___NORMAL@FALTA___Custom_S_TS_SB |  |  | b3a0f05e-a43e-4987-9664-6b2ab339c7d7 | Transit;NORMAL;FALTA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  | 3318464c-b4db-4052-8f62-984a82bed1b1 | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA
null@null___NORMAL@DEFEITO___Custom_S_TS_SI |  |  | a9894d24-135c-4e7b-b8be-9bc122849a5c | Transit;NORMAL;DEFEITO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SI;Alarme de Estado em Ponto Telessinalizado SI;Alarme de Estado em Ponto Telessinalizado SI;Alarme de Estado em Ponto Telessinalizado SI
null@null___NORMAL@ATUADO___Custom_S_TS_SI |  |  | 9dc12e55-d022-469e-8177-3a9739f98546 | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SI;Alarme de Estado em Ponto Telessinalizado SI;Alarme de Estado em Ponto Telessinalizado SI;Alarme de Estado em Ponto Telessinalizado SI
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS |  |  | 89142b13-37f0-4791-9940-db88dfa90839 | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS
null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS |  |  | 327d67af-b2c3-4d6f-b850-08371eaef8e3 | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS
null@null___NORMAL@ATUADO___Custom_S_TS_SB |  |  | df150184-40aa-49e4-8676-b36b56adfffc | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB sem temporizacao;Alarme de Estado em Ponto Telessinalizado SB sem temporizacao;Alarme de Estado em Ponto Telessinalizado SB sem temporizacao;Alarme de Estado em Ponto Telessinalizado SB sem temporizacao
null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS |  |  | f86c33b8-6d2d-42db-a138-83e9df4dd790 | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS
null@null___NORMAL@ATUADO___Custom_S_TS_SA |  |  | aba5eec1-6268-464b-a141-f943b4fed6b7 | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE |  |  | 7bf0bf18-4079-44b8-809f-5e74dbacc82e | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;1;2;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;TRUE | Alarme de Estado em Ponto Telecontrolado SE;Alarme de Estado em Ponto Telecontrolado SE;Alarme de Estado em Ponto Telecontrolado SE;Alarme de Estado em Ponto Telecontrolado SE
null@null___REMOTO@LOCAL___Custom_S_TS_SS |  |  | 1dac907a-d6e3-42f8-ba71-4d801f99a716 | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS
null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB |  |  | 5079bf20-9a7c-4632-a068-75e30dcfb560 | Transit;CARREGADA;DESCARREGADA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS |  |  | 82107e55-8311-4d6f-b51e-6e2e5099a81f | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS
null@null___NORMAL@FALHA___Custom_S_TS_SB |  |  | 30c921f9-7b77-4cc5-893d-5c91765e61bd | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS |  |  | 00d7c00c-471c-4cf6-b9f7-94ca1909009e | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS
null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS |  |  | 3406f2cb-403f-49a7-bf04-cadb523c6223 | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS
null@null___REMOTO@LOCAL___Custom___INV_S_TS_SS |  |  | 808fdfbe-d938-4095-a956-c49d044b683e | Transit;REMOTO;LOCAL;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS
null@null___NORMAL@DEFEITO___Custom_S_TS_SB |  |  | af6b9182-8f8c-4840-b58d-df2acf02b6e9 | Transit;NORMAL;DEFEITO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB
null@null___NORMAL@FALHA___Custom___INV_S_TS_SB |  |  | 59dce93e-75d8-4fad-a224-f156dca33b3c | Transit;NORMAL;FALHA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB
null@null___COMPLETA@INCOMPLETA___Custom_S_TS_SA |  |  | cc7d3836-90ce-4480-9205-bc7b9bf149cc | Transit;COMPLETA;INCOMPLETA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA
null@null___LIGADO@DESLIGADO___Custom_S_TS_SB |  |  | 4aa7975d-06aa-4156-9d93-7eb4af52e3ea | Transit;LIGADO;DESLIGADO;Error | 0;2;1;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB sem temporizacao;Alarme de Estado em Ponto Telessinalizado SB sem temporizacao;Alarme de Estado em Ponto Telessinalizado SB sem temporizacao;Alarme de Estado em Ponto Telessinalizado SB sem temporizacao
null@null___ABERTO@FECHADO___SwitchStatus_D_TS_SO_terra |  |  | 77bd3426-1621-45a4-86b4-138c7f7fa71a | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 0;1;2;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SO;Alarme de Estado em Ponto Telessinalizado SO;Alarme de Estado em Ponto Telessinalizado SO;Alarme de Estado em Ponto Telessinalizado SO
null@null___NORMAL@TRANSFERIDA___Custom_S_TS_SA |  |  | b6536904-a8cd-47e3-8eac-4014716ae62c | Transit;NORMAL;TRANSFERIDA;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA;Alarme de Estado em Ponto Telessinalizado SA
ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO |  |  | f0107821-8e5f-485b-bf9a-6d42132eb32e | Transit;ABERTO;FECHADO;Error | 0;1;2;3 | 0;1;2;3 | ;ABRIR;FECHAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;TRUE | Alarme de Estado em Ponto Telecontrolado SO;Alarme de Estado em Ponto Telecontrolado SO;Alarme de Estado em Ponto Telecontrolado SO;Alarme de Estado em Ponto Telecontrolado SO
DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV |  |  | b3fa1bf2-fc9d-481b-be2d-0b7eaa29c641 | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESATIVAR;ATIVAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Abnormal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SV;Alarme de Estado em Ponto Telecontrolado SV;Alarme de Estado em Ponto Telecontrolado SV;Alarme de Estado em Ponto Telecontrolado SV
null@null___DESABILITOU@HABILITOU___Custom_S_TS_SS |  |  | 294b701e-f7b6-44db-8efb-3f801552fe27 | Transit;DESABILITOU;HABILITOU;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS
null@null___NÃO PERMITIDO@PERMITIDO___Custom_S_TS_SS |  |  | fcbd0f6e-5b23-4bc5-a6e5-965c166384a6 | Transit;NÃO PERMITIDO;PERMITIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS
null@null___DESATIVADO@ATIVADO___Custom_S_TS_SS |  |  | b5c7ea68-6305-45fa-9e64-b8d17a259741 | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS
null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS |  |  | ac10e5d2-e465-4a89-86e0-679309bdb0a9 | Transit;BLOQUEADA;LIBERADA;Error | 0;1;2;3 | 2;1;0;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS
null@INDIVIDUAL___DESATIVADO@ATIVADO___Custom_S_TC_SS |  |  | 27ea22da-5974-4f81-a7c1-c5772ebc44e8 | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;INDIVIDUAL; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS
null@MESTRE___DESATIVADO@ATIVADO___Custom_S_TC_SS |  |  | bf739aef-5a0d-4ad0-ab8c-cebd5ca9d11f | Transit;DESATIVADO;ATIVADO;Error | 0;1;2;3 | 2;0;1;3 | ;;MESTRE; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | TRUE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS
AUMENTAR@DIMINUIR___null@null___INV_TapIncrement_S_TC_SS_VF |  |  | 87ebb87c-cf51-41a3-9f26-44113eb182a4 | Transit;;;Error | 0;1;2;3 | 0;1;2;3 | ;AUMENTAR;DIMINUIR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Normal;Normal;Normal;Normal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS
DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TC_SV |  |  | e3c9e933-d75d-4dd9-814b-a37ba1c61422 | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SV;Alarme de Estado em Ponto Telecontrolado SV;Alarme de Estado em Ponto Telecontrolado SV;Alarme de Estado em Ponto Telecontrolado SV
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV___admsINV_S_TC_SS |  |  | 439c8e84-f1c8-4e53-bf66-725a2bd1315a | Transit;INCLUIDO;EXCLUIDO;Error | 0;2;1;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS
null@null___DESLIGADO@LIGADO___Custom___INV_S_TS_SB |  |  | a7a74a38-a789-4a2f-9a6c-874715ca285a | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;1;0;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB;Alarme de Estado em Ponto Telessinalizado SB
DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SC_USO_BC |  |  | 2b73e442-9b11-4cfb-81f8-ff3e706a30c7 | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 0;1;2;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SC;Alarme de Estado em Ponto Telecontrolado SC;Alarme de Estado em Ponto Telecontrolado SC;Alarme de Estado em Ponto Telecontrolado SC
INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS_AUTO |  |  | f78e74b4-cf17-4909-b9fc-5c3410b74ab7 | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;1;0;3 | ;INCLUIR;EXCLUIR; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Normal;Normal;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS;Alarme de Estado em Ponto Telecontrolado SS
REARMAR@null___NORMAL@ATUADO___Custom_S_TC_SA |  |  | b928b78f-9d6b-498f-aad0-7226d65b8d1a | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;REARMAR;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telecontrolado SA;Alarme de Estado em Ponto Telecontrolado SA;Alarme de Estado em Ponto Telecontrolado SA;Alarme de Estado em Ponto Telecontrolado SA
null@null___MANUAL DESATIVOU@MANUAL ATIVOU___Custom_S_TS_SS |  |  | e3d08b30-aba3-4242-a9dc-5e69d58f5c6b | Transit;MANUAL DESATIVOU;MANUAL ATIVOU;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS
null@null___AUTOM DESATIVADO@AUTOM ATIVOU___Custom_S_TS_SS |  |  | 47cb64f2-8605-4375-a4e3-2175dbe3d1fb | Transit;AUTOM DESATIVADO;AUTOM ATIVOU;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS
null@null___INCLUIDO@EXCLUIDO___Custom_S_TS_SS |  |  | 1a8e15af-1aa5-489d-81f0-3eee83fa826e | Transit;INCLUIDO;EXCLUIDO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FFFF0000;#FF00FF00;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS;Alarme de Estado em Ponto Telessinalizado SS
null@null___NORMAL@ATUADO___Custom_S_TS_SP |  |  | c4385961-b437-4afd-83d8-85b9745cfe29 | Transit;NORMAL;ATUADO;Error | 0;1;2;3 | 2;0;1;3 | ;;; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado SP;Alarme de Estado em Ponto Telessinalizado SP;Alarme de Estado em Ponto Telessinalizado SP;Alarme de Estado em Ponto Telessinalizado SP
null@null___DESLIGADO@LIGADO___SwitchStatus_S_TS |  |  | 44883595-670b-449d-b498-54d4a30ea086 | Transit;DESLIGADO;LIGADO;Error | 0;1;2;3 | 2;0;1;3 | ;DESLIGAR;LIGAR; | #FF000000;#FF00FF00;#FFFF0000;#FFA9A9A9 | Abnormal;Auto;Auto;Abnormal | FALSE;TRUE;TRUE;FALSE | Alarme de Estado em Ponto Telessinalizado;Alarme de Estado em Ponto Telessinalizado;Alarme de Estado em Ponto Telessinalizado;Alarme de Estado em Ponto Telessinalizado

## ManualDiscreteSignals
Signal Details
DSIGNAL
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | MEASUREMENT_PSR |  | IDOBJ_AORGROUP | SIGNAL_DEVICEMAPPING | [7 empty] | DSIGNAL_TYPE | MEASUREMENT_TYPE | MEASUREMENT_PHASE | MEASUREMENT_SIDE | SIGNAL_DIRECTION | SIGNAL_ANNUALSCH | DSIGNAL_MAPPING | DSIGNAL_NORMALVALUE | DSIGNAL_DOMCATALOG
Signal Name | Delete | Signal Alias | Signal Custom ID | Device Name | Device Custom ID | Signal AOR Group | Substation | Feeder | Feeder Object | Bank | Bay | Device | Device Mapping | Description | Signal Type | Measurement Type | Phases | Side | Direction | Annual Schedule | Message Mapping | Normal Value | DOM Catalog

## ManualAnalogSignals
Signal Details
ASIGNAL | [27 empty] | ADVALMLIMITS
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | MEASUREMENT_PSR |  | IDOBJ_AORGROUP | SIGNAL_DEVICEMAPPING | [7 empty] | ASIGNAL_TYPE | MEASUREMENT_TYPE | MEASUREMENT_UNIT | MEASUREMENT_PHASE | MEASUREMENT_SIDE | SIGNAL_DIRECTION | SIGNAL_ANNUALSCH | ASIGNAL_FLOWDIRECTION | ASIGNAL_RATEDVALUE | ASIGNAL_MINSETPOINT | ASIGNAL_MAXSETPOINT | ASIGNAL_TRUST | ASIGNAL_ALARMLIMITS | IDOBJ_NAME | ADVALMLIMITS_ROCALARMGROWTH | ADVALMLIMITS_ROCLIMITGROWTH | ADVALMLIMITS_ROCALARMDROP | ADVALMLIMITS_ROCLIMITDROP | ADVALMLIMITS_FLATLINEALARM | ADVALMLIMITS_FLATLINETIMEOUT | ADVALMLIMITS_CREEPALARM | ADVALMLIMITS_CREEPDEADBAND
Signal Name | Delete | Signal Alias | Signal Custom ID | Device Name | Device Custom ID | Signal AOR Group | Substation | Feeder | Feeder Object | Bank | Bay | Device | Device Mapping | Description | Signal Type | Measurement Type | Display Unit | Phases | Side | Direction | Annual Schedule | Flow Direction | Rated Value | Min. Setpoint | Max. Setpoint | Trust Factor | Alarm Limits | Advanced Alarms - Name | Advanced Alarms - Rate-Of-Growth Alarm | Advanced Alarms - Rate-Of-Growth Limit | Advanced Alarms - Rate-Of-Drop Alarm | Advanced Alarms - Rate-Of-Drop Limit | Advanced Alarm - Flatline Alarm | Advanced Alarm - Flatline Timeout [s] | Advanced Alarm - Creep Alarm | Advanced Alarm - Creep Deadband

## DNP3_RTUs
DNP3 Remote Unit
RTUDNP3 | [55 empty] | COMMCHANNELDNP3
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | IDOBJ_AORGROUP | PSR_LOCATION | EQUIPMENT_CONT |  | RTU_TYPE | REMOTETERMINALUNIT_LISTENONLYMODE¦TERMINALSERVER_LISTENONLYMODE | TERMINALSERVER_DELAYBETWEENCOMMANDS | RTU_TIMEZONE | RTU_USEDST | RTU_ENABLETIMEOFFSET | RTU_TIMEOFFSETPAST | RTU_TIMEOFFSETFUTURE | RTU_PARENTREMOTE | RTU_INITIALPOLL | RTU_INITSEQUENCERETRYPERIOD | REMOTETERMINALUNIT_FASTPOLLING | REMOTETERMINALUNIT_FASTTIMEOUT | REMOTETERMINALUNIT_REQTIMEOUT | RTU_WATCHDOGTIMEOUT | RTU_REDUNDANCYBEHAVIOR | REMOTETERMINALUNIT_COMMRETRIES | REMOTETERMINALUNIT_SCANAFTERCMD | REMOTETERMINALUNIT_CMDSCANDELAY | REMOTETERMINALUNIT_SCANAFTERUCOS | RTUDNP3_SRCADDRESS | RTUDNP3_DESTADDRESS | RTUDNP3_C1UNSOLICITED | RTUDNP3_C2UNSOLICITED | RTUDNP3_C3UNSOLICITED | RTUDNP3_INTEGRITYSCOPE | RTUDNP3_KEEPALIVEPERIOD | RTUDNP3_COLDRESTART | RTUDNP3_ENABLEFREEZE | RTUDNP3_PROTTYPE | RTUDNP3_CLEAR | RTUDNP3_NOACK | RTUDNP3_FREEZECYCLE | RTUDNP3_USERNUMBER | RTUDNP3_ENABLESECURE | RTUDNP3_SECURE | REMOTETERMINALUNIT_PERIODICPOLL | REMOTETERMINALUNIT_POLLCYCLE | RTUDNP3_C1POLL | RTUDNP3_C1POLLCYCLE | RTUDNP3_C2POLL | RTUDNP3_C2POLLCYCLE | RTUDNP3_C3POLL | RTUDNP3_C3POLLCYCLE | RTUDNP3_TIMESYNC | RTUDNP3_TIMESYNCCYCLE | RTUDNP3_TIMESYNCMODE | RTUDNP3_INITIALRESETLINKSTATES | COMMCHANNEL_FRONTEND
Remote Unit (Terminal Server) Name | Delete | Remote Unit Alias | Remote Unit Custom ID | Remote Unit AOR Group | Remote Unit Description | Container Name | Container Custom ID | Remote Unit Type | Listen-Only Mode | Delay Between RTUs [s] | Time Zone | DST-Aware | Enable Time Offset | Time Offset Past [s] | Time Offset Future [s] | Parent Remote | Enable Initial Integrity Scan | Initial Sequence Retry Period | Fast-Scan Period [s] | Fast-Scan Timeout [s] | Request Timeout [s] | Watchdog Timeout [s] | Redundancy Behavior | Command Attempts | Scan After Command | Scan Delay [s] | Scan After Uncommanded Change | Source Address | Destination Address | Class 1 Unsolicited Messages | Class 2 Unsolicited Messages | Class 3 Unsolicited Messages | Scan Scope | Keep Alive Period | RTU Cold Restart | Enable Freeze and Read | Protection Type | Clear | No Acknowledgement | Freeze and Read Periodic Cycle [s] | User Number | Enable Secure | Secure DNP3 Settings | Enable Class 0 Periodic Scan | Class 0 Scan Cycle [s] | Enable Class 1 Periodic Scan | Class 1 Scan Cycle [s] | Enable Class 2 Periodic Scan | Class 2 Scan Cycle [s] | Enable Class 3 Periodic Scan | Class 3 Scan Cycle [s] | Enable Time Synchronization | Synchronization Cycle [s] | Time Sync Mode | Initial Reset Link States | Front-End Name
UTR_GTD_1 |  | UTR_GTD_1__SEL_SEL-2241 | 458e14ac-5d26-4df3-b0e3-1ecb85825473 | GTA Trans | SEL_SEL-2241 | GRAVATAI 4 | f65e22f4-a384-4f59-8ab9-af397906a3d7 | RTU | FALSE |  | (UTC-03:00) Brasilia | FALSE | TRUE | 20 | 1 |  | TRUE | 100 | 120 | 240 | 120 | 0 | PrioritizeCostFactor | 2 | FALSE | 0 | FALSE | 1 | 2 | FALSE | FALSE | FALSE | Class0123 | 0 | TRUE | FALSE | None | FALSE | FALSE | 3600 | 1 | FALSE |  | TRUE | 3600 | TRUE | 6 | TRUE | 6 | FALSE | 15 | TRUE | 28800 | Serial | TRUE | prod-FrontEndProcessor-Default

## DNP3_UDPLinks
DNP3 Communication Link
COMMLINKDNP3 | [13 empty] | UDPLINK
IDOBJ_NAME | DELETE | COMMLINK_RTU | IDOBJ_ALIAS | COMMLINK_COMMCOST | IDOBJ_AORGROUP | COMMLINK_CONNRETRIES | COMMLINK_LATENCYTIMEOUT | COMMLINKDNP3_PERIODICLINKSTATUSCHECK | COMMLINKDNP3_CONFIRMMODE | COMMLINKDNP3_CONFIRMTIMEOUT | COMMLINK_MEDIUM | COMMLINKDNP3_LINKSTATUSCHECKCYCLE | IDOBJ_CUSTOMID | UDPLINK_IPADDRESS | UDPLINK_DESTPORT | UDPLINK_USESOURCEPORT | UDPLINK_SOURCEPORT | UDPLINK_UDPCONNTIMEOUT
Communication Link Name | Delete | Remote Unit | Communication Link Alias | Cost Factor | Communication Link AOR Group | Connection Attempts | Link Latency [s] | Periodic link status check | Confirm Mode | Confirm Timeout [s] | Communication Medium | Link status check cycle [s] | Communication Link Custom ID | IP Address | Destination Port | Use Source Port | Source Port | Connect Timeout [s]

## DNP3_TCPLinks
DNP3 Communication Link
COMMLINKDNP3 | [13 empty] | TCPIPLINK
IDOBJ_NAME | DELETE | COMMLINK_RTU | IDOBJ_ALIAS | COMMLINK_COMMCOST | IDOBJ_AORGROUP | COMMLINK_CONNRETRIES | COMMLINK_LATENCYTIMEOUT | COMMLINKDNP3_PERIODICLINKSTATUSCHECK | COMMLINKDNP3_CONFIRMMODE | COMMLINKDNP3_CONFIRMTIMEOUT | COMMLINK_MEDIUM | COMMLINKDNP3_LINKSTATUSCHECKCYCLE | IDOBJ_CUSTOMID | TCPIPLINK_IPADDRESS | TCPIPLINK_PORT | TCPIPLINK_TCPCONNTIMEOUT
Communication Link Name | Delete | Remote Unit | Communication Link Alias | Cost Factor | Communication Link AOR Group | Connection Attempts | Link Latency [s] | Periodic link status check | Confirm Mode | Confirm Timeout [s] | Communication Medium | Link status check cycle [s] | Communication Link Custom ID | IP Address | Port | TCP Connection Timeout [s]
UTR_GTD_1_Link1__ CPFL Fiber |  | UTR_GTD_1 | UTR_GTD_1_Link1 | 0 | GTA Trans | 3 | 2 | FALSE | Never | 10 | SAT Hughes | 3600 | 493f6549-c3d7-4fbf-899b-111a05ce6250 | 10.34.13.2 | 20000 | 60
UTR_GTD_1_Link8__SAT Starlink |  | UTR_GTD_1 | UTR_GTD_1_Link8 | 8 | GTA Trans | 3 | 2 | FALSE | Never | 10 | SAT Starlink | 3600 | 9a450c02-f314-416a-89f3-06001148c754 | 10.27.0.82 | 21238 | 60
UTR_GTD_1_Link9__SAT Starlink |  | UTR_GTD_1 | UTR_GTD_1_Link9 | 9 | GTA Trans | 3 | 2 | FALSE | Never | 10 | SAT Starlink | 3600 | 02865134-888d-44a7-9d01-19dbf7f69ec3 | 10.27.0.66 | 21238 | 60
UTR_GTD_1_Link2__M2M Vivo |  | UTR_GTD_1 | UTR_GTD_1_Link2 | 0 | GTA Trans | 3 | 2 | FALSE | Never | 10 | M2M Vivo | 3600 | 32819d6b-d914-442b-b6a7-38cef214100e | 99.43.11.99 | 99 | 60

## DNP3_ScanGroups
DNP3 Scan Group
SCANGROUPDNP3
SCANGROUP_RTU | SCANGROUP_SCANCYCLE | SCANGROUPDNP3_OBJGROUP | SCANGROUPDNP3_OBJVARIATION | SCANGROUPDNP3_ALLPOINTS | SCANGROUP_STARTCOORD | SCANGROUP_ENDCOORD
Remote Unit | Scan Cycle [s] | Group | Object Variation | All Points | Start Coordinate | End Coordinate

## DNP3_DiscreteSignals
Signal Details | [22 empty] | Remote Points
DSIGNAL | [22 empty] | REMOTEPOINT | [15 empty] | CHATTERPROCESSING
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | MEASUREMENT_TYPE | IDOBJ_AORGROUP | SIGNAL_DEVICEMAPPING | [7 empty] | DSIGNAL_TYPE | MEASUREMENT_PHASE | MEASUREMENT_SIDE | SIGNAL_DIRECTION | SIGNAL_ANNUALSCH | DSIGNAL_MAPPING | DSIGNAL_NORMALVALUE | DSIGNAL_DOMCATALOG | MEASUREMENT_PSR | IDOBJ_NAME | DELETE | IDOBJ_CUSTOMID | IDOBJ_ALIAS | REMOTEPOINT_TYPE | REMOTEOUTPUT_CMDTIMEOUT | REMOTEOUTPUT_SBOMODE | DINPUTDNP3_DATATYPE¦DOUTPUTDNP3_INDATATYPE | REMOTEINPUTDNP3_INCOORDS¦REMOTEOUTPUTDNP3_INCOORDS | REMOTEINPUTDNP3_OUTREGISTER¦REMOTEOUTPUTDNP3_OUTREGISTER | REMOTEOUTPUTDNP3_POLLAFTERCMD | REMOTEOUTPUTDNP3_POLLDELAY | DOUTPUTDNP3_OUTDATATYPE | REMOTEOUTPUTDNP3_OUTCOORDS | DOUTPUTDNP3_CTRLCODES | DOUTPUTDNP3_CMDTIMES | CHATTERPROCESSING_ENABLE | CHATTERPROCESSING_NUMBEROFCHANGES | CHATTERPROCESSING_OSCILLATIONPERIOD | CHATTERPROCESSING_SUPPRESSIONPERIOD
Signal Name | Delete | Signal Alias | Signal Custom ID | Measurement Type | Signal AOR Group | Substation | Feeder | Feeder Object | Bank | Bay | Device | Device Mapping | Description | Signal Type | Phases | Side | Direction | Annual Schedule | Message Mapping | Normal Value | DOM Catalog | Remote Unit | Remote Point Name | Delete Remote Point | Remote Point Custom ID | Remote Point Alias | Remote Point Type | Command Timeout [s] | Commanding Mode | Input Data Type | Input Coordinates | Output Register | Scan After Command | Scan Delay [s] | Output Data Type | Output Coordinates | Control Codes | Command Times [s] | Enable Oscillation Processing | Number of Changes | Oscillation Period [s] | Suppression Period [s]
GTD_AL13_52-13_CCMO |  | VCC MOT | GTD_AL13_52-13_CCMO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_CCMO |  | GTD_AL13_52-13_CCMO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1706 | FALSE
GTD_TR1BT_TR1BT_50EF |  | 50EF - END FAULT | 49f23d26-ba43-4a46-9a35-0ff0ec71d79e | Status | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_50EF |  | 61645d9c-6bc8-4a83-9c10-bd2cb3f6f54a | 20260327 | Status |  |  | SingleBit | 3233 | FALSE
GTD_AL14_52-14_DR |  | RELE | GTD_AL14_52-14_DR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_DR |  | GTD_AL14_52-14_DR_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1820 | FALSE
GTD_AL22_52-22_BBA1 |  | BOB AB 1 | GTD_AL22_52-22_BBA1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_BBA1 |  | GTD_AL22_52-22_BBA1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2509 | FALSE
GTD_AL13_52-13_BBFC |  | BOB FEC | GTD_AL13_52-13_BBFC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_BBFC |  | GTD_AL13_52-13_BBFC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1708 | FALSE
GTD_AL22_52-22_51N |  | 51N | GTD_AL22_52-22_51N_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL22_52-22_51N |  | GTD_AL22_52-22_51N_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2531 | FALSE | FALSE | 15 | SingleCoord | 2501;2501 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL22_52-22_81U2 |  | AJUSTE PARA 81 ESTAGIO 2 | GTD_AL22_52-22_81U2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_81U2 |  | GTD_AL22_52-22_81U2_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2541 | FALSE | FALSE | 5 | SingleCoord | 2505 | ClosePulseOn | 0.25
GTD_AL22_52-22_FSIN |  | FALHA SINCRONISMO IRIG-B | GTD_AL22_52-22_FSIN_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_FSIN |  | GTD_AL22_52-22_FSIN_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2518 | FALSE
GTD_AL23_52-23_SGFT |  | SGF_TRIP | GTD_AL23_52-23_SGFT_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_SGFT |  | GTD_AL23_52-23_SGFT_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2635 | FALSE
GTD_AL22_52-22_TOED |  | TEMPERATURA OLEO ENROLAMENTO TRIP | GTD_AL22_52-22_TOED_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_TOED |  | GTD_AL22_52-22_TOED_UTR_GTD_1 | 20251121 | Status |  |  | SingleBit | 2557 | FALSE
GTD_AL14_52-14_BBFC |  | BOB FEC | GTD_AL14_52-14_BBFC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_BBFC |  | GTD_AL14_52-14_BBFC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1808 | FALSE
GTD_AL22_52-22_43TC |  | 43TC | GTD_AL22_52-22_43TC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_43TC |  | GTD_AL22_52-22_43TC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2515 | FALSE
GTD_AL23_52-23_TRIP |  | TRIP EXTERNO | GTD_AL23_52-23_TRIP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_TRIP |  | GTD_AL23_52-23_TRIP_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2657 | FALSE
GTD_AL13_52-13_FA |  | FASE A | GTD_AL13_52-13_FA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_FA |  | GTD_AL13_52-13_FA_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1723 | FALSE
GTD_AL23_52-23_CCCO |  | VCC CMD | GTD_AL23_52-23_CCCO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_CCCO |  | GTD_AL23_52-23_CCCO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2607 | FALSE
GTD_AL22_52-22_TRIP |  | TRIP EXTERNO | GTD_AL22_52-22_TRIP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_TRIP |  | GTD_AL22_52-22_TRIP_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2558 | FALSE
GTD_AL14_52-14_81E3 |  | 81 ESTAGIO 3 | GTD_AL14_52-14_81E3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_81E3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_81E3 |  | GTD_AL14_52-14_81E3_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1846 | FALSE
GTD_AL13_52-13_FSIN |  | FALHA SINCRONISMO IRIG-B | GTD_AL13_52-13_FSIN_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_FSIN |  | GTD_AL13_52-13_FSIN_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1718 | FALSE
GTD_AL13_52-13_CCCO |  | VCC CMD | GTD_AL13_52-13_CCCO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_CCCO |  | GTD_AL13_52-13_CCCO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1707 | FALSE
GTD_AL23_52-23_81E3 |  | 81 ESTAGIO 3 | GTD_AL23_52-23_81E3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_81E3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_81E3 |  | GTD_AL23_52-23_81E3_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2646 | FALSE
GTD_AL22_52-22_51N1 |  | 51N 1 | GTD_AL22_52-22_51N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_51N1 |  | GTD_AL22_52-22_51N1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2534 | FALSE
GTD_AL14_52-14_81E2 |  | 81 ESTAGIO 2 | GTD_AL14_52-14_81E2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_81E2 |  | GTD_AL14_52-14_81E2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1845 | FALSE
GTD_AL22_52-22_79RE |  | 79 RESET | GTD_AL22_52-22_79RE_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_79RE |  | GTD_AL22_52-22_79RE_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2554 | FALSE
GTD_AL22_52-22_DJF1 |  | DJ | GTD_AL22_52-22_DJF1_UTR_GTD_1_SwitchStatus | SwitchStatus | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_GTD_1 | GTD_AL22_52-22_DJF1 |  | GTD_AL22_52-22_DJF1_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | MultiCoord | 2500;2501 | FALSE | FALSE | 15 | SingleCoord | 2500;2500 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_AL22_52-22_79LO |  | 79 BLOQUEADO | GTD_AL22_52-22_79LO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_79LO |  | GTD_AL22_52-22_79LO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2553 | FALSE
GTD_AL13_52-13_81E4 |  | 81 ESTAGIO 4 | GTD_AL13_52-13_81E4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_81E4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_81E4 |  | GTD_AL13_52-13_81E4_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1747 | FALSE
GTD_TR1_TR1_RTD2_DPT1 |  | DEFEITO PT100 | caa08b4c-b2f8-494b-b652-dc3b29caa2e2 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_RTD2_DPT1 |  | 32ca3a81-ba58-45e1-b065-9156f856632b | 20260407 | Status |  |  | SingleBit | 851 | FALSE
GTD_AL22_52-22_81E3 |  | 81 ESTAGIO 3 | GTD_AL22_52-22_81E3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_81E3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_81E3 |  | GTD_AL22_52-22_81E3_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2547 | FALSE
GTD_AL22_52-22_FC |  | FASE C | GTD_AL22_52-22_FC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_FC |  | GTD_AL22_52-22_FC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2526 | FALSE
GTD_AL13_52-13_FUTP |  | FALHA CIRCUITO TP | GTD_AL13_52-13_FUTP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_FUTP |  | GTD_AL13_52-13_FUTP_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1754 | FALSE
GTD_BP2_BP2_87_FC |  | FASE C | b2d13761-afa8-48fa-89b3-a5cde796d898 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BP2_BP2_87_FC |  | 67ddad3a-3811-4966-83b3-86e68466d687 | 20260402 | Status |  |  | SingleBit | 3321 | FALSE
GTD_AL13_52-13_79_1 |  | 79 LIGA | GTD_AL13_52-13_79_1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_79_1 |  | GTD_AL13_52-13_79_1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1750 | FALSE
GTD_AL13_52-13_DR |  | RELE | GTD_AL13_52-13_DR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_DR |  | GTD_AL13_52-13_DR_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1720 | FALSE
GTD_AL22_52-22_FA |  | FASE A | GTD_AL22_52-22_FA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_FA |  | GTD_AL22_52-22_FA_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2524 | FALSE
GTD_AL22_52-22_50N1 |  | 50N 1 | GTD_AL22_52-22_50N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_50N1 |  | GTD_AL22_52-22_50N1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2532 | FALSE
GTD_AL22_52-22_81U5 |  | AJUSTE PARA 81 ESTAGIO 5 | GTD_AL22_52-22_81U5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_81U5 |  | GTD_AL22_52-22_81U5_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2544 | FALSE | FALSE | 5 | SingleCoord | 2508 | ClosePulseOn | 0.25
GTD_AL13_52-13_51F |  | 51F | GTD_AL13_52-13_51F_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_51F |  | GTD_AL13_52-13_51F_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1729 | FALSE
GTD_AL22_52-22_79_1 |  | 79 LIGA | GTD_AL22_52-22_79_1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_79_1 |  | GTD_AL22_52-22_79_1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2551 | FALSE
GTD_TR1_TR1_RTD1_DPT1 |  | DEFEITO PT100 | 267fea0b-dcc6-475d-8410-a293c70d1878 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_RTD1_DPT1 |  | e9438799-f737-46ab-be50-fdf20864d5f2 | 20260407 | Status |  |  | SingleBit | 850 | FALSE
GTD_AL13_52-13_81E2 |  | 81 ESTAGIO 2 | GTD_AL13_52-13_81E2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_81E2 |  | GTD_AL13_52-13_81E2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1745 | FALSE
GTD_AL23_52-23_51N1 |  | 51N 1 | GTD_AL23_52-23_51N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_51N1 |  | GTD_AL23_52-23_51N1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2633 | FALSE
GTD_AL13_52-13_43LR |  | 43LR | GTD_AL13_52-13_43LR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_43LR |  | GTD_AL13_52-13_43LR_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1704 | FALSE
GTD_AL14_52-14_81E5 |  | 81 ESTAGIO 5 | GTD_AL14_52-14_81E5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_81E5 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_81E5 |  | GTD_AL14_52-14_81E5_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1848 | FALSE
GTD_AL22_52-22_MOLA |  | MOLA | GTD_AL22_52-22_MOLA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_MOLA |  | GTD_AL22_52-22_MOLA_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2503 | FALSE
GTD_TR1_TR1_RTD3_DPT1 |  | DEFEITO PT100 | 28789561-fd76-43a4-9e95-5c5cde2bcd9f | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_RTD3_DPT1 |  | c8078819-b524-4e6f-903c-f1308d04caa4 | 20260407 | Status |  |  | SingleBit | 852 | FALSE
GTD_AL14_52-14_50F2 |  | 50F 2 | GTD_AL14_52-14_50F2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_50F2 |  | GTD_AL14_52-14_50F2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1828 | FALSE
GTD_SE_RET1_BATL |  | TENSAO BAIXA BATERIA | 54296d1f-98a4-4618-8222-9ede66c0e720 | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_SE_RET1_BATL |  | ed0315bc-1e4c-478b-9d7d-664bccd8cac8 | 20260408 | Status |  |  | SingleBit | 3422 | FALSE
GTD_AL22_52-22_43LR |  | 43LR | GTD_AL22_52-22_43LR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_43LR |  | GTD_AL22_52-22_43LR_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2504 | FALSE
GTD_AL22_52-22_2649 |  | 26 49 - FUNCAO TEMPERATURA | GTD_AL22_52-22_2649_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_2649 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL22_52-22_2649 |  | GTD_AL22_52-22_2649_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2556 | FALSE | FALSE | 5 | SingleCoord | 2510;2510 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_AL22_52-22_FCOM |  | COMUNIC | GTD_AL22_52-22_FCOM_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_FCOM |  | GTD_AL22_52-22_FCOM_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2521 | FALSE
GTD_AL22_52-22_DR |  | RELE | GTD_AL22_52-22_DR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_DR |  | GTD_AL22_52-22_DR_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2520 | FALSE
GTD_BP2_BP2_CCPN |  | FALTA VCC PAINEL | ce4bd4c2-4da9-4e5d-ae20-88b299d1503c | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BP2_BP2_CCPN |  | 4711d93a-f7f4-4366-8e70-db87a4978293 | 20260327 | Status |  |  | SingleBit | 3305 | FALSE
GTD_AL13_52-13_79RE |  | 79 RESET | GTD_AL13_52-13_79RE_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_79RE |  | GTD_AL13_52-13_79RE_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1753 | FALSE
GTD_AL23_52-23_43LR |  | 43LR | GTD_AL23_52-23_43LR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_43LR |  | GTD_AL23_52-23_43LR_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2604 | FALSE
GTD_AL13_52-13_TRIP |  | TRIP EXTERNO | GTD_AL13_52-13_TRIP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_TRIP |  | GTD_AL13_52-13_TRIP_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1757 | FALSE
GTD_AL14_52-14_43LR |  | 43LR | GTD_AL14_52-14_43LR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_43LR |  | GTD_AL14_52-14_43LR_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1804 | FALSE
GTD_BP1_BP1_43TC |  | 43TC | ed172675-c165-42a9-83f6-a2cf3bd95507 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT |  | Custom | Unknown | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_BP1_BP1_43TC |  | eb0ee5ff-e93f-416c-a96b-3e7523a07b75 | 20260402 | Status |  |  | SingleBit | 3200 | FALSE
GTD_AL13_52-13_51N1 |  | 51N 1 | GTD_AL13_52-13_51N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_51N1 |  | GTD_AL13_52-13_51N1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1733 | FALSE
GTD_AL13_52-13_50F2 |  | 50F 2 | GTD_AL13_52-13_50F2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_50F2 |  | GTD_AL13_52-13_50F2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1728 | FALSE
GTD_AL23_52-23_BBA1 |  | BOB AB 1 | GTD_AL23_52-23_BBA1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_BBA1 |  | GTD_AL23_52-23_BBA1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2609 | FALSE
GTD_AL22_52-22_46 |  | 46 | GTD_AL22_52-22_46_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_46 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_46 |  | GTD_AL22_52-22_46_UTR_GTD_1 | 20251121 | Status |  |  | SingleBit | 2537 | FALSE
GTD_TR2_TR2_FCTM |  | FALHA COMUNICACAO RELE MONITORAMENTO DE TEMPERATURA | 224ef28f-56ec-4ee9-bdcd-c7a67f0079b4 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_FCTM |  | 84877cb1-4200-405c-8763-a2abb934fec3 | 20260407 | Status |  |  | SingleBit | 1173 | FALSE
GTD_AL14_52-14_50N2 |  | 50N 2 | GTD_AL14_52-14_50N2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_50N2 |  | GTD_AL14_52-14_50N2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1832 | FALSE
GTD_AL22_52-22_SGFT |  | SGF_TRIP | GTD_AL22_52-22_SGFT_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_SGFT |  | GTD_AL22_52-22_SGFT_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2536 | FALSE
GTD_AL13_52-13_BBA2 |  | BOB AB 2 | GTD_AL13_52-13_BBA2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_BBA2 |  | GTD_AL13_52-13_BBA2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1710 | FALSE
GTD_AL13_52-13_79OK |  | 79 OK | GTD_AL13_52-13_79OK_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_79OK |  | GTD_AL13_52-13_79OK_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1751 | FALSE
GTD_AL23_52-23_CCMO |  | VCC MOT | GTD_AL23_52-23_CCMO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_CCMO |  | GTD_AL23_52-23_CCMO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2606 | FALSE
GTD_AL23_52-23_MOLA |  | MOLA | GTD_AL23_52-23_MOLA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_MOLA |  | GTD_AL23_52-23_MOLA_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2603 | FALSE
GTD_AL23_52-23_DR |  | RELE | GTD_AL23_52-23_DR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_DR |  | GTD_AL23_52-23_DR_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2620 | FALSE
GTD_AL22_52-22_FUTP |  | FALHA CIRCUITO TP | GTD_AL22_52-22_FUTP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_FUTP |  | GTD_AL22_52-22_FUTP_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2555 | FALSE
GTD_AL14_52-14_79_1 |  | 79 LIGA | GTD_AL14_52-14_79_1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_79_1 |  | GTD_AL14_52-14_79_1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1850 | FALSE
GTD_AL22_52-22_81E4 |  | 81 ESTAGIO 4 | GTD_AL22_52-22_81E4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_81E4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_81E4 |  | GTD_AL22_52-22_81E4_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2548 | FALSE
GTD_AL14_52-14_43TC |  | 43TC | GTD_AL14_52-14_43TC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_43TC |  | GTD_AL14_52-14_43TC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1815 | FALSE
GTD_AL22_52-22_81E2 |  | 81 ESTAGIO 2 | GTD_AL22_52-22_81E2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_81E2 |  | GTD_AL22_52-22_81E2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2546 | FALSE
GTD_AL22_52-22_50F1 |  | 50F 1 | GTD_AL22_52-22_50F1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_50F1 |  | GTD_AL22_52-22_50F1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2528 | FALSE
GTD_AL13_52-13_SGFT |  | SGF_TRIP | GTD_AL13_52-13_SGFT_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_SGFT |  | GTD_AL13_52-13_SGFT_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1735 | FALSE
GTD_AL22_52-22_79OK |  | 79 OK | GTD_AL22_52-22_79OK_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_79OK |  | GTD_AL22_52-22_79OK_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2552 | FALSE
GTD_AL22_52-22_81 |  | 81 | GTD_AL22_52-22_81_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL22_52-22_81 |  | GTD_AL22_52-22_81_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2538 | FALSE | FALSE | 15 | SingleCoord | 2503;2503 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL23_52-23_50N2 |  | 50N 2 | GTD_AL23_52-23_50N2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_50N2 |  | GTD_AL23_52-23_50N2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2632 | FALSE
GTD_AL22_52-22_81U1 |  | AJUSTE PARA 81 ESTAGIO 1 | GTD_AL22_52-22_81U1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_81U1 |  | GTD_AL22_52-22_81U1_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2540 | FALSE | FALSE | 5 | SingleCoord | 2504 | ClosePulseOn | 0.25
GTD_AL13_52-13_FB |  | FASE B | GTD_AL13_52-13_FB_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_FB |  | GTD_AL13_52-13_FB_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1724 | FALSE
GTD_AL22_52-22_81E5 |  | 81 ESTAGIO 5 | GTD_AL22_52-22_81E5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_81E5 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_81E5 |  | GTD_AL22_52-22_81E5_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2549 | FALSE
GTD_AL23_52-23_50F2 |  | 50F 2 | GTD_AL23_52-23_50F2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_50F2 |  | GTD_AL23_52-23_50F2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2628 | FALSE
GTD_AL13_52-13_46 |  | 46 | GTD_AL13_52-13_46_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_46 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_46 |  | GTD_AL13_52-13_46_UTR_GTD_1 | 20251121 | Status |  |  | SingleBit | 1736 | FALSE
GTD_AL13_52-13_50N2 |  | 50N 2 | GTD_AL13_52-13_50N2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_50N2 |  | GTD_AL13_52-13_50N2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1732 | FALSE
GTD_AL14_52-14_51N1 |  | 51N 1 | GTD_AL14_52-14_51N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_51N1 |  | GTD_AL14_52-14_51N1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1833 | FALSE
GTD_AL23_52-23_43TC |  | 43TC | GTD_AL23_52-23_43TC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_43TC |  | GTD_AL23_52-23_43TC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2615 | FALSE
GTD_AL13_52-13_81E5 |  | 81 ESTAGIO 5 | GTD_AL13_52-13_81E5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_81E5 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_81E5 |  | GTD_AL13_52-13_81E5_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1748 | FALSE
GTD_AL22_52-22_50N2 |  | 50N 2 | GTD_AL22_52-22_50N2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_50N2 |  | GTD_AL22_52-22_50N2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2533 | FALSE
GTD_AL14_52-14_50N1 |  | 50N 1 | GTD_AL14_52-14_50N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_50N1 |  | GTD_AL14_52-14_50N1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1831 | FALSE
GTD_AL22_52-22_81U3 |  | AJUSTE PARA 81 ESTAGIO 3 | GTD_AL22_52-22_81U3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_81U3 |  | GTD_AL22_52-22_81U3_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2542 | FALSE | FALSE | 5 | SingleCoord | 2506 | ClosePulseOn | 0.25
GTD_AL22_52-22_81E1 |  | 81 ESTAGIO 1 | GTD_AL22_52-22_81E1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_81E1 |  | GTD_AL22_52-22_81E1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2545 | FALSE
GTD_AL22_52-22_CCMO |  | VCC MOT | GTD_AL22_52-22_CCMO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_CCMO |  | GTD_AL22_52-22_CCMO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2506 | FALSE
GTD_AL14_52-14_51F |  | 51F | GTD_AL14_52-14_51F_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_51F |  | GTD_AL14_52-14_51F_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1829 | FALSE
GTD_AL23_52-23_FSIN |  | FALHA SINCRONISMO IRIG-B | GTD_AL23_52-23_FSIN_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_FSIN |  | GTD_AL23_52-23_FSIN_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2618 | FALSE
GTD_AL23_52-23_81E1 |  | 81 ESTAGIO 1 | GTD_AL23_52-23_81E1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_81E1 |  | GTD_AL23_52-23_81E1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2644 | FALSE
GTD_AL14_52-14_46 |  | 46 | GTD_AL14_52-14_46_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_46 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_46 |  | GTD_AL14_52-14_46_UTR_GTD_1 | 20251121 | Status |  |  | SingleBit | 1836 | FALSE
GTD_AL14_52-14_79RE |  | 79 RESET | GTD_AL14_52-14_79RE_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_79RE |  | GTD_AL14_52-14_79RE_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1853 | FALSE
GTD_AL13_52-13_50N1 |  | 50N 1 | GTD_AL13_52-13_50N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_50N1 |  | GTD_AL13_52-13_50N1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1731 | FALSE
GTD_AL22_52-22_FB |  | FASE B | GTD_AL22_52-22_FB_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_FB |  | GTD_AL22_52-22_FB_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2525 | FALSE
GTD_AL23_52-23_79_1 |  | 79 LIGA | GTD_AL23_52-23_79_1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_79_1 |  | GTD_AL23_52-23_79_1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2650 | FALSE
GTD_AL22_52-22_BBFC |  | BOB FEC | GTD_AL22_52-22_BBFC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_BBFC |  | GTD_AL22_52-22_BBFC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2508 | FALSE
GTD_AL13_52-13_50EF |  | 50EF - END FAULT | dd7aa014-7b36-4d75-9fb8-380881a35df0 | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_50EF |  | f64d170c-3307-4128-96d7-1ec7e035194b | 20260327 | Status |  |  | SingleBit | 3236 | FALSE
GTD_AL13_52-13_81E1 |  | 81 ESTAGIO 1 | GTD_AL13_52-13_81E1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_81E1 |  | GTD_AL13_52-13_81E1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1744 | FALSE
GTD_AL14_52-14_50F1 |  | 50F 1 | GTD_AL14_52-14_50F1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_50F1 |  | GTD_AL14_52-14_50F1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1827 | FALSE
GTD_AL22_52-22_SGF |  | SGF | GTD_AL22_52-22_SGF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_SGF |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL22_52-22_SGF |  | GTD_AL22_52-22_SGF_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2535 | FALSE | FALSE | 15 | SingleCoord | 2502;2502 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL22_52-22_79 |  | 79 | GTD_AL22_52-22_79_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL22_52-22_79 |  | GTD_AL22_52-22_79_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2550 | FALSE | FALSE | 15 | SingleCoord | 2509;2509 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL14_52-14_BBA1 |  | BOB AB 1 | GTD_AL14_52-14_BBA1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_BBA1 |  | GTD_AL14_52-14_BBA1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1809 | FALSE
GTD_AL22_52-22_62BF |  | 62BF | GTD_AL22_52-22_62BF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_62BF |  | GTD_AL22_52-22_62BF_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2523 | FALSE
GTD_AL23_52-23_79OK |  | 79 OK | GTD_AL23_52-23_79OK_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_79OK |  | GTD_AL23_52-23_79OK_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2651 | FALSE
GTD_AL13_52-13_79LO |  | 79 BLOQUEADO | GTD_AL13_52-13_79LO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_79LO |  | GTD_AL13_52-13_79LO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1752 | FALSE
GTD_AL23_52-23_81E2 |  | 81 ESTAGIO 2 | GTD_AL23_52-23_81E2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_81E2 |  | GTD_AL23_52-23_81E2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2645 | FALSE
GTD_AL14_52-14_79LO |  | 79 BLOQUEADO | GTD_AL14_52-14_79LO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_79LO |  | GTD_AL14_52-14_79LO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1852 | FALSE
GTD_AL23_52-23_51F |  | 51F | GTD_AL23_52-23_51F_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_51F |  | GTD_AL23_52-23_51F_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2629 | FALSE
GTD_TR1_TR1_27CD |  | 27 - BLOQUEIO SUBTENSAO CDC | 37d02c50-77e5-4045-9bf9-120f74376d71 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_27CD |  | 7468c491-8cd5-43df-8307-7341c874433c | 20260407 | Status |  |  | SingleBit | 855 | FALSE
GTD_AL22_52-22_CCCO |  | VCC CMD | GTD_AL22_52-22_CCCO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_CCCO |  | GTD_AL22_52-22_CCCO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2507 | FALSE
GTD_AL22_52-22_50F2 |  | 50F 2 | GTD_AL22_52-22_50F2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_50F2 |  | GTD_AL22_52-22_50F2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2529 | FALSE
GTD_AL13_52-13_GOOS |  | FALHA GOOSE | GTD_AL13_52-13_GOOS_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_GOOS |  | GTD_AL13_52-13_GOOS_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1716 | FALSE
GTD_AL22_52-22_GOOS |  | FALHA GOOSE | GTD_AL22_52-22_GOOS_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_GOOS |  | GTD_AL22_52-22_GOOS_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2516 | FALSE
GTD_AL22_52-22_81U4 |  | AJUSTE PARA 81 ESTAGIO 4 | GTD_AL22_52-22_81U4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_81U4 |  | GTD_AL22_52-22_81U4_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2543 | FALSE | FALSE | 5 | SingleCoord | 2507 | ClosePulseOn | 0.25
GTD_AL14_52-14_BBA2 |  | BOB AB 2 | GTD_AL14_52-14_BBA2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_BBA2 |  | GTD_AL14_52-14_BBA2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1810 | FALSE
GTD_AL23_52-23_46 |  | 46 | GTD_AL23_52-23_46_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_46 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_46 |  | GTD_AL23_52-23_46_UTR_GTD_1 | 20251121 | Status |  |  | SingleBit | 2636 | FALSE
GTD_AL23_52-23_BBFC |  | BOB FEC | GTD_AL23_52-23_BBFC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_BBFC |  | GTD_AL23_52-23_BBFC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2608 | FALSE
GTD_AL14_52-14_79OK |  | 79 OK | GTD_AL14_52-14_79OK_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_79OK |  | GTD_AL14_52-14_79OK_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1851 | FALSE
GTD_AL23_52-23_FA |  | FASE A | GTD_AL23_52-23_FA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_FA |  | GTD_AL23_52-23_FA_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2623 | FALSE
GTD_AL14_52-14_81E1 |  | 81 ESTAGIO 1 | GTD_AL14_52-14_81E1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_81E1 |  | GTD_AL14_52-14_81E1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1844 | FALSE
GTD_AL23_52-23_FUTP |  | FALHA CIRCUITO TP | GTD_AL23_52-23_FUTP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_FUTP |  | GTD_AL23_52-23_FUTP_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2654 | FALSE
GTD_AL23_52-23_FC |  | FASE C | GTD_AL23_52-23_FC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_FC |  | GTD_AL23_52-23_FC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2625 | FALSE
GTD_AL23_52-23_GOOS |  | FALHA GOOSE | GTD_AL23_52-23_GOOS_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_GOOS |  | GTD_AL23_52-23_GOOS_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2616 | FALSE
GTD_AL13_52-13_FCOM |  | COMUNIC | GTD_AL13_52-13_FCOM_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_FCOM |  | GTD_AL13_52-13_FCOM_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1721 | FALSE
GTD_AL23_52-23_FB |  | FASE B | GTD_AL23_52-23_FB_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_FB |  | GTD_AL23_52-23_FB_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2624 | FALSE
GTD_AL13_52-13_FC |  | FASE C | GTD_AL13_52-13_FC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_FC |  | GTD_AL13_52-13_FC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1725 | FALSE
GTD_AL12_52-12_50EF |  | 50EF - END FAULT | 6055bb28-8713-4195-a761-3475a49acc3a | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_50EF |  | 18cb6b72-7c3f-4af8-9211-27109a281439 | 20260327 | Status |  |  | SingleBit | 3235 | FALSE
GTD_AL13_52-13_81E3 |  | 81 ESTAGIO 3 | GTD_AL13_52-13_81E3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_81E3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_81E3 |  | GTD_AL13_52-13_81E3_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1746 | FALSE
GTD_AL23_52-23_TOED |  | TEMPERATURA OLEO ENROLAMENTO TRIP | GTD_AL23_52-23_TOED_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_TOED |  | GTD_AL23_52-23_TOED_UTR_GTD_1 | 20251121 | Status |  |  | SingleBit | 2656 | FALSE
GTD_AL22_52-22_51F |  | 51F | GTD_AL22_52-22_51F_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_51F |  | GTD_AL22_52-22_51F_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2530 | FALSE
GTD_AL22_52-22_BBA2 |  | BOB AB 2 | GTD_AL22_52-22_BBA2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_BBA2 |  | GTD_AL22_52-22_BBA2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2510 | FALSE
GTD_AL23_52-23_50N1 |  | 50N 1 | GTD_AL23_52-23_50N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_50N1 |  | GTD_AL23_52-23_50N1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2631 | FALSE
GTD_AL14_52-14_62BF |  | 62BF | GTD_AL14_52-14_62BF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_62BF |  | GTD_AL14_52-14_62BF_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1822 | FALSE
GTD_AL14_52-14_81E4 |  | 81 ESTAGIO 4 | GTD_AL14_52-14_81E4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_81E4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_81E4 |  | GTD_AL14_52-14_81E4_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1847 | FALSE
GTD_AL13_52-13_MOLA |  | MOLA | GTD_AL13_52-13_MOLA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_MOLA |  | GTD_AL13_52-13_MOLA_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1703 | FALSE
GTD_AL23_52-23_81E5 |  | 81 ESTAGIO 5 | GTD_AL23_52-23_81E5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_81E5 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_81E5 |  | GTD_AL23_52-23_81E5_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2648 | FALSE
GTD_AL13_52-13_TOED |  | TEMPERATURA OLEO ENROLAMENTO TRIP | GTD_AL13_52-13_TOED_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_TOED |  | GTD_AL13_52-13_TOED_UTR_GTD_1 | 20251121 | Status |  |  | SingleBit | 1756 | FALSE
GTD_AL25_52-25_FC |  | FASE C | GTD_AL25_52-25_FC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_FC |  | GTD_AL25_52-25_FC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2825 | FALSE
GTD_LTGTA_LTGTA_A_67N1 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E1 | 362713d9-b0e7-48cb-889d-9f405efe1179 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_67N1 |  | GTD_DS_00088 | 20260113 | Status |  |  | SingleBit | 147 | FALSE
GTD_LTGTA_LTGTA_P_21 |  | 21 - FUNCAO DISTANCIA | b4267775-32f7-4f5f-803f-389ca34bf268 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_21 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_21 |  | GTD_DS_00032 | 20260113 | Status |  |  | SingleBit | 68 | FALSE
GTD_AL21_52-21_79LO |  | 79 BLOQUEADO | 55d66d13-f80b-4eaa-b27e-184790cd3cfb | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_79LO |  | f05143d7-7aaa-4575-b929-a8588816affd | 20230330 | Status |  |  | SingleBit | 2452 | FALSE
GTD_LTKGC_LTKGC_P_79OK |  | 79 COM SUCESSO | 3a561d06-1c71-4366-b640-8cacfbc9cffc | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_79OK |  | GTD_DS_00157 | 20260126 | Status |  |  | SingleBit | 287 | FALSE
GTD_AL12_52-12_81E2 |  | 81 ESTAGIO 2 | GTD_AL12_52-12_81E2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_81E2 |  | GTD_AL12_52-12_81E2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1645 | FALSE
GTD_LTKGC_LTKGC_A_27_T |  | 27 - TRIP SUBTENSAO | 3fe56a26-a7a7-4edc-822b-81007f91da9e | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | Unknown | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_27_T |  | GTD_DS_00194 | 20260126 | Status |  |  | SingleBit | 350 | FALSE
GTD_AL13_52-13_79 |  | 79 | GTD_AL13_52-13_79_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL13_52-13_79 |  | GTD_AL13_52-13_79_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 1749 | FALSE | FALSE | 15 | SingleCoord | 1709;1709 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TRF2_24-2_FA |  | FASE A | GTD_TRF2_24-02_FA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_FA |  | GTD_TRF2_24-02_FA_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2926 | FALSE
GTD_AL12_52-12_81U5 |  | AJUSTE PARA 81 ESTAGIO 5 | GTD_AL12_52-12_81U5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_81U5 |  | GTD_AL12_52-12_81U5_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1643 | FALSE | FALSE | 5 | SingleCoord | 1608 | ClosePulseOn | 0.25
GTD_AL12_52-12_50F2 |  | 50F 2 | GTD_AL12_52-12_50F2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_50F2 |  | GTD_AL12_52-12_50F2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1628 | FALSE
GTD_LTKGC_LTKGC_A_51N1 |  | 51 NEUTRO | a3c56fda-6e39-472e-b1b1-31eaf7f6d6e2 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_51N1 |  | GTD_DS_00180 | 20260126 | Status |  |  | SingleBit | 337 | FALSE
GTD_AL24_52-24_FUTP |  | FALHA CIRCUITO TP | GTD_AL24_52-24_FUTP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_FUTP |  | GTD_AL24_52-24_FUTP_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2754 | FALSE
GTD_AL25_52-25_62BF |  | 62BF | GTD_AL25_52-25_62BF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_62BF |  | GTD_AL25_52-25_62BF_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2822 | FALSE
GTD_LTGTA_LTGTA_A_79LO |  | 79 BLOQUEADO | d4183678-910f-4bff-8850-9fd0adb5d3b7 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_79LO |  | GTD_DS_00098 | 20260113 | Status |  |  | SingleBit | 158 | FALSE
GTD_TRF2_24-2_43LR |  | 43LR | GTD_TRF2_24-02_43LR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_43LR |  | GTD_TRF2_24-02_43LR_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2904 | FALSE
GTD_LTKGC_LTKGC_A_21Z3 |  | 21 - TRIP ZONA 3 | 149a96b5-10d1-4c0b-971b-ae5a9ce9fe64 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_21Z3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_21Z3 |  | GTD_DS_00188 | 20260126 | Status |  |  | SingleBit | 341 | FALSE
GTD_TRF1_24-1_81U4 |  | AJUSTE PARA 81 ESTAGIO 4 | GTD_TRF1_24-01_81U4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_81U4 |  | GTD_TRF1_24-01_81U4_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2045 | FALSE | FALSE | 5 | SingleCoord | 2007 | ClosePulseOn | 0.25
GTD_AL12_52-12_BBA1 |  | BOB AB 1 | GTD_AL12_52-12_BBA1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_BBA1 |  | GTD_AL12_52-12_BBA1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1609 | FALSE
GTD_TRF1_24-1_SGF |  | SGF | GTD_TRF1_24-01_SGF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_SGF |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_TRF1_24-1_SGF |  | GTD_TRF1_24-01_SGF_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2037 | FALSE | FALSE | 15 | SingleCoord | 2002;2002 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_LTKGC_LTKGC_OI |  | OPERACAO INDEVIDA SEC | d95fed4b-767b-4cbd-bf86-9572ce6be7bf | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_OI |  | GTD_DS_00221 | 20260126 | Status |  |  | SingleBit | 237 | FALSE
GTD_TRF1_24-1_81E5 |  | 81 ESTAGIO 5 | GTD_TRF1_24-01_81E5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_81E5 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-01_81E5 |  | GTD_TRF1_24-01_81E5_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2051 | FALSE
GTD_AL11_52-11_50EF |  | 50EF - END FAULT | cc343a16-469a-4650-bcb1-64a0b2b21fd2 | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_50EF |  | 7b7ff26e-da42-4c86-8026-f2efc8274a60 | 20260327 | Status |  |  | SingleBit | 3234 | FALSE
GTD_AL13_52-13_2649 |  | 26 49 - FUNCAO TEMPERATURA | GTD_AL13_52-13_2649_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_2649 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL13_52-13_2649 |  | GTD_AL13_52-13_2649_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1755 | FALSE | FALSE | 5 | SingleCoord | 1710;1710 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TRF1_24-1_43TC |  | 43TC | GTD_TRF1_24-01_43TC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_43TC |  | GTD_TRF1_24-01_43TC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2015 | FALSE
GTD_AL12_52-12_79 |  | 79 | GTD_AL12_52-12_79_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL12_52-12_79 |  | GTD_AL12_52-12_79_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 1649 | FALSE | FALSE | 15 | SingleCoord | 1609;1609 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL24_52-24_50F1 |  | 50F 1 | GTD_AL24_52-24_50F1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_50F1 |  | GTD_AL24_52-24_50F1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2727 | FALSE
GTD_LTKGC_52-3_P_FVLT |  | FALTA POTENCIAL LT | 51db72b8-eb19-46ff-8ddd-2d5220e40b38 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_52-3_P_FVLT |  | GTD_DS_00163 | 20260126 | Status |  |  | SingleBit | 296 | FALSE
GTD_BP2_BP2_DR |  | DEFEITO RELE | da3b3abb-506f-4adc-9bdb-9ff82b20293c | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_BP2_BP2_DR |  | a479e441-5372-4c24-973b-f92384abdcd3 | 20260327 | Status |  |  | SingleBit | 3317 | FALSE
GTD_AL13_52-13_DJF1 |  | DJ | GTD_AL13_52-13_DJF1_UTR_GTD_1_SwitchStatus | SwitchStatus | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_GTD_1 | GTD_AL13_52-13_DJF1 |  | GTD_AL13_52-13_DJF1_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | MultiCoord | 1700;1701 | FALSE | FALSE | 15 | SingleCoord | 1700;1700 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_LTGTA_LTGTA_A_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | a43c64e6-8bcd-44e1-ab2a-8c219755ed5f | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_67FT |  | GTD_DS_00087 | 20260113 | Status |  |  | SingleBit | 146 | FALSE
GTD_AL15_52-15_51F |  | 51F | GTD_AL15_52-15_51F_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_51F |  | GTD_AL15_52-15_51F_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1929 | FALSE
GTD_LTGTA_LTGTA_P_67F2 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E2 | e348dd44-5770-43d8-8beb-e9ad2004009a | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_67F2 |  | GTD_DS_00039 | 20260113 | Status |  |  | SingleBit | 75 | FALSE
GTD_TRF1_24-1_FC |  | FASE C | GTD_TRF1_24-01_FC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_FC |  | GTD_TRF1_24-01_FC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2028 | FALSE
GTD_TRF2_24-2_TRIP |  | TRIP EXTERNO | GTD_TRF2_24-02_TRIP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_TRIP |  | GTD_TRF2_24-02_TRIP_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2960 | FALSE
GTD_LTKGC_LTKGC_A_TEXT |  | TRIP EXTERNO | adb1f066-ed0f-4db5-a0e8-927167632278 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_TEXT |  | GTD_DS_00213 | 20260126 | Status |  |  | SingleBit | 368 | FALSE
GTD_AL24_52-24_81U3 |  | AJUSTE PARA 81 ESTAGIO 3 | GTD_AL24_52-24_81U3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_81U3 |  | GTD_AL24_52-24_81U3_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2741 | FALSE | FALSE | 5 | SingleCoord | 2706 | ClosePulseOn | 0.25
GTD_TRF2_24-2_FSIN |  | FALHA SINCRONISMO IRIG-B | GTD_TRF2_24-02_FSIN_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_FSIN |  | GTD_TRF2_24-02_FSIN_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2918 | FALSE
GTD_LTGTA_52-1_SF6B |  | BAIXA PRESSAO SF6 BLOQUEIO | 105a733c-831f-4669-89d1-bbd0ea503336 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_52-1_SF6B |  | GTD_DS_00002 | 20260113 | Status |  |  | SingleBit | 4 | FALSE
GTD_AL15_52-15_DR |  | RELE | GTD_AL15_52-15_DR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_DR |  | GTD_AL15_52-15_DR_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1920 | FALSE
GTD_AL25_52-25_51N1 |  | 51N 1 | GTD_AL25_52-25_51N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_51N1 |  | GTD_AL25_52-25_51N1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2833 | FALSE
GTD_TRF2_24-2_81E2 |  | 81 ESTAGIO 2 | GTD_TRF2_24-02_81E2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_81E2 |  | GTD_TRF2_24-02_81E2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2948 | FALSE
GTD_LTGTA_LTGTA_A_67 |  | 67 - FUNCAO DIRECIONAL SOBRECORRENTE | b41e2aea-b780-40cd-9ff7-b6801fd6d398 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_67 |  | GTD_DS_00084 | 20260113 | Status |  |  | SingleBit | 143 | FALSE
GTD_TRF1_24-1_DR |  | RELE | GTD_TRF1_24-01_DR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_DR |  | GTD_TRF1_24-01_DR_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2023 | FALSE
GTD_AL12_52-12_81U4 |  | AJUSTE PARA 81 ESTAGIO 4 | GTD_AL12_52-12_81U4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_81U4 |  | GTD_AL12_52-12_81U4_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1642 | FALSE | FALSE | 5 | SingleCoord | 1607 | ClosePulseOn | 0.25
GTD_LTKGC_52-3_43LR |  | 43LR | ddc333d0-f656-4017-a9e8-a1911b761043 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom___INV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_LTKGC_52-3_43LR |  | GTD_DS_00145 | 20260126 | Status |  |  | SingleBit | 206 | FALSE
GTD_LTKGC_LTKGC_P_21Z1 |  | 21 - TRIP ZONA 1 | 598af697-8c93-4ee0-8d73-aeebdddfce5e | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_21Z1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_21Z1 |  | GTD_DS_00152 | 20260126 | Status |  |  | SingleBit | 269 | FALSE
GTD_AL24_52-24_51N1 |  | 51N 1 | GTD_AL24_52-24_51N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_51N1 |  | GTD_AL24_52-24_51N1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2733 | FALSE
GTD_AL21_52-21_79RE |  | 79 RESET | cc2f21fd-bcb4-4e06-846e-35dec0ce6773 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_79RE |  | 7a8132ab-7ded-4ea8-8bdf-6aff59a39fde | 20230330 | Status |  |  | SingleBit | 2453 | FALSE
GTD_TRF2_24-2_CCCO |  | VCC CMD | GTD_TRF2_24-02_CCCO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_CCCO |  | GTD_TRF2_24-02_CCCO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2907 | FALSE
GTD_AL15_52-15_50F1 |  | 50F 1 | GTD_AL15_52-15_50F1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_50F1 |  | GTD_AL15_52-15_50F1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1927 | FALSE
GTD_AL12_52-12_81E1 |  | 81 ESTAGIO 1 | GTD_AL12_52-12_81E1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_81E1 |  | GTD_AL12_52-12_81E1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1644 | FALSE
GTD_AL25_52-25_FA |  | FASE A | GTD_AL25_52-25_FA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_FA |  | GTD_AL25_52-25_FA_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2823 | FALSE
GTD_AL13_52-13_81U3 |  | AJUSTE PARA 81 ESTAGIO 3 | GTD_AL13_52-13_81U3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_81U3 |  | GTD_AL13_52-13_81U3_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1741 | FALSE | FALSE | 5 | SingleCoord | 1706 | ClosePulseOn | 0.25
GTD_AL25_52-25_81U2 |  | AJUSTE PARA 81 ESTAGIO 2 | GTD_AL25_52-25_81U2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_81U2 |  | GTD_AL25_52-25_81U2_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2840 | FALSE | FALSE | 5 | SingleCoord | 2805 | ClosePulseOn | 0.25
GTD_LTKGC_LTKGC_P_79LO |  | 79 BLOQUEADO | 28f83778-0afd-4900-adf0-807ff9b0cb95 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_79LO |  | GTD_DS_00153 | 20260126 | Status |  |  | SingleBit | 288 | FALSE
GTD_LTGTA_LTGTA_A_62BF |  | 62BF | d524ed9b-3a1d-4e26-afa9-9b3843dcb2df | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_62BF |  | GTD_DS_00068 | 20260113 | Status |  |  | SingleBit | 127 | FALSE
GTD_LTKGC_LTKGC_A_67F2 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E2 | cc50ae33-3702-485b-9116-476fc1b53552 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_67F2 |  | GTD_DS_00192 | 20260126 | Status |  |  | SingleBit | 345 | FALSE
GTD_AL21_52-21_BBA1 |  | BOB AB 1 | 269481a8-6a9a-4a15-aabc-8c3a672f2869 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_BBA1 |  | d2c22b38-8b5e-4049-8dde-955a165a0246 | 20230330 | Status |  |  | SingleBit | 2409 | FALSE
GTD_LTGTA_LTGTA_P_FA |  | FASE A | e7eb1d8a-9d01-46f3-8643-41a1cdf3fccf | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_FA |  | GTD_DS_00022 | 20260113 | Status |  |  | SingleBit | 58 | FALSE
GTD_AL14_52-14_SGF |  | SGF | GTD_AL14_52-14_SGF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_SGF |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL14_52-14_SGF |  | GTD_AL14_52-14_SGF_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 1834 | FALSE | FALSE | 15 | SingleCoord | 1802;1802 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL15_52-15_43LR |  | 43LR | GTD_AL15_52-15_43LR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_43LR |  | GTD_AL15_52-15_43LR_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1904 | FALSE
GTD_AL25_52-25_51F |  | 51F | GTD_AL25_52-25_51F_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_51F |  | GTD_AL25_52-25_51F_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2829 | FALSE
GTD_AL15_52-15_FCOM |  | COMUNIC | GTD_AL15_52-15_FCOM_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_FCOM |  | GTD_AL15_52-15_FCOM_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1921 | FALSE
GTD_TRF2_24-2_2649 |  | 26 49 - FUNCAO TEMPERATURA | GTD_TRF2_24-02_2649_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_2649 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_TRF2_24-2_2649 |  | GTD_TRF2_24-02_2649_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2958 | FALSE | FALSE | 5 | SingleCoord | 2910;2910 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_BP2_BP2_87_87 |  | 87 | 9faec373-c893-4ba7-af8a-e174e0e221c0 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_PROT_87 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_BP2_BP2_87_87 |  | 66433446-868f-48b2-9067-c8cbc06043bc | 20260402 | Status | 30 | DirectOperate | SingleBit | 3304 | FALSE | FALSE | 5 | SingleCoord | 3300;3300 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_LTKGC_LTKGC_A_25VT |  | 25 - TRIP DIFERENCA TENSAO | 682be17c-9795-4573-9232-ff3f0265318b | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_25VT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_25VT |  | GTD_DS_00202 | 20260126 | Status |  |  | SingleBit | 362 | FALSE
GTD_AL24_52-24_FSIN |  | FALHA SINCRONISMO IRIG-B | GTD_AL24_52-24_FSIN_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_FSIN |  | GTD_AL24_52-24_FSIN_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2718 | FALSE
GTD_LTGTA_LTGTA_P_62BF |  | 62BF | 79997d37-d753-4549-afdf-72397ec72d70 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_62BF |  | GTD_DS_00021 | 20260113 | Status |  |  | SingleBit | 57 | FALSE
GTD_TRF1_24-1_DJF1 |  | DJ | GTD_TRF1_24-01_DJF1_UTR_GTD_1_SwitchStatus | SwitchStatus | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_GTD_1 | GTD_TRF1_24-1_DJF1 |  | GTD_TRF1_24-01_DJF1_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | MultiCoord | 2000;2001 | FALSE | FALSE | 15 | SingleCoord | 2000;2000 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_LTGTA_89-6_DSEC |  | SECCIONADORA | 67e3d2c2-8000-4892-821c-bbfac34fe207 | Status | GTD Trans | [6 empty] | GTD_LTGTA_89-6_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_89-6_DSEC |  | GTD_DS_00010 | 20260113 | Status |  |  | SingleBit | 26 | FALSE
GTD_LTGTA_LTGTA_A_81E1 |  | 81 - TRIP SUB FREQUENCIA E1 | e14e3ca2-9425-4d66-a6b1-79427537a51c | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_81E1 |  | GTD_DS_00093 | 20260113 | Status |  |  | SingleBit | 152 | FALSE
GTD_LTKGC_LTKGC_P_25AT |  | 25 - TRIP DIFERENCA DE ANGULO | 3bfd17ae-890f-4136-971d-60a2b750330a | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_25AT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_25AT |  | GTD_DS_00159 | 20260126 | Status |  |  | SingleBit | 294 | FALSE
GTD_TRF2_24-2_81U1 |  | AJUSTE PARA 81 ESTAGIO 1 | GTD_TRF2_24-02_81U1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_81U1 |  | GTD_TRF2_24-02_81U1_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2942 | FALSE | FALSE | 5 | SingleCoord | 2904 | ClosePulseOn | 0.25
GTD_AL24_52-24_62BF |  | 62BF | GTD_AL24_52-24_62BF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_62BF |  | GTD_AL24_52-24_62BF_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2722 | FALSE
GTD_AL15_52-15_BBA1 |  | BOB AB 1 | GTD_AL15_52-15_BBA1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_BBA1 |  | GTD_AL15_52-15_BBA1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1909 | FALSE
GTD_AL25_52-25_50N2 |  | 50N 2 | GTD_AL25_52-25_50N2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_50N2 |  | GTD_AL25_52-25_50N2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2832 | FALSE
GTD_AL15_52-15_81U2 |  | AJUSTE PARA 81 ESTAGIO 2 | GTD_AL15_52-15_81U2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_81U2 |  | GTD_AL15_52-15_81U2_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1940 | FALSE | FALSE | 5 | SingleCoord | 1905 | ClosePulseOn | 0.25
GTD_LTGTA_LTGTA_P_51N1 |  | 51 NEUTRO | ec371b98-a6bb-4165-8c21-5e78dd3c6db2 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_51N1 |  | GTD_DS_00031 | 20260113 | Status |  |  | SingleBit | 67 | FALSE
GTD_AL15_52-15_FUTP |  | FALHA CIRCUITO TP | GTD_AL15_52-15_FUTP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_FUTP |  | GTD_AL15_52-15_FUTP_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1954 | FALSE
GTD_LTGTA_LTGTA_A_FC |  | FASE C | 0ba0831f-cc38-4a77-981a-e002cd8ede83 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_FC |  | GTD_DS_00071 | 20260113 | Status |  |  | SingleBit | 130 | FALSE
GTD_AL24_52-24_81U1 |  | AJUSTE PARA 81 ESTAGIO 1 | GTD_AL24_52-24_81U1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_81U1 |  | GTD_AL24_52-24_81U1_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2739 | FALSE | FALSE | 5 | SingleCoord | 2704 | ClosePulseOn | 0.25
GTD_AL12_52-12_FSIN |  | FALHA SINCRONISMO IRIG-B | GTD_AL12_52-12_FSIN_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_FSIN |  | GTD_AL12_52-12_FSIN_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1618 | FALSE
GTD_AL24_52-24_81E3 |  | 81 ESTAGIO 3 | GTD_AL24_52-24_81E3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_81E3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_81E3 |  | GTD_AL24_52-24_81E3_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2746 | FALSE
GTD_AL13_52-13_SGF |  | SGF | GTD_AL13_52-13_SGF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_SGF |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL13_52-13_SGF |  | GTD_AL13_52-13_SGF_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 1734 | FALSE | FALSE | 15 | SingleCoord | 1702;1702 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_LTKGC_LTKGC_A_59_T |  | 59 - TRIP SOBRETENSAO | 371854f4-5c85-497e-810f-bf2ac8b9f769 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | Unknown | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_59_T |  | GTD_DS_00193 | 20260126 | Status |  |  | SingleBit | 351 | FALSE
GTD_TRF2_24-2_GOOS |  | FALHA GOOSE | GTD_TRF2_24-02_GOOS_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_GOOS |  | GTD_TRF2_24-02_GOOS_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2916 | FALSE
GTD_AL13_52-13_81 |  | 81 | GTD_AL13_52-13_81_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL13_52-13_81 |  | GTD_AL13_52-13_81_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 1737 | FALSE | FALSE | 15 | SingleCoord | 1703;1703 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL12_52-12_81U2 |  | AJUSTE PARA 81 ESTAGIO 2 | GTD_AL12_52-12_81U2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_81U2 |  | GTD_AL12_52-12_81U2_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1640 | FALSE | FALSE | 5 | SingleCoord | 1605 | ClosePulseOn | 0.25
GTD_LTGTA_LTGTA_A_DR |  | DEFEITO RELE | 748e6ccb-ea4e-476a-83c8-9c133b5dbcb9 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_DR |  | GTD_DS_00066 | 20260113 | Status |  |  | SingleBit | 125 | FALSE
GTD_AL12_52-12_81U1 |  | AJUSTE PARA 81 ESTAGIO 1 | GTD_AL12_52-12_81U1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_81U1 |  | GTD_AL12_52-12_81U1_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1639 | FALSE | FALSE | 5 | SingleCoord | 1604 | ClosePulseOn | 0.25
GTD_AL25_52-25_81U3 |  | AJUSTE PARA 81 ESTAGIO 3 | GTD_AL25_52-25_81U3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_81U3 |  | GTD_AL25_52-25_81U3_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2841 | FALSE | FALSE | 5 | SingleCoord | 2806 | ClosePulseOn | 0.25
GTD_LTKGC_LTKGC_P_25FT |  | 25 - TRIP DIFERENCA FREQUENCIA | 80f76587-29c8-45cd-8de3-8d496e0ce77f | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_25FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_25FT |  | GTD_DS_00155 | 20260126 | Status |  |  | SingleBit | 293 | FALSE
GTD_AL12_52-12_FUTP |  | FALHA CIRCUITO TP | GTD_AL12_52-12_FUTP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_FUTP |  | GTD_AL12_52-12_FUTP_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1654 | FALSE
GTD_AL21_52-21_SGFT |  | SGF_TRIP | 0595031f-7ef4-447f-aabf-7004cbe20446 | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_SGFT |  | f4c0b60f-c200-4b09-9882-dbf1a2085cf6 | 20230330 | Status |  |  | SingleBit | 2435 | FALSE
GTD_LTGTA_LTGTA_P_67N1 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E1 | 8cb54435-a1d5-4c88-9587-3c312f652c47 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_67N1 |  | GTD_DS_00041 | 20260113 | Status |  |  | SingleBit | 77 | FALSE
GTD_AL15_52-15_79LO |  | 79 BLOQUEADO | GTD_AL15_52-15_79LO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_79LO |  | GTD_AL15_52-15_79LO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1952 | FALSE
GTD_AL24_52-24_SGFT |  | SGF_TRIP | GTD_AL24_52-24_SGFT_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_SGFT |  | GTD_AL24_52-24_SGFT_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2735 | FALSE
GTD_AL13_52-13_81U2 |  | AJUSTE PARA 81 ESTAGIO 2 | GTD_AL13_52-13_81U2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_81U2 |  | GTD_AL13_52-13_81U2_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1740 | FALSE | FALSE | 5 | SingleCoord | 1705 | ClosePulseOn | 0.25
GTD_LTGTA_LTGTA_A_GOOS |  | FALHA GOOSE | f2a84c3b-c7ac-45ad-88bc-79f519d292da | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_GOOS |  | GTD_DS_00064 | 20260113 | Status |  |  | SingleBit | 122 | FALSE
GTD_AL15_52-15_TRIP |  | TRIP EXTERNO | GTD_AL15_52-15_TRIP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_TRIP |  | GTD_AL15_52-15_TRIP_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1957 | FALSE
GTD_TRF1_24-1_FB |  | FASE B | GTD_TRF1_24-01_FB_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_FB |  | GTD_TRF1_24-01_FB_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2027 | FALSE
GTD_LTKGC_LTKGC_P_79_1 |  | 79 PARTIDA | 5ce06f3b-d88e-47f2-9e1c-695068abc1c0 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_79_1 |  | GTD_DS_00160 | 20260126 | Status |  |  | SingleBit | 286 | FALSE
GTD_TRF2_24-2_50N2 |  | 50N 2 | GTD_TRF2_24-02_50N2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_50N2 |  | GTD_TRF2_24-02_50N2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2935 | FALSE
GTD_AL21_52-21_62BF |  | 62BF | 9a417c0c-23b9-45d5-9555-d67762e6b9e6 | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_62BF |  | d0e0ea98-ec13-47c2-a1ea-f0eda325a5a6 | 20230330 | Status |  |  | SingleBit | 2422 | FALSE
GTD_TRF1_24-1_TOED |  | TEMPERATURA OLEO ENROLAMENTO TRIP | GTD_TRF1_24-01_TOED_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_TOED |  | GTD_TRF1_24-01_TOED_UTR_GTD_1 | 20251121 | Status |  |  | SingleBit | 2059 | FALSE
GTD_AL15_52-15_BBA2 |  | BOB AB 2 | GTD_AL15_52-15_BBA2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_BBA2 |  | GTD_AL15_52-15_BBA2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1910 | FALSE
GTD_AL15_52-15_DJF1 |  | DJ | GTD_AL15_52-15_DJF1_UTR_GTD_1_SwitchStatus | SwitchStatus | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_GTD_1 | GTD_AL15_52-15_DJF1 |  | GTD_AL15_52-15_DJF1_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | MultiCoord | 1900;1901 | FALSE | FALSE | 15 | SingleCoord | 1900;1900 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_AL25_52-25_FSIN |  | FALHA SINCRONISMO IRIG-B | GTD_AL25_52-25_FSIN_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_FSIN |  | GTD_AL25_52-25_FSIN_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2818 | FALSE
GTD_TRF1_24-1_50F2 |  | 50F 2 | GTD_TRF1_24-01_50F2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_50F2 |  | GTD_TRF1_24-01_50F2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2031 | FALSE
GTD_LTGTA_LTGTA_A_67F2 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E2 | aac107dc-cbcb-4225-904d-371108c42224 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_67F2 |  | GTD_DS_00086 | 20260113 | Status |  |  | SingleBit | 145 | FALSE
GTD_AL12_52-12_79_1 |  | 79 LIGA | GTD_AL12_52-12_79_1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_79_1 |  | GTD_AL12_52-12_79_1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1650 | FALSE
GTD_LTKGC_LTKGC_P_21Z2 |  | 21 - TRIP ZONA 2 | 64c1eb39-b9f5-421c-9a70-6dc75d1d2d16 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_21Z2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_21Z2 |  | GTD_DS_00144 | 20260126 | Status |  |  | SingleBit | 270 | FALSE
GTD_AL21_52-21_BBA2 |  | BOB AB 2 | ca65d56e-65bc-429c-a9f4-cb987ca9b807 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_BBA2 |  | 4f71505a-8366-4bb7-8644-6a50fe7764a7 | 20230330 | Status |  |  | SingleBit | 2410 | FALSE
GTD_LTKGC_LTKGC_A_25FT |  | 25 - TRIP DIFERENCA FREQUENCIA | 062438f6-5517-4f83-b26d-b014daa66282 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_25FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_25FT |  | GTD_DS_00205 | 20260126 | Status |  |  | SingleBit | 363 | FALSE
GTD_LTGTA_LTGTA_P_51F |  | 51 FASE | 8072b7a1-4b8e-4418-9649-b2734ec60762 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_51F |  | GTD_DS_00028 | 20260113 | Status |  |  | SingleBit | 64 | FALSE
GTD_AL15_52-15_43TC |  | 43TC | GTD_AL15_52-15_43TC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_43TC |  | GTD_AL15_52-15_43TC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1915 | FALSE
GTD_TRF2_24-2_81U3 |  | AJUSTE PARA 81 ESTAGIO 3 | GTD_TRF2_24-02_81U3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_81U3 |  | GTD_TRF2_24-02_81U3_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2944 | FALSE | FALSE | 5 | SingleCoord | 2906 | ClosePulseOn | 0.25
GTD_BP1_BP1_GOOS |  | FALHA GOOSE | 936e9da3-d7b9-464a-b967-1c68735fe323 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BP1_BP1_GOOS |  | 16eeb22d-6477-4ef2-975f-deaf44f157ba | 20260327 | Status |  |  | SingleBit | 3201 | FALSE
GTD_BP1_BP1_CCPN |  | FALTA VCC PAINEL | 195c6314-f283-4dd5-847f-3e7549625d99 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BP1_BP1_CCPN |  | 3f3034e4-ea71-44ad-a64c-e364efa20a9a | 20260327 | Status |  |  | SingleBit | 3205 | FALSE
GTD_AL12_52-12_DJF1 |  | DJ | GTD_AL12_52-12_DJF1_UTR_GTD_1_SwitchStatus | SwitchStatus | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_GTD_1 | GTD_AL12_52-12_DJF1 |  | GTD_AL12_52-12_DJF1_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | MultiCoord | 1600;1601 | FALSE | FALSE | 15 | SingleCoord | 1600;1600 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_LTKGC_LTKGC_P_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | 7caddcec-1794-4e23-9503-05b4826bd525 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_67NT |  | GTD_DS_00146 | 20260126 | Status |  |  | SingleBit | 279 | FALSE
GTD_AL24_52-24_MOLA |  | MOLA | GTD_AL24_52-24_MOLA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_MOLA |  | GTD_AL24_52-24_MOLA_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2703 | FALSE
GTD_TRF1_24-1_81U5 |  | AJUSTE PARA 81 ESTAGIO 5 | GTD_TRF1_24-01_81U5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_81U5 |  | GTD_TRF1_24-01_81U5_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2046 | FALSE | FALSE | 5 | SingleCoord | 2008 | ClosePulseOn | 0.25
GTD_LTKGC_LTKGC_A_21Z2 |  | 21 - TRIP ZONA 2 | 90089104-0714-42cb-89f7-ee98d7940782 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_21Z2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_21Z2 |  | GTD_DS_00199 | 20260126 | Status |  |  | SingleBit | 340 | FALSE
GTD_AL25_52-25_46 |  | 46 | GTD_AL25_52-25_46_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_46 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_46 |  | GTD_AL25_52-25_46_UTR_GTD_1 | 20251121 | Status |  |  | SingleBit | 2836 | FALSE
GTD_LTKGC_LTKGC_A_51F |  | 51 FASE | 1b3fea42-361d-4dd1-9a32-caca4de7cb6f | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_51F |  | GTD_DS_00177 | 20260126 | Status |  |  | SingleBit | 334 | FALSE
GTD_LTGTA_LTGTA_P_81E2 |  | 81 - TRIP SUB FREQUENCIA E2 | 06af9594-7ba7-4b86-a3c7-ff8476a4d460 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_81E2 |  | GTD_DS_00047 | 20260113 | Status |  |  | SingleBit | 83 | FALSE
GTD_LTGTA_LTGTA_P_50F1 |  | 50 FASE ESTAGIO 1 | a5a15896-7f86-469f-823e-31e21d9b350a | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_50F1 |  | GTD_DS_00026 | 20260113 | Status |  |  | SingleBit | 62 | FALSE
GTD_AL24_52-24_81E4 |  | 81 ESTAGIO 4 | GTD_AL24_52-24_81E4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_81E4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_81E4 |  | GTD_AL24_52-24_81E4_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2747 | FALSE
GTD_TRF2_24-2_81U4 |  | AJUSTE PARA 81 ESTAGIO 4 | GTD_TRF2_24-02_81U4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_81U4 |  | GTD_TRF2_24-02_81U4_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2945 | FALSE | FALSE | 5 | SingleCoord | 2907 | ClosePulseOn | 0.25
GTD_LTKGC_LTKGC_A_21 |  | 21 - FUNCAO DISTANCIA | 65e4f2c1-b4a8-4cef-a300-2bbe5d6b1d1a | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_21 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_21 |  | GTD_DS_00184 | 20260126 | Status |  |  | SingleBit | 338 | FALSE
GTD_TRF2_24-2_46 |  | 46 | GTD_TRF2_24-02_46_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_46 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_46 |  | GTD_TRF2_24-02_46_UTR_GTD_1 | 20251121 | Status |  |  | SingleBit | 2939 | FALSE
GTD_AL24_52-24_TRIP |  | TRIP EXTERNO | GTD_AL24_52-24_TRIP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_TRIP |  | GTD_AL24_52-24_TRIP_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2757 | FALSE
GTD_AL14_52-14_DJF1 |  | DJ | GTD_AL14_52-14_DJF1_UTR_GTD_1_SwitchStatus | SwitchStatus | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_GTD_1 | GTD_AL14_52-14_DJF1 |  | GTD_AL14_52-14_DJF1_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | MultiCoord | 1800;1801 | FALSE | FALSE | 15 | SingleCoord | 1800;1800 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_LTGTA_LTGTA_P_FC |  | FASE C | 799b58ff-4fc5-42f8-907f-42902f91003d | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_FC |  | GTD_DS_00024 | 20260113 | Status |  |  | SingleBit | 60 | FALSE
GTD_LTKGC_LTKGC_A_FCOM |  | FALHA COMUNICACAO | c30dd7ff-ed40-4ef0-9504-a9dca04dd76a | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom___INV_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_FCOM |  | GTD_DS_00189 | 20260126 | Status |  |  | SingleBit | 326 | FALSE
GTD_AL14_52-14_50EF |  | 50EF - END FAULT | a0a63476-03ce-4fae-8adc-0a547ffd48a8 | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_50EF |  | c353df70-89d6-4712-a5fa-c0b5fc7707df | 20260327 | Status |  |  | SingleBit | 3237 | FALSE
GTD_LTGTA_LTGTA_P_50F2 |  | 50 FASE ESTAGIO 2 | 8b0bb6ab-7b72-4a5d-9e29-d4b9037d8d63 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_50F2 |  | GTD_DS_00027 | 20260113 | Status |  |  | SingleBit | 63 | FALSE
GTD_LTGTA_LTGTA_A_FCOM |  | FALHA COMUNICACAO | 9a80ad14-579b-41e9-afbf-a43cfd2bb584 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom___INV_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_FCOM |  | GTD_DS_00067 | 20260113 | Status |  |  | SingleBit | 126 | FALSE
GTD_AL24_52-24_51F |  | 51F | GTD_AL24_52-24_51F_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_51F |  | GTD_AL24_52-24_51F_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2729 | FALSE
GTD_LTGTA_LTGTA_TPIN |  | TRANSFERENCIA DE PROTECAO | d45574c0-04a1-4366-a7ed-4491df4cf394 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___COMPLETA@INCOMPLETA___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_TPIN |  | GTD_DS_00013 | 20260113 | Status |  |  | SingleBit | 36 | FALSE
GTD_TRF2_24-2_79LO |  | 79 BLOQUEADO | GTD_TRF2_24-02_79LO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_79LO |  | GTD_TRF2_24-02_79LO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2955 | FALSE
GTD_AL24_52-24_81E1 |  | 81 ESTAGIO 1 | GTD_AL24_52-24_81E1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_81E1 |  | GTD_AL24_52-24_81E1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2744 | FALSE
GTD_AL14_52-14_81U3 |  | AJUSTE PARA 81 ESTAGIO 3 | GTD_AL14_52-14_81U3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_81U3 |  | GTD_AL14_52-14_81U3_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1841 | FALSE | FALSE | 5 | SingleCoord | 1806 | ClosePulseOn | 0.25
GTD_AL25_52-25_43TC |  | 43TC | GTD_AL25_52-25_43TC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_43TC |  | GTD_AL25_52-25_43TC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2815 | FALSE
GTD_AL14_52-14_FSIN |  | FALHA SINCRONISMO IRIG-B | GTD_AL14_52-14_FSIN_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_FSIN |  | GTD_AL14_52-14_FSIN_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1818 | FALSE
GTD_AL14_52-14_SGFT |  | SGF_TRIP | GTD_AL14_52-14_SGFT_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_SGFT |  | GTD_AL14_52-14_SGFT_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1835 | FALSE
GTD_TRF1_24-1_FA |  | FASE A | GTD_TRF1_24-01_FA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_FA |  | GTD_TRF1_24-01_FA_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2026 | FALSE
GTD_LTGTA_LTGTA_P_FVLT |  | FALTA POTENCIAL LT | 2985f26e-6db6-48ad-a3ee-96a15ea75e06 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_FVLT |  | GTD_DS_00060 | 20260113 | Status |  |  | SingleBit | 96 | FALSE
GTD_TRF2_24-2_81E4 |  | 81 ESTAGIO 4 | GTD_TRF2_24-02_81E4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_81E4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_81E4 |  | GTD_TRF2_24-02_81E4_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2950 | FALSE
GTD_AL24_52-24_50N1 |  | 50N 1 | GTD_AL24_52-24_50N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_50N1 |  | GTD_AL24_52-24_50N1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2731 | FALSE
GTD_TRF2_24-2_FUTP |  | FALHA CIRCUITO TP | GTD_TRF2_24-02_FUTP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_FUTP |  | GTD_TRF2_24-02_FUTP_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2957 | FALSE
GTD_AL21_52-21_81E1 |  | 81 ESTAGIO 1 | ea0a034f-e3ff-497d-b0ed-1d291dc2b8c1 | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_81E1 |  | 36ec8d7a-f43f-4594-92cb-659375cde572 | 20230330 | Status |  |  | SingleBit | 2444 | FALSE
GTD_AL23_52-23_BBA2 |  | BOB AB 2 | GTD_AL23_52-23_BBA2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_BBA2 |  | GTD_AL23_52-23_BBA2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2610 | FALSE
GTD_AL14_52-14_FA |  | FASE A | GTD_AL14_52-14_FA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_FA |  | GTD_AL14_52-14_FA_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1823 | FALSE
GTD_AL25_52-25_81E1 |  | 81 ESTAGIO 1 | GTD_AL25_52-25_81E1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_81E1 |  | GTD_AL25_52-25_81E1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2844 | FALSE
GTD_TRF1_24-1_81U3 |  | AJUSTE PARA 81 ESTAGIO 3 | GTD_TRF1_24-01_81U3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_81U3 |  | GTD_TRF1_24-01_81U3_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2044 | FALSE | FALSE | 5 | SingleCoord | 2006 | ClosePulseOn | 0.25
GTD_TRF1_24-1_79_1 |  | 79 LIGA | GTD_TRF1_24-01_79_1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_79_1 |  | GTD_TRF1_24-01_79_1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2053 | FALSE
GTD_AL13_52-13_81U1 |  | AJUSTE PARA 81 ESTAGIO 1 | GTD_AL13_52-13_81U1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_81U1 |  | GTD_AL13_52-13_81U1_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1739 | FALSE | FALSE | 5 | SingleCoord | 1704 | ClosePulseOn | 0.25
GTD_TRF2_24-2_BBA2 |  | BOB AB 2 | GTD_TRF2_24-02_BBA2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_BBA2 |  | GTD_TRF2_24-02_BBA2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2910 | FALSE
GTD_LTKGC_LTKGC_P_GOOS |  | FALHA GOOSE | 2a6e76eb-28d3-4c62-a5e4-7745eaa75e33 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_GOOS |  | GTD_DS_00166 | 20260126 | Status |  |  | SingleBit | 252 | FALSE
GTD_AL12_52-12_51N1 |  | 51N 1 | GTD_AL12_52-12_51N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_51N1 |  | GTD_AL12_52-12_51N1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1633 | FALSE
GTD_AL21_52-21_50F1 |  | 50F 1 | 7c2c1ad0-892e-4274-a71e-5f73d4f89cb7 | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_50F1 |  | f3cf207d-1079-4419-8611-ce0a22aa823e | 20230330 | Status |  |  | SingleBit | 2427 | FALSE
GTD_LTGTA_LTGTA_P_21Z1 |  | 21 - TRIP ZONA 1 | d9ee3479-cd6b-40a7-85bd-c3961d7bb75c | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_21Z1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_21Z1 |  | GTD_DS_00033 | 20260113 | Status |  |  | SingleBit | 69 | FALSE
GTD_AL15_52-15_FC |  | FASE C | GTD_AL15_52-15_FC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_FC |  | GTD_AL15_52-15_FC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1925 | FALSE
GTD_BP1_BP1_DR |  | DEFEITO RELE | c92d657f-51eb-4361-8a47-7fe6bf4cf6f1 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_BP1_BP1_DR |  | 789123a1-45d3-46fc-890f-b2b53aa32812 | 20260327 | Status |  |  | SingleBit | 3217 | FALSE
GTD_TRF1_24-1_43LR |  | 43LR | GTD_TRF1_24-01_43LR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_43LR |  | GTD_TRF1_24-01_43LR_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2004 | FALSE
GTD_LTKGC_LTKGC_P_21Z3 |  | 21 - TRIP ZONA 3 | ba02ade5-ccc4-4528-b0ca-577c3f05eb13 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_21Z3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_21Z3 |  | GTD_DS_00142 | 20260126 | Status |  |  | SingleBit | 271 | FALSE
GTD_LTGTA_LTGTA_A_FCSF |  | FECHAMENTO SOB FALTA | 57a53924-4ab8-4aa5-984e-4fce7dc51745 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_FCSF |  | GTD_DS_00106 | 20260113 | Status |  |  | SingleBit | 167 | FALSE
GTD_AL25_52-25_81E2 |  | 81 ESTAGIO 2 | GTD_AL25_52-25_81E2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_81E2 |  | GTD_AL25_52-25_81E2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2845 | FALSE
GTD_LTGTA_LTGTA_P_FCSF |  | FECHAMENTO SOB FALTA | 2d6cab7a-9084-477b-9750-9fe0a4a3f70c | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_FCSF |  | GTD_DS_00061 | 20260113 | Status |  |  | SingleBit | 97 | FALSE
GTD_BP2_BP2_87_FA |  | FASE A | e2eeeca0-5bc8-4a9c-b159-5ba8bc2a35d4 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BP2_BP2_87_FA |  | 0fd48265-73cf-4ad7-adb4-19c5e2a77954 | 20260402 | Status |  |  | SingleBit | 3319 | FALSE
GTD_AL12_52-12_FC |  | FASE C | GTD_AL12_52-12_FC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_FC |  | GTD_AL12_52-12_FC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1625 | FALSE
GTD_AL21_52-21_50EF |  | 50EF - END FAULT | b2c19d72-990f-4fcd-a20d-3e72e6430947 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_50EF |  | 61581938-9878-4c48-9fe0-0fb3fc6896d1 | 20260327 | Status |  |  | SingleBit | 3334 | FALSE
GTD_LTGTA_LTGTA_MDLT |  | DJAUX TP LT | 371bd7b2-60c1-412a-a8eb-4bc154a74a62 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_MDLT |  | GTD_DS_00015 | 20260113 | Status |  |  | SingleBit | 38 | FALSE
GTD_BC3_52-16_50EF |  | 50EF - END FAULT | 1bcce5ed-3f88-46c3-8246-1fcbd90a73f6 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-16_50EF |  | 7ffe55a5-2227-4f5f-86fe-6e4f9b3d4afd | 20260327 | Status |  |  | SingleBit | 3340 | FALSE
GTD_AL13_52-13_50F1 |  | 50F 1 | GTD_AL13_52-13_50F1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_50F1 |  | GTD_AL13_52-13_50F1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1727 | FALSE
GTD_AL12_52-12_51N |  | 51N | GTD_AL12_52-12_51N_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL12_52-12_51N |  | GTD_AL12_52-12_51N_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 1630 | FALSE | FALSE | 15 | SingleCoord | 1601;1601 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TRF2_24-2_81U2 |  | AJUSTE PARA 81 ESTAGIO 2 | GTD_TRF2_24-02_81U2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_81U2 |  | GTD_TRF2_24-02_81U2_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2943 | FALSE | FALSE | 5 | SingleCoord | 2905 | ClosePulseOn | 0.25
GTD_LTKGC_LTKGC_P_67N1 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E1 | a0f16224-6c63-49bd-a50b-aea53407177f | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_67N1 |  | GTD_DS_00148 | 20260126 | Status |  |  | SingleBit | 277 | FALSE
GTD_AL15_52-15_GOOS |  | FALHA GOOSE | GTD_AL15_52-15_GOOS_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_GOOS |  | GTD_AL15_52-15_GOOS_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1916 | FALSE
GTD_TRF1_24-1_81U2 |  | AJUSTE PARA 81 ESTAGIO 2 | GTD_TRF1_24-01_81U2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_81U2 |  | GTD_TRF1_24-01_81U2_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2043 | FALSE | FALSE | 5 | SingleCoord | 2005 | ClosePulseOn | 0.25
GTD_AL24_52-24_51N |  | 51N | GTD_AL24_52-24_51N_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL24_52-24_51N |  | GTD_AL24_52-24_51N_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2730 | FALSE | FALSE | 15 | SingleCoord | 2701;2701 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_LTKGC_52-3_BBFC |  | BOBINA FECHAMENTO | 0bd645bd-d543-405f-8fef-0f8bd7b11b7e | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_52-3_BBFC |  | GTD_DS_00224 | 20260126 | Status |  |  | SingleBit | 207 | FALSE
GTD_AL24_52-24_FCOM |  | COMUNIC | GTD_AL24_52-24_FCOM_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_FCOM |  | GTD_AL24_52-24_FCOM_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2721 | FALSE
GTD_AL13_52-13_81U4 |  | AJUSTE PARA 81 ESTAGIO 4 | GTD_AL13_52-13_81U4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_81U4 |  | GTD_AL13_52-13_81U4_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1742 | FALSE | FALSE | 5 | SingleCoord | 1707 | ClosePulseOn | 0.25
GTD_LTGTA_LTGTA_P_79LO |  | 79 BLOQUEADO | a36ecf75-cc35-473d-ab3f-39a43563d9c0 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_79LO |  | GTD_DS_00052 | 20260113 | Status |  |  | SingleBit | 88 | FALSE
GTD_LTGTA_52-1_MOLA |  | MOLA | 137992f2-cae9-45d6-967a-91dd1c329db8 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_52-1_MOLA |  | GTD_DS_00111 | 20260113 | Status |  |  | SingleBit | 5 | FALSE
GTD_AL14_52-14_CCCO |  | VCC CMD | GTD_AL14_52-14_CCCO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_CCCO |  | GTD_AL14_52-14_CCCO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1807 | FALSE
GTD_TRF1_24-1_GOOS |  | FALHA GOOSE | GTD_TRF1_24-01_GOOS_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_GOOS |  | GTD_TRF1_24-01_GOOS_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2016 | FALSE
GTD_LTKGC_LTKGC_A_21Z4 |  | 21 - TRIP ZONA 4 | 5180e6ab-87f9-47a4-a7a8-228f8f7b4336 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_21Z4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_21Z4 |  | GTD_DS_00182 | 20260126 | Status |  |  | SingleBit | 342 | FALSE
GTD_AL24_52-24_FC |  | FASE C | GTD_AL24_52-24_FC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_FC |  | GTD_AL24_52-24_FC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2725 | FALSE
GTD_AL25_52-25_BBFC |  | BOB FEC | GTD_AL25_52-25_BBFC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_BBFC |  | GTD_AL25_52-25_BBFC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2808 | FALSE
GTD_AL23_52-23_81U2 |  | AJUSTE PARA 81 ESTAGIO 2 | GTD_AL23_52-23_81U2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_81U2 |  | GTD_AL23_52-23_81U2_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2640 | FALSE | FALSE | 5 | SingleCoord | 2605 | ClosePulseOn | 0.25
GTD_TRF2_24-2_MOLA |  | MOLA | GTD_TRF2_24-02_MOLA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_MOLA |  | GTD_TRF2_24-02_MOLA_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2903 | FALSE
GTD_TRF1_24-1_51N |  | 51N | GTD_TRF1_24-01_51N_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_TRF1_24-1_51N |  | GTD_TRF1_24-01_51N_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2033 | FALSE | FALSE | 15 | SingleCoord | 2001;2001 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TR2_TR2_RTD2_DPT1 |  | DEFEITO PT100 | 9ef5622f-8f0c-4b3e-bfec-6cbd77550f58 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_RTD2_DPT1 |  | b9842a7e-89b8-4dfc-8e2a-c418a260b92d | 20260407 | Status |  |  | SingleBit | 1167 | FALSE
GTD_IB_52-18_51N1 |  | 51N 1 | 51bd965d-8e24-488a-916c-df783af793e1 | Status | GTD Trans | [6 empty] | GTD_IB_52-160_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_51N1 |  | 89f7b339-92e1-4810-b3b1-813035bb4778 |  | Status |  |  | SingleBit | 2332 | FALSE
GTD_LTGTA_LTGTA_A_N |  | NEUTRO | 1c150dce-68a1-4182-bb68-42e3e326337c | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_N |  | GTD_DS_00072 | 20260113 | Status |  |  | SingleBit | 131 | FALSE
GTD_TRF2_24-2_79_1 |  | 79 LIGA | GTD_TRF2_24-02_79_1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_79_1 |  | GTD_TRF2_24-02_79_1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2953 | FALSE
GTD_LTKGC_LTKGC_A_67 |  | 67 - FUNCAO DIRECIONAL SOBRECORRENTE | 9dfe1713-c3e8-4dff-a574-efd2abc4a49c | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_67 |  | GTD_DS_00183 | 20260126 | Status |  |  | SingleBit | 343 | FALSE
GTD_AL24_52-24_79RE |  | 79 RESET | GTD_AL24_52-24_79RE_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_79RE |  | GTD_AL24_52-24_79RE_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2753 | FALSE
GTD_AL12_52-12_FA |  | FASE A | GTD_AL12_52-12_FA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_FA |  | GTD_AL12_52-12_FA_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1623 | FALSE
GTD_LTKGC_LTKGC_P_81E2 |  | 81 - TRIP SUB FREQUENCIA E2 | 4bf9252e-5e35-4810-bc48-f3f22f023fd9 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_81E2 |  | GTD_DS_00149 | 20260126 | Status |  |  | SingleBit | 283 | FALSE
GTD_TRF2_24-2_SGFT |  | SGF_TRIP | GTD_TRF2_24-02_SGFT_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_SGFT |  | GTD_TRF2_24-02_SGFT_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2938 | FALSE
GTD_LTGTA_LTGTA_A_TEXT |  | TRIP EXTERNO | cf0e8dbc-98af-413d-a849-ec41e189f70a | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_TEXT |  | GTD_DS_00107 | 20260113 | Status |  |  | SingleBit | 168 | FALSE
GTD_AL23_52-23_51N |  | 51N | GTD_AL23_52-23_51N_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL23_52-23_51N |  | GTD_AL23_52-23_51N_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2630 | FALSE | FALSE | 15 | SingleCoord | 2601;2601 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TRF1_24-1_CCCO |  | VCC CMD | GTD_TRF1_24-01_CCCO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_CCCO |  | GTD_TRF1_24-01_CCCO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2007 | FALSE
GTD_AL24_52-24_81U4 |  | AJUSTE PARA 81 ESTAGIO 4 | GTD_AL24_52-24_81U4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_81U4 |  | GTD_AL24_52-24_81U4_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2742 | FALSE | FALSE | 5 | SingleCoord | 2707 | ClosePulseOn | 0.25
GTD_AL12_52-12_MOLA |  | MOLA | GTD_AL12_52-12_MOLA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_MOLA |  | GTD_AL12_52-12_MOLA_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1603 | FALSE
GTD_TRF2_24-2_BBA1 |  | BOB AB 1 | GTD_TRF2_24-02_BBA1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_BBA1 |  | GTD_TRF2_24-02_BBA1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2909 | FALSE
GTD_AL21_52-21_81E2 |  | 81 ESTAGIO 2 | 38573281-17dc-404c-b2f4-c3db79a8cdbc | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_81E2 |  | 4458a115-396b-455b-acbf-4fdc77e99010 | 20230330 | Status |  |  | SingleBit | 2445 | FALSE
GTD_LTGTA_LTGTA_P_FB |  | FASE B | c7db16ee-c478-4260-8de5-8ff45963eb7d | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_FB |  | GTD_DS_00023 | 20260113 | Status |  |  | SingleBit | 59 | FALSE
GTD_AL14_52-14_51N |  | 51N | GTD_AL14_52-14_51N_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL14_52-14_51N |  | GTD_AL14_52-14_51N_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 1830 | FALSE | FALSE | 15 | SingleCoord | 1801;1801 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_LTKGC_LTKGC_A_FCSF |  | FECHAMENTO SOB FALTA | 923109df-7a2b-425d-b9af-19bec9518997 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_FCSF |  | GTD_DS_00210 | 20260126 | Status |  |  | SingleBit | 367 | FALSE
GTD_AL15_52-15_BBFC |  | BOB FEC | GTD_AL15_52-15_BBFC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_BBFC |  | GTD_AL15_52-15_BBFC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1908 | FALSE
GTD_AL13_52-13_BBA1 |  | BOB AB 1 | GTD_AL13_52-13_BBA1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_BBA1 |  | GTD_AL13_52-13_BBA1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1709 | FALSE
GTD_LTGTA_LTGTA_A_FVLT |  | FALTA POTENCIAL LT | 828635e2-ed61-4966-85e0-4fd28be12498 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_FVLT |  | GTD_DS_00105 | 20260113 | Status |  |  | SingleBit | 166 | FALSE
GTD_TRF1_24-1_BBA2 |  | BOB AB 2 | GTD_TRF1_24-01_BBA2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_BBA2 |  | GTD_TRF1_24-01_BBA2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2010 | FALSE
GTD_LTGTA_LTGTA_A_FB |  | FASE B | 53c2996d-1c05-44b3-9b6d-3091ece925bd | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_FB |  | GTD_DS_00070 | 20260113 | Status |  |  | SingleBit | 129 | FALSE
GTD_AL12_52-12_79LO |  | 79 BLOQUEADO | GTD_AL12_52-12_79LO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_79LO |  | GTD_AL12_52-12_79LO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1652 | FALSE
GTD_TRF2_24-2_FC |  | FASE C | GTD_TRF2_24-02_FC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_FC |  | GTD_TRF2_24-02_FC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2928 | FALSE
GTD_LTKGC_LTKGC_P_79RE |  | 79 RESET | 22d0a98a-68e3-4117-a59c-6d13634b7cba | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_79RE |  | GTD_DS_00162 | 20260126 | Status |  |  | SingleBit | 289 | FALSE
GTD_LTGTA_LTGTA_P_67 |  | 67 - FUNCAO DIRECIONAL SOBRECORRENTE | b83266b6-bc8e-46c4-b7ba-cc408ea8702e | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_67 |  | GTD_DS_00037 | 20260113 | Status |  |  | SingleBit | 73 | FALSE
GTD_AL15_52-15_CCMO |  | VCC MOT | GTD_AL15_52-15_CCMO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_CCMO |  | GTD_AL15_52-15_CCMO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1906 | FALSE
GTD_AL25_52-25_FB |  | FASE B | GTD_AL25_52-25_FB_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_FB |  | GTD_AL25_52-25_FB_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2824 | FALSE
GTD_TRF1_24-1_50F1 |  | 50F 1 | GTD_TRF1_24-01_50F1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_50F1 |  | GTD_TRF1_24-01_50F1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2030 | FALSE
GTD_LTKGC_LTKGC_A_25AT |  | 25 - TRIP DIFERENCA DE ANGULO | e797cd62-e09c-47ab-8b39-95252143585f | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_25AT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_25AT |  | GTD_DS_00204 | 20260126 | Status |  |  | SingleBit | 364 | FALSE
GTD_TRF2_24-2_79OK |  | 79 OK | GTD_TRF2_24-02_79OK_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_79OK |  | GTD_TRF2_24-02_79OK_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2954 | FALSE
GTD_AL12_52-12_81E5 |  | 81 ESTAGIO 5 | GTD_AL12_52-12_81E5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_81E5 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_81E5 |  | GTD_AL12_52-12_81E5_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1648 | FALSE
GTD_LTKGC_LTKGC_P_N |  | NEUTRO | c9714238-b31c-4a4f-92a9-3d508275a849 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_N |  | GTD_DS_00132 | 20260126 | Status |  |  | SingleBit | 261 | FALSE
GTD_AL12_52-12_FB |  | FASE B | GTD_AL12_52-12_FB_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_FB |  | GTD_AL12_52-12_FB_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1624 | FALSE
GTD_AL23_52-23_50EF |  | 50EF - END FAULT | b3b4041e-02e9-47f0-8c6c-287b36d4b060 | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_50EF |  | 80941226-44e4-4604-acf3-53b10fe9d604 | 20260327 | Status |  |  | SingleBit | 3336 | FALSE
GTD_AL21_52-21_50F2 |  | 50F 2 | a9638b88-3594-47ad-b671-6b671a940152 | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_50F2 |  | b89a2189-a863-4ae9-a80d-4c75f65e14fb | 20230330 | Status |  |  | SingleBit | 2428 | FALSE
GTD_AL15_52-15_81E5 |  | 81 ESTAGIO 5 | GTD_AL15_52-15_81E5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_81E5 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_81E5 |  | GTD_AL15_52-15_81E5_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1948 | FALSE
GTD_LTKGC_LTKGC_A_FUTP |  | FALHA FUSIVEL TP | 9e8dbd4d-242b-4c4a-a4ff-018a1b381dcb | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_FUTP |  | GTD_DS_00208 | 20260126 | Status |  |  | SingleBit | 365 | FALSE
GTD_AL25_52-25_FUTP |  | FALHA CIRCUITO TP | GTD_AL25_52-25_FUTP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_FUTP |  | GTD_AL25_52-25_FUTP_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2854 | FALSE
GTD_TRF2_24-2_50F1 |  | 50F 1 | GTD_TRF2_24-02_50F1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_50F1 |  | GTD_TRF2_24-02_50F1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2930 | FALSE
GTD_LTKGC_LTKGC_P_67F2 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E2 | c321e4ad-0684-4704-a510-24b8c432f216 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_67F2 |  | GTD_DS_00141 | 20260126 | Status |  |  | SingleBit | 275 | FALSE
GTD_AL12_52-12_FCOM |  | COMUNIC | GTD_AL12_52-12_FCOM_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_FCOM |  | GTD_AL12_52-12_FCOM_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1621 | FALSE
GTD_LTGTA_LTGTA_A_81O1 |  | 81 - TRIP SOBRE FREQUENCIA E1 | 48c0f058-e418-4ac8-8640-7288f6bcfcf1 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_81O1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_81O1 |  | GTD_DS_00095 | 20260113 | Status |  |  | SingleBit | 154 | FALSE
GTD_LTKGC_LTKGC_A_67F1 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E1 | 86b59b4a-2721-487a-a929-6bdacbe83ed4 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_67F1 |  | GTD_DS_00186 | 20260126 | Status |  |  | SingleBit | 344 | FALSE
GTD_BP1_BP1_87_FB |  | FASE B | 77c36e37-37d2-4aa8-ad2a-bbd7060fd7cd | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BP1_BP1_87_FB |  | eb364fd3-56d6-4f21-b408-2121faad48cc | 20260402 | Status |  |  | SingleBit | 3220 | FALSE
GTD_AL14_52-14_81U5 |  | AJUSTE PARA 81 ESTAGIO 5 | GTD_AL14_52-14_81U5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_81U5 |  | GTD_AL14_52-14_81U5_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1843 | FALSE | FALSE | 5 | SingleCoord | 1808 | ClosePulseOn | 0.25
GTD_AL25_52-25_BBA1 |  | BOB AB 1 | GTD_AL25_52-25_BBA1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_BBA1 |  | GTD_AL25_52-25_BBA1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2809 | FALSE
GTD_LTGTA_LTGTA_P_FCOM |  | FALHA COMUNICACAO | 83df07b7-2549-4a67-ae67-579374be9302 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom___INV_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_FCOM |  | GTD_DS_00020 | 20260113 | Status |  |  | SingleBit | 56 | FALSE
GTD_LTGTA_LTGTA_P_25ER |  | 25 FALHA SINCRONISMO | 0fe0fb78-937a-409c-8951-4f53debd9728 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_25ER |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_25ER |  | GTD_DS_00055 | 20260113 | Status |  |  | SingleBit | 91 | FALSE
GTD_TRF1_24-1_SGFT |  | SGF_TRIP | GTD_TRF1_24-01_SGFT_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_SGFT |  | GTD_TRF1_24-01_SGFT_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2038 | FALSE
GTD_LTKGC_LTKGC_A_21Z1 |  | 21 - TRIP ZONA 1 | 51435353-5bba-4cf0-a8ca-6afe28c2314b | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_21Z1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_21Z1 |  | GTD_DS_00181 | 20260126 | Status |  |  | SingleBit | 339 | FALSE
GTD_TRF2_24-2_SGF |  | SGF | GTD_TRF2_24-02_SGF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_SGF |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_TRF2_24-2_SGF |  | GTD_TRF2_24-02_SGF_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2937 | FALSE | FALSE | 15 | SingleCoord | 2902;2902 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL24_52-24_GOOS |  | FALHA GOOSE | GTD_AL24_52-24_GOOS_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_GOOS |  | GTD_AL24_52-24_GOOS_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2716 | FALSE
GTD_AL25_52-25_BBA2 |  | BOB AB 2 | GTD_AL25_52-25_BBA2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_BBA2 |  | GTD_AL25_52-25_BBA2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2810 | FALSE
GTD_AL14_52-14_81U1 |  | AJUSTE PARA 81 ESTAGIO 1 | GTD_AL14_52-14_81U1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_81U1 |  | GTD_AL14_52-14_81U1_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1839 | FALSE | FALSE | 5 | SingleCoord | 1804 | ClosePulseOn | 0.25
GTD_LTKGC_LTKGC_P_67F1 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E1 | 5c5203b0-7f73-453a-9af2-7223e88bff93 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_67F1 |  | GTD_DS_00138 | 20260126 | Status |  |  | SingleBit | 274 | FALSE
GTD_LTKGC_LTKGC_A_62BF |  | 62BF | 5f34ff5c-c9f4-45e1-8fc2-0827731afe66 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_62BF |  | GTD_DS_00191 | 20260126 | Status |  |  | SingleBit | 327 | FALSE
GTD_AL15_52-15_TOED |  | TEMPERATURA OLEO ENROLAMENTO TRIP | GTD_AL15_52-15_TOED_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_TOED |  | GTD_AL15_52-15_TOED_UTR_GTD_1 | 20251121 | Status |  |  | SingleBit | 1956 | FALSE
GTD_LTGTA_LTGTA_A_50F1 |  | 50 FASE ESTAGIO 1 | fcf67d49-67a8-459e-91d3-225b7b598832 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_50F1 |  | GTD_DS_00073 | 20260113 | Status |  |  | SingleBit | 132 | FALSE
GTD_TRF2_24-2_50F2 |  | 50F 2 | GTD_TRF2_24-02_50F2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_50F2 |  | GTD_TRF2_24-02_50F2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2931 | FALSE
GTD_LTKGC_LTKGC_P_27_T |  | 27 - TRIP SUBTENSAO | b402cd0a-16c9-49a7-9cad-40291f424d27 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_27_T |  | GTD_DS_00151 | 20260126 | Status |  |  | SingleBit | 280 | FALSE
GTD_TRF2_24-2_79RE |  | 79 RESET | GTD_TRF2_24-02_79RE_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_79RE |  | GTD_TRF2_24-02_79RE_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2956 | FALSE
GTD_AL12_52-12_CCMO |  | VCC MOT | GTD_AL12_52-12_CCMO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_CCMO |  | GTD_AL12_52-12_CCMO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1606 | FALSE
GTD_TRF1_24-1_81U1 |  | AJUSTE PARA 81 ESTAGIO 1 | GTD_TRF1_24-01_81U1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_81U1 |  | GTD_TRF1_24-01_81U1_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2042 | FALSE | FALSE | 5 | SingleCoord | 2004 | ClosePulseOn | 0.25
GTD_AL14_52-14_FUTP |  | FALHA CIRCUITO TP | GTD_AL14_52-14_FUTP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_FUTP |  | GTD_AL14_52-14_FUTP_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1854 | FALSE
GTD_AL23_52-23_DJF1 |  | DJ | GTD_AL23_52-23_DJF1_UTR_GTD_1_SwitchStatus | SwitchStatus | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_GTD_1 | GTD_AL23_52-23_DJF1 |  | GTD_AL23_52-23_DJF1_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | MultiCoord | 2600;2601 | FALSE | FALSE | 15 | SingleCoord | 2600;2600 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TRF1_24-1_BBFC |  | BOB FEC | GTD_TRF1_24-01_BBFC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_BBFC |  | GTD_TRF1_24-01_BBFC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2008 | FALSE
GTD_AL25_52-25_2649 |  | 26 49 - FUNCAO TEMPERATURA | GTD_AL25_52-25_2649_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_2649 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL25_52-25_2649 |  | GTD_AL25_52-25_2649_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2855 | FALSE | FALSE | 5 | SingleCoord | 2810;2810 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_AL24_52-24_43TC |  | 43TC | GTD_AL24_52-24_43TC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_43TC |  | GTD_AL24_52-24_43TC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2715 | FALSE
GTD_AL15_52-15_81U1 |  | AJUSTE PARA 81 ESTAGIO 1 | GTD_AL15_52-15_81U1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_81U1 |  | GTD_AL15_52-15_81U1_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1939 | FALSE | FALSE | 5 | SingleCoord | 1904 | ClosePulseOn | 0.25
GTD_AL15_52-15_51N1 |  | 51N 1 | GTD_AL15_52-15_51N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_51N1 |  | GTD_AL15_52-15_51N1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1933 | FALSE
GTD_AL21_52-21_FCOM |  | COMUNIC | 52ca5977-38f7-4e9d-a39b-ad5d32addb19 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_FCOM |  | 3b1704bb-9deb-4157-8771-a5daabe15376 | 20230330 | Status |  |  | SingleBit | 2421 | FALSE
GTD_LTGTA_LTGTA_A_25AT |  | 25 - TRIP DIFERENCA DE ANGULO | 8a6566a5-e808-47f0-ad5d-f7c6070afd15 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_25AT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_25AT |  | GTD_DS_00103 | 20260113 | Status |  |  | SingleBit | 164 | FALSE
GTD_AL15_52-15_81E4 |  | 81 ESTAGIO 4 | GTD_AL15_52-15_81E4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_81E4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_81E4 |  | GTD_AL15_52-15_81E4_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1947 | FALSE
GTD_LTKGC_LTKGC_A_79LO |  | 79 BLOQUEADO | f611cf66-457b-4eea-83fa-7a114758f8a1 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_79LO |  | GTD_DS_00207 | 20260126 | Status |  |  | SingleBit | 358 | FALSE
GTD_LTGTA_LTGTA_P_21Z4 |  | 21 - TRIP ZONA 4 | 543ef98e-7739-4910-bbbb-341e2b20dffa | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_21Z4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_21Z4 |  | GTD_DS_00036 | 20260113 | Status |  |  | SingleBit | 72 | FALSE
GTD_LTGTA_LTGTA_A_50F2 |  | 50 FASE ESTAGIO 2 | 6bd795c8-7138-4720-8c38-e57e97e2f73b | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_50F2 |  | GTD_DS_00074 | 20260113 | Status |  |  | SingleBit | 133 | FALSE
GTD_AL14_52-14_81U2 |  | AJUSTE PARA 81 ESTAGIO 2 | GTD_AL14_52-14_81U2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_81U2 |  | GTD_AL14_52-14_81U2_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1840 | FALSE | FALSE | 5 | SingleCoord | 1805 | ClosePulseOn | 0.25
GTD_LTKGC_52-3_SF6A |  | BAIXA PRESSAO SF6 ALARME | 62e53a49-5539-452e-a376-ab2d5f194d6e | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_52-3_SF6A |  | GTD_DS_00118 | 20260126 | Status |  |  | SingleBit | 203 | FALSE
GTD_LTGTA_LTGTA_A_50N1 |  | 50 NEUTRO ESTAGIO 1 | 80fe708a-9707-4d1f-89ab-52fb9848c563 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_50N1 |  | GTD_DS_00076 | 20260113 | Status |  |  | SingleBit | 135 | FALSE
GTD_BP1_BP1_87_FA |  | FASE A | d57f5af2-2cdf-4ce1-bcad-7f79009064ee | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BP1_BP1_87_FA |  | ca8f7c28-4955-4f37-9f81-4dd2bd8fc869 | 20260402 | Status |  |  | SingleBit | 3219 | FALSE
GTD_LTKGC_52-3_SF6B |  | BAIXA PRESSAO SF6 BLOQUEIO | 8130b54d-6c10-4b13-9267-c9c5463b6c7a | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_52-3_SF6B |  | GTD_DS_00119 | 20260126 | Status |  |  | SingleBit | 204 | FALSE
GTD_AL12_52-12_DR |  | RELE | GTD_AL12_52-12_DR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_DR |  | GTD_AL12_52-12_DR_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1620 | FALSE
GTD_AL23_52-23_2649 |  | 26 49 - FUNCAO TEMPERATURA | GTD_AL23_52-23_2649_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_2649 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL23_52-23_2649 |  | GTD_AL23_52-23_2649_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2655 | FALSE | FALSE | 5 | SingleCoord | 2610;2610 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TRF2_24-2_FB |  | FASE B | GTD_TRF2_24-02_FB_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_FB |  | GTD_TRF2_24-02_FB_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2927 | FALSE
GTD_AL21_52-21_50N1 |  | 50N 1 | 6f489276-530f-4f16-a221-7609f30adf96 | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_50N1 |  | 5edcb339-79a8-4678-84a4-1d84c4ed0593 | 20230330 | Status |  |  | SingleBit | 2431 | FALSE
GTD_AL15_52-15_CCCO |  | VCC CMD | GTD_AL15_52-15_CCCO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_CCCO |  | GTD_AL15_52-15_CCCO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1907 | FALSE
GTD_AL12_52-12_BBA2 |  | BOB AB 2 | GTD_AL12_52-12_BBA2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_BBA2 |  | GTD_AL12_52-12_BBA2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1610 | FALSE
GTD_LTGTA_LTGTA_A_25VT |  | 25 - TRIP DIFERENCA TENSAO | ded116a5-7225-4aaf-920c-cbc1d8cc688a | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_25VT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_25VT |  | GTD_DS_00101 | 20260113 | Status |  |  | SingleBit | 162 | FALSE
GTD_TRF2_24-2_81E1 |  | 81 ESTAGIO 1 | GTD_TRF2_24-02_81E1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_81E1 |  | GTD_TRF2_24-02_81E1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2947 | FALSE
GTD_AL22_52-22_50EF |  | 50EF - END FAULT | 46b14103-4ed5-4db1-a6d0-925bd7ec9bec | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_50EF |  | d0afd8d3-08a0-40b8-ace4-07f587bc709c | 20260327 | Status |  |  | SingleBit | 3335 | FALSE
GTD_TRF1_24-1_BBA1 |  | BOB AB 1 | GTD_TRF1_24-01_BBA1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_BBA1 |  | GTD_TRF1_24-01_BBA1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2009 | FALSE
GTD_LTKGC_LTKGC_P_FA |  | FASE A | c0cc9f48-b326-4aa2-a2db-f3c2d390e5c8 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_FA |  | GTD_DS_00124 | 20260126 | Status |  |  | SingleBit | 258 | FALSE
GTD_AL12_52-12_CCCO |  | VCC CMD | GTD_AL12_52-12_CCCO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_CCCO |  | GTD_AL12_52-12_CCCO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1607 | FALSE
GTD_AL14_52-14_TRIP |  | TRIP EXTERNO | GTD_AL14_52-14_TRIP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_TRIP |  | GTD_AL14_52-14_TRIP_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1857 | FALSE
GTD_AL14_52-14_TOED |  | TEMPERATURA OLEO ENROLAMENTO TRIP | GTD_AL14_52-14_TOED_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_TOED |  | GTD_AL14_52-14_TOED_UTR_GTD_1 | 20251121 | Status |  |  | SingleBit | 1856 | FALSE
GTD_LTGTA_LTGTA_43TC |  | 43TC | 7402f06e-f9c3-427a-a89c-bf6e3c9ff907 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_43TC |  | GTD_DS_00011 | 20260113 | Status |  |  | SingleBit | 32 | FALSE
GTD_AL25_52-25_50F2 |  | 50F 2 | GTD_AL25_52-25_50F2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_50F2 |  | GTD_AL25_52-25_50F2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2828 | FALSE
GTD_AL21_52-21_FUTP |  | FALHA CIRCUITO TP | 932d8941-0481-4883-8f97-67ff878044e6 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_FUTP |  | ec60001c-b0d5-4141-b7d1-97dc1b0d37b3 | 20230330 | Status |  |  | SingleBit | 2454 | FALSE
GTD_AL15_52-15_81E1 |  | 81 ESTAGIO 1 | GTD_AL15_52-15_81E1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_81E1 |  | GTD_AL15_52-15_81E1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1944 | FALSE
GTD_BC1_52-16_50EF |  | 50EF - END FAULT | dbdde1e0-e2fc-4697-9dd8-bf16bc2bb678 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_50EF |  | 4acfd2eb-0d35-4c20-88ec-97ca747809c7 | 20260327 | Status |  |  | SingleBit | 3240 | FALSE
GTD_AL23_52-23_79RE |  | 79 RESET | GTD_AL23_52-23_79RE_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_79RE |  | GTD_AL23_52-23_79RE_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2653 | FALSE
GTD_LTKGC_LTKGC_P_81O1 |  | 81 - TRIP SOBRE FREQUENCIA E1 | f0fe1895-c8ef-4cfd-b8a6-6968bec98a5a | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_81O1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_81O1 |  | GTD_DS_00147 | 20260126 | Status |  |  | SingleBit | 284 | FALSE
GTD_TRF2_24-2_DJF1 |  | DJ | GTD_TRF2_24-02_DJF1_UTR_GTD_1_SwitchStatus | SwitchStatus | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_GTD_1 | GTD_TRF2_24-2_DJF1 |  | GTD_TRF2_24-02_DJF1_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | MultiCoord | 2900;2901 | FALSE | FALSE | 15 | SingleCoord | 2900;2900 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_AL25_52-25_81 |  | 81 | GTD_AL25_52-25_81_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL25_52-25_81 |  | GTD_AL25_52-25_81_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2837 | FALSE | FALSE | 15 | SingleCoord | 2803;2803 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL21_52-21_BBFC |  | BOB FEC | aa8b94a7-c32f-47ca-9b5d-8d4e546747c3 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_BBFC |  | 72c52d4f-836d-4d83-afbc-75b2051f9722 | 20230330 | Status |  |  | SingleBit | 2408 | FALSE
GTD_TRF1_24-1_FCOM |  | COMUNIC | GTD_TRF1_24-01_FCOM_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_FCOM |  | GTD_TRF1_24-01_FCOM_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2024 | FALSE
GTD_LTKGC_LTKGC_A_81E2 |  | 81 - TRIP SUB FREQUENCIA E2 | 34c3426a-5f4f-4955-a430-b83dafc45fd3 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_81E2 |  | GTD_DS_00195 | 20260126 | Status |  |  | SingleBit | 353 | FALSE
GTD_AL24_52-24_79OK |  | 79 OK | GTD_AL24_52-24_79OK_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_79OK |  | GTD_AL24_52-24_79OK_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2751 | FALSE
GTD_TR2_TR2_27CD |  | 27 - BLOQUEIO SUBTENSAO CDC | 1f05bb5a-4b63-4a49-afff-bc68adf29440 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_27CD |  | da8c1008-2f78-49ce-96fa-5487ef57f042 | 20260407 | Status |  |  | SingleBit | 1171 | FALSE
GTD_LTGTA_LTGTA_P_21Z2 |  | 21 - TRIP ZONA 2 | 267539cc-7725-422b-9e31-a03f7ddc1cb4 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_21Z2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_21Z2 |  | GTD_DS_00034 | 20260113 | Status |  |  | SingleBit | 70 | FALSE
GTD_LTGTA_52-1_BBA2 |  | BOBINA ABERTURA 2 | cbfc0ef6-8e1b-41eb-a498-5ec5953fffef | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_52-1_BBA2 |  | GTD_DS_00007 | 20260113 | Status |  |  | SingleBit | 9 | FALSE
GTD_AL12_52-12_81E3 |  | 81 ESTAGIO 3 | GTD_AL12_52-12_81E3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_81E3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_81E3 |  | GTD_AL12_52-12_81E3_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1646 | FALSE
GTD_LTGTA_52-1_BBA1 |  | BOBINA ABERTURA 1 | dc1f92e7-2482-4a86-8735-ad331d05e0d6 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_52-1_BBA1 |  | GTD_DS_00006 | 20260113 | Status |  |  | SingleBit | 8 | FALSE
GTD_BP1_BP1_FCOM |  | FALHA COMUNICACAO | 3e17726b-61ef-4846-a135-411d6a30e44a | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom___INV_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BP1_BP1_FCOM |  | 447c2a15-3651-4519-9f46-6566569904be | 20260327 | Status |  |  | SingleBit | 3218 | FALSE
GTD_LTKGC_LTKGC_A_50N2 |  | 50 NEUTRO ESTAGIO 2 | 3723bce7-8d74-4deb-ba4a-a01dded9c891 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_50N2 |  | GTD_DS_00179 | 20260126 | Status |  |  | SingleBit | 336 | FALSE
GTD_AL25_52-25_79RE |  | 79 RESET | GTD_AL25_52-25_79RE_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_79RE |  | GTD_AL25_52-25_79RE_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2853 | FALSE
GTD_TRF1_24-1_81 |  | 81 | GTD_TRF1_24-01_81_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_TRF1_24-01_81 |  | GTD_TRF1_24-01_81_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2040 | FALSE | FALSE | 15 | SingleCoord | 2003;2003 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_LTGTA_LTGTA_A_67F1 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E1 | 95349a6e-fa6f-4351-aecc-87558b60db0c | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_67F1 |  | GTD_DS_00085 | 20260113 | Status |  |  | SingleBit | 144 | FALSE
GTD_LTGTA_29-1_SECG |  | LAMINA DE TERRA | 987ffe0e-65bc-4e09-97f1-247a8824a98d | SwitchStatus | GTD Trans | [6 empty] | GTD_LTGTA_29-1_SEC |  | SwitchStatus | ABC | None | Read |  | null@null___ABERTO@FECHADO___SwitchStatus_D_TS_SO_terra | 1 |  | UTR_GTD_1 | GTD_LTGTA_29-1_SECG |  | GTD_DS_00116 | 20260113 | Status |  |  | MultiCoord | 28;29 | FALSE
GTD_AL15_52-15_SGFT |  | SGF_TRIP | GTD_AL15_52-15_SGFT_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_SGFT |  | GTD_AL15_52-15_SGFT_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1935 | FALSE
GTD_AL15_52-15_MOLA |  | MOLA | GTD_AL15_52-15_MOLA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_MOLA |  | GTD_AL15_52-15_MOLA_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1903 | FALSE
GTD_LTGTA_LTGTA_P_DR |  | DEFEITO RELE | 1a3de915-1e34-475a-a4f2-a5cff1f5ca99 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_DR |  | GTD_DS_00019 | 20260113 | Status |  |  | SingleBit | 55 | FALSE
GTD_TR2BT_TR2BT_50EF |  | 50EF - END FAULT | 82e6e864-923a-43b7-81c0-dc99d3334d13 | Status | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_50EF |  | 6ec22508-37b5-4a9b-a344-cb5cebd6000a | 20260327 | Status |  |  | SingleBit | 3333 | FALSE
GTD_AL24_52-24_FB |  | FASE B | GTD_AL24_52-24_FB_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_FB |  | GTD_AL24_52-24_FB_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2724 | FALSE
GTD_AL15_52-15_79 |  | 79 | GTD_AL15_52-15_79_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL15_52-15_79 |  | GTD_AL15_52-15_79_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 1949 | FALSE | FALSE | 15 | SingleCoord | 1909;1909 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_LTGTA_LTGTA_A_67N2 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E2 | 12f3e204-34af-42ce-b484-7d9368bd2761 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_67N2 |  | GTD_DS_00089 | 20260113 | Status |  |  | SingleBit | 148 | FALSE
GTD_TRF2_24-2_TOED |  | TEMPERATURA OLEO ENROLAMENTO TRIP | GTD_TRF2_24-02_TOED_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_TOED |  | GTD_TRF2_24-02_TOED_UTR_GTD_1 | 20251121 | Status |  |  | SingleBit | 2959 | FALSE
GTD_LTGTA_LTGTA_A_FA |  | FASE A | f400bde8-8d55-46f4-b056-db7001172bc7 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_FA |  | GTD_DS_00069 | 20260113 | Status |  |  | SingleBit | 128 | FALSE
GTD_LTKGC_LTKGC_A_67N1 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E1 | 2d90b930-fd6a-4455-b5bc-6c8b5e59e103 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_67N1 |  | GTD_DS_00197 | 20260126 | Status |  |  | SingleBit | 347 | FALSE
GTD_AL23_52-23_81U1 |  | AJUSTE PARA 81 ESTAGIO 1 | GTD_AL23_52-23_81U1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_81U1 |  | GTD_AL23_52-23_81U1_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2639 | FALSE | FALSE | 5 | SingleCoord | 2604 | ClosePulseOn | 0.25
GTD_AL14_52-14_79 |  | 79 | GTD_AL14_52-14_79_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL14_52-14_79 |  | GTD_AL14_52-14_79_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 1849 | FALSE | FALSE | 15 | SingleCoord | 1809;1809 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TRF1_24-1_81E3 |  | 81 ESTAGIO 3 | GTD_TRF1_24-01_81E3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_81E3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-01_81E3 |  | GTD_TRF1_24-01_81E3_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2049 | FALSE
GTD_AL12_52-12_81 |  | 81 | GTD_AL12_52-12_81_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL12_52-12_81 |  | GTD_AL12_52-12_81_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 1637 | FALSE | FALSE | 15 | SingleCoord | 1603;1603 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_LTGTA_LTGTA_MTRF |  | MODULO TRANSFERIDO | 3e7e72e1-8200-42a7-a39e-3e4792a9a491 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@TRANSFERIDA___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_MTRF |  | GTD_DS_00012 | 20260113 | Status |  |  | SingleBit | 35 | FALSE
GTD_AL15_52-15_62BF |  | 62BF | GTD_AL15_52-15_62BF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_62BF |  | GTD_AL15_52-15_62BF_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1922 | FALSE
GTD_AL21_52-21_FC |  | FASE C | 695e34a9-918c-4849-8a28-96b56508e376 | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_FC |  | df2821e1-62f6-42a4-b7dd-58c3ac0c82ae | 20230330 | Status |  |  | SingleBit | 2425 | FALSE
GTD_AL24_52-24_50N2 |  | 50N 2 | GTD_AL24_52-24_50N2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_50N2 |  | GTD_AL24_52-24_50N2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2732 | FALSE
GTD_AL14_52-14_2649 |  | 26 49 - FUNCAO TEMPERATURA | GTD_AL14_52-14_2649_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_2649 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL14_52-14_2649 |  | GTD_AL14_52-14_2649_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1855 | FALSE | FALSE | 5 | SingleCoord | 1810;1810 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_LTKGC_LTKGC_A_79_1 |  | 79 PARTIDA | ee8ad614-1103-4a4f-ba4a-d793b5e9121f | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_79_1 |  | GTD_DS_00201 | 20260126 | Status |  |  | SingleBit | 356 | FALSE
GTD_AL23_52-23_50F1 |  | 50F 1 | GTD_AL23_52-23_50F1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_50F1 |  | GTD_AL23_52-23_50F1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2627 | FALSE
GTD_LTGTA_LTGTA_A_51N1 |  | 51 NEUTRO | 0037365a-0e6f-42ce-aa0c-012b6f427a7b | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_51N1 |  | GTD_DS_00078 | 20260113 | Status |  |  | SingleBit | 137 | FALSE
GTD_AL25_52-25_81U1 |  | AJUSTE PARA 81 ESTAGIO 1 | GTD_AL25_52-25_81U1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_81U1 |  | GTD_AL25_52-25_81U1_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2839 | FALSE | FALSE | 5 | SingleCoord | 2804 | ClosePulseOn | 0.25
GTD_LTKGC_LTKGC_P_DR |  | DEFEITO RELE | bc808561-562e-4a4c-b45a-034e837f170f | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_DR |  | GTD_DS_00165 | 20260126 | Status |  |  | SingleBit | 255 | FALSE
GTD_AL12_52-12_43LR |  | 43LR | GTD_AL12_52-12_43LR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_43LR |  | GTD_AL12_52-12_43LR_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1604 | FALSE
GTD_TRF1_24-1_81E2 |  | 81 ESTAGIO 2 | GTD_TRF1_24-01_81E2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-01_81E2 |  | GTD_TRF1_24-01_81E2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2048 | FALSE
GTD_BP2_BP2_FCOM |  | FALHA COMUNICACAO | 485dacc5-134d-4c23-b056-6b113fe256e1 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom___INV_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BP2_BP2_FCOM |  | e491998e-c131-4213-a61c-7b1c4018045d | 20260327 | Status |  |  | SingleBit | 3318 | FALSE
GTD_AL21_52-21_50N2 |  | 50N 2 | a8034009-2d02-444b-9c50-38b25ba0f1d7 | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_50N2 |  | c2dabb62-ec83-4085-844d-d46bae692992 | 20230330 | Status |  |  | SingleBit | 2432 | FALSE
GTD_LTGTA_LTGTA_P_50N2 |  | 50 NEUTRO ESTAGIO 2 | ae36b620-a2bf-4781-a558-09b52b08aa60 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_50N2 |  | GTD_DS_00030 | 20260113 | Status |  |  | SingleBit | 66 | FALSE
GTD_AL14_52-14_FC |  | FASE C | GTD_AL14_52-14_FC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_FC |  | GTD_AL14_52-14_FC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1825 | FALSE
GTD_TRF1_24-1_TRIP |  | TRIP EXTERNO | GTD_TRF1_24-01_TRIP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_TRIP |  | GTD_TRF1_24-01_TRIP_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2060 | FALSE
GTD_LTGTA_LTGTA_A_25ER |  | 25 FALHA SINCRONISMO | ff6dbfa2-2d64-47d1-b58a-f9539e813594 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_25ER |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_25ER |  | GTD_DS_00100 | 20260113 | Status |  |  | SingleBit | 161 | FALSE
GTD_TRF1_24-1_FUTP |  | FALHA CIRCUITO TP | GTD_TRF1_24-01_FUTP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_FUTP |  | GTD_TRF1_24-01_FUTP_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2057 | FALSE
GTD_AL12_52-12_51F |  | 51F | GTD_AL12_52-12_51F_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_51F |  | GTD_AL12_52-12_51F_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1629 | FALSE
GTD_LTKGC_52-3_BBA1 |  | BOBINA ABERTURA 1 | 252f4d92-6da8-497f-ab69-fd09e136d899 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_52-3_BBA1 |  | GTD_DS_00120 | 20260126 | Status |  |  | SingleBit | 208 | FALSE
GTD_BP2_BP2_87_FB |  | FASE B | 79bce531-f59a-440b-8183-abc0eed27670 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BP2_BP2_87_FB |  | dfd45c70-f8ed-4d96-97bc-9e58b13f1902 | 20260402 | Status |  |  | SingleBit | 3320 | FALSE
GTD_TRF2_24-2_81E5 |  | 81 ESTAGIO 5 | GTD_TRF2_24-02_81E5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_81E5 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_81E5 |  | GTD_TRF2_24-02_81E5_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2951 | FALSE
GTD_LTGTA_89-2_DSEC |  | SECCIONADORA | a65f23c8-7074-43c8-9077-be8082457f79 | Status | GTD Trans | [6 empty] | GTD_LTGTA_89-2_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_89-2_DSEC |  | GTD_DS_00008 | 20260113 | Status |  |  | SingleBit | 16 | FALSE
GTD_AL15_52-15_79RE |  | 79 RESET | GTD_AL15_52-15_79RE_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_79RE |  | GTD_AL15_52-15_79RE_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1953 | FALSE
GTD_LTKGC_LTKGC_A_N |  | NEUTRO | 089727f6-0ea7-435b-9153-c38394697c89 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_N |  | GTD_DS_00175 | 20260126 | Status |  |  | SingleBit | 331 | FALSE
GTD_AL13_52-13_81U5 |  | AJUSTE PARA 81 ESTAGIO 5 | GTD_AL13_52-13_81U5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_81U5 |  | GTD_AL13_52-13_81U5_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1743 | FALSE | FALSE | 5 | SingleCoord | 1708 | ClosePulseOn | 0.25
GTD_AL25_52-25_MOLA |  | MOLA | GTD_AL25_52-25_MOLA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_MOLA |  | GTD_AL25_52-25_MOLA_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2803 | FALSE
GTD_LTKGC_LTKGC_P_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | 4fdd3b9e-4117-454d-83a4-2b43423db83a | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_67FT |  | GTD_DS_00143 | 20260126 | Status |  |  | SingleBit | 276 | FALSE
GTD_TRF2_24-2_81U5 |  | AJUSTE PARA 81 ESTAGIO 5 | GTD_TRF2_24-02_81U5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_81U5 |  | GTD_TRF2_24-02_81U5_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2946 | FALSE | FALSE | 5 | SingleCoord | 2908 | ClosePulseOn | 0.25
GTD_LTKGC_LTKGC_P_FCOM |  | FALHA COMUNICACAO | 0cd8ba05-31b9-4d16-961d-9b9af776d85f | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom___INV_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_FCOM |  | GTD_DS_00127 | 20260126 | Status |  |  | SingleBit | 256 | FALSE
GTD_LTKGC_LTKGC_A_81E1 |  | 81 - TRIP SUB FREQUENCIA E1 | 3b4a5d08-690e-47a4-9e90-a75feceafe98 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_81E1 |  | GTD_DS_00200 | 20260126 | Status |  |  | SingleBit | 352 | FALSE
GTD_AL24_52-24_81U5 |  | AJUSTE PARA 81 ESTAGIO 5 | GTD_AL24_52-24_81U5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_81U5 |  | GTD_AL24_52-24_81U5_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2743 | FALSE | FALSE | 5 | SingleCoord | 2708 | ClosePulseOn | 0.25
GTD_AL21_52-21_43LR |  | 43LR | 622c49eb-1f51-4680-b76b-d072a68cabb9 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_43LR |  | 3aba28ae-c4c5-4808-98b1-27aa942655c9 | 20230330 | Status |  |  | SingleBit | 2404 | FALSE
GTD_AL24_52-24_79LO |  | 79 BLOQUEADO | GTD_AL24_52-24_79LO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_79LO |  | GTD_AL24_52-24_79LO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2752 | FALSE
GTD_AL15_52-15_SGF |  | SGF | GTD_AL15_52-15_SGF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_SGF |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL15_52-15_SGF |  | GTD_AL15_52-15_SGF_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 1934 | FALSE | FALSE | 15 | SingleCoord | 1902;1902 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_LTGTA_52-1_SF6A |  | BAIXA PRESSAO SF6 ALARME | 403e166e-93a6-4e2d-99c5-7d0c46cf9d22 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_52-1_SF6A |  | GTD_DS_00001 | 20260113 | Status |  |  | SingleBit | 3 | FALSE
GTD_LTKGC_LTKGC_43TC |  | 43TC | c5138495-724e-4825-9a84-af1b38c0db9d | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_43TC |  | GTD_DS_00222 | 20260126 | Status |  |  | SingleBit | 232 | FALSE
GTD_LTGTA_LTGTA_25 |  | 25 RELE SINCRONISMO | 2217e112-585c-4eae-a28d-7086935f1cfb | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_25 |  | GTD_DS_00054 | 20260113 | Status | 30 | AutoSelectWithValue | SingleBit | 90 | FALSE | FALSE | 15 | SingleCoord | 6;6 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_LTGTA_52-1_DJF1 |  | DISJUNTOR NF | a0ad7c05-ae9d-4e33-b4a5-e7e8a4817bb6 | SwitchStatus | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_GTD_1 | GTD_LTGTA_52-1_DJF1 |  | GTD_DS_00112 | 20260113 | Status | 30 | AutoSelectWithValue | MultiCoord | 1;2 | FALSE | FALSE | 15 | SingleCoord | 0;0 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_LTGTA_LTGTA_A_25FT |  | 25 - TRIP DIFERENCA FREQUENCIA | 74e903bd-2870-4d0f-ad4c-df669b0228a5 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_25FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_25FT |  | GTD_DS_00102 | 20260113 | Status |  |  | SingleBit | 163 | FALSE
GTD_TRF2_24-2_62BF |  | 62BF | GTD_TRF2_24-02_62BF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_62BF |  | GTD_TRF2_24-02_62BF_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2925 | FALSE
GTD_LTKGC_LTKGC_A_50F2 |  | 50 FASE ESTAGIO 2 | c090d6fd-42af-4687-8ae6-146d3def3a16 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_50F2 |  | GTD_DS_00178 | 20260126 | Status |  |  | SingleBit | 333 | FALSE
GTD_BC4_52-27_50EF |  | 50EF - END FAULT | b4c04ae4-92cd-4c6a-a0e2-6e19f03f55f1 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_50EF |  | 00231fc0-753c-44c5-8b5e-479e31c619a7 | 20260327 | Status |  |  | SingleBit | 3341 | FALSE
GTD_TRF2_24-2_51N |  | 51N | GTD_TRF2_24-02_51N_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_TRF2_24-2_51N |  | GTD_TRF2_24-02_51N_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2933 | FALSE | FALSE | 15 | SingleCoord | 2901;2901 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL25_52-25_79OK |  | 79 OK | GTD_AL25_52-25_79OK_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_79OK |  | GTD_AL25_52-25_79OK_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2851 | FALSE
GTD_LTKGC_LTKGC_A_79RE |  | 79 RESET | 10cebb76-9dbb-4664-a158-71a950155bae | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_79RE |  | GTD_DS_00206 | 20260126 | Status |  |  | SingleBit | 359 | FALSE
GTD_TRF1_24-1_50N2 |  | 50N 2 | GTD_TRF1_24-01_50N2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_50N2 |  | GTD_TRF1_24-01_50N2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2035 | FALSE
GTD_AL14_52-14_MOLA |  | MOLA | GTD_AL14_52-14_MOLA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_MOLA |  | GTD_AL14_52-14_MOLA_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1803 | FALSE
GTD_LTGTA_89-6_SECB |  | SECCIONADORA BYPASS | 9214b09f-de66-4d1e-ba3c-fb29b76cc66e | SwitchStatus | GTD Trans | [6 empty] | GTD_LTGTA_89-6_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 1 |  | UTR_GTD_1 | GTD_LTGTA_89-6_SECB |  | GTD_DS_00115 | 20260113 | Status | 30 | AutoSelectWithValue | MultiCoord | 23;24 | FALSE | FALSE | 15 | SingleCoord | 3;3 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_LTGTA_LTGTA_P_25FT |  | 25 - TRIP DIFERENCA FREQUENCIA | 0856c0fe-3621-4866-b889-a7b7bdc69785 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_25FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_25FT |  | GTD_DS_00057 | 20260113 | Status |  |  | SingleBit | 93 | FALSE
GTD_TRF2_24-2_51F |  | 51F | GTD_TRF2_24-02_51F_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_51F |  | GTD_TRF2_24-02_51F_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2932 | FALSE
GTD_LTKGC_LTKGC_MDLT |  | DJAUX TP LT | 5541654a-6da8-4303-9d3f-b87b2207cbfa | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_MDLT |  | GTD_DS_00176 | 20260126 | Status |  |  | SingleBit | 238 | FALSE
GTD_TRF1_24-1_46 |  | 46 | GTD_TRF1_24-01_46_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_46 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_46 |  | GTD_TRF1_24-01_46_UTR_GTD_1 | 20251121 | Status |  |  | SingleBit | 2039 | FALSE
GTD_AL24_52-24_FA |  | FASE A | GTD_AL24_52-24_FA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_FA |  | GTD_AL24_52-24_FA_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2723 | FALSE
GTD_AL15_52-15_81U5 |  | AJUSTE PARA 81 ESTAGIO 5 | GTD_AL15_52-15_81U5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_81U5 |  | GTD_AL15_52-15_81U5_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1943 | FALSE | FALSE | 5 | SingleCoord | 1908 | ClosePulseOn | 0.25
GTD_AL21_52-21_DR |  | RELE | 5e2035ef-5ef9-4732-a0ae-2a6d60148193 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_DR |  | d0519292-d7c7-4270-88fb-549c4f9ca014 | 20230330 | Status |  |  | SingleBit | 2420 | FALSE
GTD_AL12_52-12_BBFC |  | BOB FEC | GTD_AL12_52-12_BBFC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_BBFC |  | GTD_AL12_52-12_BBFC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1608 | FALSE
GTD_AL25_52-25_43LR |  | 43LR | GTD_AL25_52-25_43LR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_43LR |  | GTD_AL25_52-25_43LR_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2804 | FALSE
GTD_AL23_52-23_81E4 |  | 81 ESTAGIO 4 | GTD_AL23_52-23_81E4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_81E4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_81E4 |  | GTD_AL23_52-23_81E4_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2647 | FALSE
GTD_LTKGC_LTKGC_P_FC |  | FASE C | 21f13404-e52c-4913-95dc-1bd3ae93399d | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_FC |  | GTD_DS_00125 | 20260126 | Status |  |  | SingleBit | 260 | FALSE
GTD_TRF1_24-1_79OK |  | 79 OK | GTD_TRF1_24-01_79OK_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_79OK |  | GTD_TRF1_24-01_79OK_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2054 | FALSE
GTD_AL25_52-25_51N |  | 51N | GTD_AL25_52-25_51N_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL25_52-25_51N |  | GTD_AL25_52-25_51N_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2830 | FALSE | FALSE | 15 | SingleCoord | 2801;2801 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL24_52-24_43LR |  | 43LR | GTD_AL24_52-24_43LR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_43LR |  | GTD_AL24_52-24_43LR_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2704 | FALSE
GTD_AL23_52-23_81U4 |  | AJUSTE PARA 81 ESTAGIO 4 | GTD_AL23_52-23_81U4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_81U4 |  | GTD_AL23_52-23_81U4_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2642 | FALSE | FALSE | 5 | SingleCoord | 2607 | ClosePulseOn | 0.25
GTD_IB_52-18_51F |  | 51F | 95c38efb-1333-456c-aaa0-edfd2618e838 | Status | GTD Trans | [6 empty] | GTD_IB_52-160_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_51F |  | a8296ba8-b4aa-411b-933f-10e830e4b8bf |  | Status |  |  | SingleBit | 2329 | FALSE
GTD_AL14_52-14_81 |  | 81 | GTD_AL14_52-14_81_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL14_52-14_81 |  | GTD_AL14_52-14_81_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 1837 | FALSE | FALSE | 15 | SingleCoord | 1803;1803 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL15_52-15_FB |  | FASE B | GTD_AL15_52-15_FB_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_FB |  | GTD_AL15_52-15_FB_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1924 | FALSE
GTD_AL13_52-13_43TC |  | 43TC | GTD_AL13_52-13_43TC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_43TC |  | GTD_AL13_52-13_43TC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1715 | FALSE
GTD_AL24_52-24_CCMO |  | VCC MOT | GTD_AL24_52-24_CCMO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_CCMO |  | GTD_AL24_52-24_CCMO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2706 | FALSE
GTD_AL14_52-14_CCMO |  | VCC MOT | GTD_AL14_52-14_CCMO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_CCMO |  | GTD_AL14_52-14_CCMO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1806 | FALSE
GTD_AL24_52-24_81U2 |  | AJUSTE PARA 81 ESTAGIO 2 | GTD_AL24_52-24_81U2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_81U2 |  | GTD_AL24_52-24_81U2_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2740 | FALSE | FALSE | 5 | SingleCoord | 2705 | ClosePulseOn | 0.25
GTD_LTKGC_LTKGC_P_FUTP |  | FALHA FUSIVEL TP | ee5cb3d0-bb37-4527-bc25-b88724d9ef97 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_FUTP |  | GTD_DS_00161 | 20260126 | Status |  |  | SingleBit | 295 | FALSE
GTD_AL12_52-12_62BF |  | 62BF | GTD_AL12_52-12_62BF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_62BF |  | GTD_AL12_52-12_62BF_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1622 | FALSE
GTD_LTGTA_52-1_BBFC |  | BOBINA FECHAMENTO | d67f5b16-4b60-4fdd-8219-d98f2db6a5ad | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_52-1_BBFC |  | GTD_DS_00005 | 20260113 | Status |  |  | SingleBit | 7 | FALSE
GTD_AL25_52-25_79 |  | 79 | GTD_AL25_52-25_79_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL25_52-25_79 |  | GTD_AL25_52-25_79_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2849 | FALSE | FALSE | 15 | SingleCoord | 2809;2809 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL12_52-12_81U3 |  | AJUSTE PARA 81 ESTAGIO 3 | GTD_AL12_52-12_81U3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_81U3 |  | GTD_AL12_52-12_81U3_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1641 | FALSE | FALSE | 5 | SingleCoord | 1606 | ClosePulseOn | 0.25
GTD_LTGTA_LTGTA_P_67N2 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E2 | 23d74f62-7fc9-490d-a421-ce0694ce2a77 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_67N2 |  | GTD_DS_00042 | 20260113 | Status |  |  | SingleBit | 78 | FALSE
GTD_AL21_52-21_51F |  | 51F | 59695486-2388-411f-acd8-131fde579b21 | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_51F |  | 35786f2e-4d2d-4c03-bc9a-273588110608 | 20230330 | Status |  |  | SingleBit | 2429 | FALSE
GTD_TR1_TR1_50CD |  | 50 - SOBRECORRENTE CDC | eeaa3348-81ab-4ef7-bc97-df62902b6705 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_50CD |  | db5cf274-ce16-4f44-a46d-7308e351e90b | 20260407 | Status |  |  | SingleBit | 853 | FALSE
GTD_LTGTA_LTGTA_79 |  | 79 - RELIGAMENTO | 38dc38ae-cc98-4c17-8ad7-d8bb178e8e10 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_79 |  | GTD_DS_00049 | 20260113 | Status | 30 | AutoSelectWithValue | SingleBit | 85 | FALSE | FALSE | 15 | SingleCoord | 4;4 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_LTGTA_LTGTA_A_79RE |  | 79 RESET | 2a037750-adf2-48fa-9671-82e09e4e4c17 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_79RE |  | GTD_DS_00099 | 20260113 | Status |  |  | SingleBit | 159 | FALSE
GTD_AL25_52-25_FCOM |  | COMUNIC | GTD_AL25_52-25_FCOM_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_FCOM |  | GTD_AL25_52-25_FCOM_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2821 | FALSE
GTD_LTKGC_LTKGC_P_FCSF |  | FECHAMENTO SOB FALTA | 3b5acbb4-2043-41a7-87d0-66586412ce7f | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_FCSF |  | GTD_DS_00167 | 20260126 | Status |  |  | SingleBit | 297 | FALSE
GTD_AL12_52-12_50F1 |  | 50F 1 | GTD_AL12_52-12_50F1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_50F1 |  | GTD_AL12_52-12_50F1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1627 | FALSE
GTD_TRF2_24-2_81E3 |  | 81 ESTAGIO 3 | GTD_TRF2_24-02_81E3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_81E3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_81E3 |  | GTD_TRF2_24-02_81E3_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2949 | FALSE
GTD_AL21_52-21_43TC |  | 43TC | d27b09cf-20b2-47aa-ab43-b672d9654e52 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_43TC |  | b3217853-8517-4c80-98ed-5355db20f29c | 20230330 | Status |  |  | SingleBit | 2415 | FALSE
GTD_AL25_52-25_SGFT |  | SGF_TRIP | GTD_AL25_52-25_SGFT_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_SGFT |  | GTD_AL25_52-25_SGFT_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2835 | FALSE
GTD_AL24_52-24_SGF |  | SGF | GTD_AL24_52-24_SGF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_SGF |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL24_52-24_SGF |  | GTD_AL24_52-24_SGF_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2734 | FALSE | FALSE | 15 | SingleCoord | 2702;2702 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL13_52-13_51N |  | 51N | GTD_AL13_52-13_51N_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL13_52-13_51N |  | GTD_AL13_52-13_51N_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 1730 | FALSE | FALSE | 15 | SingleCoord | 1701;1701 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL12_52-12_43TC |  | 43TC | GTD_AL12_52-12_43TC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_43TC |  | GTD_AL12_52-12_43TC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1615 | FALSE
GTD_AL24_52-24_81E2 |  | 81 ESTAGIO 2 | GTD_AL24_52-24_81E2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_81E2 |  | GTD_AL24_52-24_81E2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2745 | FALSE
GTD_AL25_52-25_81E5 |  | 81 ESTAGIO 5 | GTD_AL25_52-25_81E5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_81E5 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_81E5 |  | GTD_AL25_52-25_81E5_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2848 | FALSE
GTD_LTGTA_LTGTA_A_50N2 |  | 50 NEUTRO ESTAGIO 2 | 998c0f7d-34cf-43f1-8d8e-224fb0c72b60 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_50N2 |  | GTD_DS_00077 | 20260113 | Status |  |  | SingleBit | 136 | FALSE
GTD_AL12_52-12_SGFT |  | SGF_TRIP | GTD_AL12_52-12_SGFT_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_SGFT |  | GTD_AL12_52-12_SGFT_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1635 | FALSE
GTD_AL21_52-21_CCMO |  | VCC MOT | 6b7ac1ad-ec03-43b2-b0ae-8e76af28db91 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_CCMO |  | dcd98495-1ece-47bd-9b0a-0642f7c5274f | 20230330 | Status |  |  | SingleBit | 2406 | FALSE
GTD_AL15_52-15_79OK |  | 79 OK | GTD_AL15_52-15_79OK_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_79OK |  | GTD_AL15_52-15_79OK_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1951 | FALSE
GTD_LTGTA_89-4_SECF |  | SECCIONADORA FONTE | b62ced3e-3fa4-4d85-8464-3c4511009a9f | SwitchStatus | GTD Trans | [6 empty] | GTD_LTGTA_89-4_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 2 |  | UTR_GTD_1 | GTD_LTGTA_89-4_SECF |  | GTD_DS_00114 | 20260113 | Status | 30 | AutoSelectWithValue | MultiCoord | 18;19 | FALSE | FALSE | 15 | SingleCoord | 2;2 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_AL24_52-24_81 |  | 81 | GTD_AL24_52-24_81_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL24_52-24_81 |  | GTD_AL24_52-24_81_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2737 | FALSE | FALSE | 15 | SingleCoord | 2703;2703 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL14_52-14_FB |  | FASE B | GTD_AL14_52-14_FB_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_FB |  | GTD_AL14_52-14_FB_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1824 | FALSE
GTD_LTGTA_LTGTA_A_79OK |  | 79 COM SUCESSO | 266122d4-3734-4c42-bc73-0141bea6f8f9 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_79OK |  | GTD_DS_00097 | 20260113 | Status |  |  | SingleBit | 157 | FALSE
GTD_TRF1_24-1_62BF |  | 62BF | GTD_TRF1_24-01_62BF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_62BF |  | GTD_TRF1_24-01_62BF_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2025 | FALSE
GTD_TR2_TR2_RTD1_DPT1 |  | DEFEITO PT100 | 31ceb2fb-35f7-4c28-a9fa-a6fbe5b03b44 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_RTD1_DPT1 |  | 8aae690b-1149-4e14-91eb-42982cf570b5 | 20260407 | Status |  |  | SingleBit | 1166 | FALSE
GTD_AL15_52-15_50N2 |  | 50N 2 | GTD_AL15_52-15_50N2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_50N2 |  | GTD_AL15_52-15_50N2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1932 | FALSE
GTD_AL25_52-25_81E3 |  | 81 ESTAGIO 3 | GTD_AL25_52-25_81E3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_81E3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_81E3 |  | GTD_AL25_52-25_81E3_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2846 | FALSE
GTD_LTKGC_LTKGC_P_59_T |  | 59 - TRIP SOBRETENSAO | 4d1683e2-e60a-41a7-af3d-b36537a50554 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | Unknown | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_59_T |  | GTD_DS_00212 | 20260126 | Status |  |  | SingleBit | 281 | FALSE
GTD_LTGTA_LTGTA_AJG2 |  | AJUSTE PARA GRUPO 2 | 94c6aa30-c192-4670-a79e-457321837e9f | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_AJG2 |  | GTD_DS_00016 | 20260113 | Status | 30 | AutoSelectWithValue | SingleBit | 51 | FALSE | FALSE | 15 | SingleCoord | 5;5 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_LTGTA_89-2_SECC |  | SECCIONADORA CARGA | 17f58d1e-c890-444e-981e-692ca75fc97d | SwitchStatus | GTD Trans | [6 empty] | GTD_LTGTA_89-2_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 2 |  | UTR_GTD_1 | GTD_LTGTA_89-2_SECC |  | GTD_DS_00113 | 20260113 | Status | 30 | AutoSelectWithValue | MultiCoord | 13;14 | FALSE | FALSE | 15 | SingleCoord | 1;1 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_LTGTA_LTGTA_P_25VT |  | 25 - TRIP DIFERENCA TENSAO | 11532f8a-460e-4a2c-9280-1d531e8f8235 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_25VT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_25VT |  | GTD_DS_00056 | 20260113 | Status |  |  | SingleBit | 92 | FALSE
GTD_TRF2_24-2_50N1 |  | 50N 1 | GTD_TRF2_24-02_50N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_50N1 |  | GTD_TRF2_24-02_50N1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2934 | FALSE
GTD_LTKGC_LTKGC_A_DR |  | DEFEITO RELE | 80f2aa5b-d81b-4318-aef4-3129326a22e6 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_DR |  | GTD_DS_00169 | 20260126 | Status |  |  | SingleBit | 325 | FALSE
GTD_AL14_52-14_GOOS |  | FALHA GOOSE | GTD_AL14_52-14_GOOS_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_GOOS |  | GTD_AL14_52-14_GOOS_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1816 | FALSE
GTD_AL24_52-24_CCCO |  | VCC CMD | GTD_AL24_52-24_CCCO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_CCCO |  | GTD_AL24_52-24_CCCO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2707 | FALSE
GTD_AL24_52-24_TOED |  | TEMPERATURA OLEO ENROLAMENTO TRIP | GTD_AL24_52-24_TOED_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_TOED |  | GTD_AL24_52-24_TOED_UTR_GTD_1 | 20251121 | Status |  |  | SingleBit | 2756 | FALSE
GTD_AL15_52-15_81U4 |  | AJUSTE PARA 81 ESTAGIO 4 | GTD_AL15_52-15_81U4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_81U4 |  | GTD_AL15_52-15_81U4_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1942 | FALSE | FALSE | 5 | SingleCoord | 1907 | ClosePulseOn | 0.25
GTD_LTGTA_LTGTA_P_GOOS |  | FALHA GOOSE | d28f17b8-07e5-4299-9eff-125014b8da94 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_GOOS |  | GTD_DS_00017 | 20260113 | Status |  |  | SingleBit | 52 | FALSE
GTD_LTKGC_52-3_MOLA |  | MOLA | ebb6e7b7-cd7f-43ab-9d55-38e577d30501 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_52-3_MOLA |  | GTD_DS_00117 | 20260126 | Status |  |  | SingleBit | 205 | FALSE
GTD_LTKGC_89-18_DSEC |  | SECCIONADORA | cd90ff56-b72d-4f28-9bf0-0d1ed96eca51 | Status | GTD Trans | [6 empty] | 89-18_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_89-18_DSEC |  | GTD_DS_00121 | 20260126 | Status |  |  | SingleBit | 226 | FALSE
GTD_TRF1_24-1_79RE |  | 79 RESET | GTD_TRF1_24-01_79RE_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_79RE |  | GTD_TRF1_24-01_79RE_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2056 | FALSE
GTD_AL12_52-12_SGF |  | SGF | GTD_AL12_52-12_SGF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_SGF |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL12_52-12_SGF |  | GTD_AL12_52-12_SGF_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 1634 | FALSE | FALSE | 15 | SingleCoord | 1602;1602 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL12_52-12_TRIP |  | TRIP EXTERNO | GTD_AL12_52-12_TRIP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_TRIP |  | GTD_AL12_52-12_TRIP_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1657 | FALSE
GTD_LTGTA_LTGTA_P_79OK |  | 79 COM SUCESSO | 6eadca29-da0c-4c22-ab56-dc45d47ebfcf | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_79OK |  | GTD_DS_00051 | 20260113 | Status |  |  | SingleBit | 87 | FALSE
GTD_AL15_52-15_81U3 |  | AJUSTE PARA 81 ESTAGIO 3 | GTD_AL15_52-15_81U3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_81U3 |  | GTD_AL15_52-15_81U3_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1941 | FALSE | FALSE | 5 | SingleCoord | 1906 | ClosePulseOn | 0.25
GTD_LTKGC_LTKGC_A_81O1 |  | 81 - TRIP SOBRE FREQUENCIA E1 | 58fcd715-d4f0-444c-9f71-7c3aa3bf3a0f | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_81O1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_81O1 |  | GTD_DS_00196 | 20260126 | Status |  |  | SingleBit | 354 | FALSE
GTD_AL24_52-24_BBFC |  | BOB FEC | GTD_AL24_52-24_BBFC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_BBFC |  | GTD_AL24_52-24_BBFC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2708 | FALSE
GTD_AL23_52-23_62BF |  | 62BF | GTD_AL23_52-23_62BF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_62BF |  | GTD_AL23_52-23_62BF_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2622 | FALSE
GTD_LTGTA_LTGTA_P_59_T |  | 59 - TRIP SOBRETENSAO | d080f9d3-a477-40c8-86d0-0d471dc98ea3 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | Unknown | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_59_T |  | GTD_DS_00045 | 20260113 | Status |  |  | SingleBit | 81 | FALSE
GTD_LTGTA_LTGTA_A_79_1 |  | 79 PARTIDA | 41406e9c-c99b-4618-9dd1-0bbf85240f2f | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_79_1 |  | GTD_DS_00096 | 20260113 | Status |  |  | SingleBit | 156 | FALSE
GTD_AL25_52-25_81E4 |  | 81 ESTAGIO 4 | GTD_AL25_52-25_81E4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_81E4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_81E4 |  | GTD_AL25_52-25_81E4_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2847 | FALSE
GTD_AL15_52-15_50N1 |  | 50N 1 | GTD_AL15_52-15_50N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_50N1 |  | GTD_AL15_52-15_50N1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1931 | FALSE
GTD_AL24_52-24_DJF1 |  | DJ | GTD_AL24_52-24_DJF1_UTR_GTD_1_SwitchStatus | SwitchStatus | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_GTD_1 | GTD_AL24_52-24_DJF1 |  | GTD_AL24_52-24_DJF1_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | MultiCoord | 2700;2701 | FALSE | FALSE | 15 | SingleCoord | 2700;2700 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_LTKGC_LTKGC_A_FA |  | FASE A | 37335acb-74da-4738-9a0d-3a86e5b89132 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_FA |  | GTD_DS_00171 | 20260126 | Status |  |  | SingleBit | 328 | FALSE
GTD_AL12_52-12_50N2 |  | 50N 2 | GTD_AL12_52-12_50N2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_50N2 |  | GTD_AL12_52-12_50N2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1632 | FALSE
GTD_AL12_52-12_81E4 |  | 81 ESTAGIO 4 | GTD_AL12_52-12_81E4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_81E4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_81E4 |  | GTD_AL12_52-12_81E4_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1647 | FALSE
GTD_BP2_BP2_43TC |  | 43TC | 4e0241a9-ddd4-4371-b8bd-7f8745dc6264 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT |  | Custom | Unknown | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_BP2_BP2_43TC |  | 43e4dbc5-3cce-4cd2-a6ac-81ca801c1684 | 20260402 | Status |  |  | SingleBit | 3300 | FALSE
GTD_AL21_52-21_51N1 |  | 51N 1 | 17d1cdc4-87fe-45df-935f-02af5454c49e | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_51N1 |  | 64465bfb-9194-42cc-a340-a143e7f59ca3 | 20230330 | Status |  |  | SingleBit | 2433 | FALSE
GTD_LTGTA_LTGTA_P_21Z3 |  | 21 - TRIP ZONA 3 | e90d9cac-e614-499e-b031-ddf986b2e63c | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_21Z3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_21Z3 |  | GTD_DS_00035 | 20260113 | Status |  |  | SingleBit | 71 | FALSE
GTD_LTGTA_LTGTA_A_21 |  | 21 - FUNCAO DISTANCIA | 532b52e4-8a76-4067-9c96-d39d9ae7876a | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_21 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_21 |  | GTD_DS_00079 | 20260113 | Status |  |  | SingleBit | 138 | FALSE
GTD_TRF1_24-1_2649 |  | 26 49 - FUNCAO TEMPERATURA | GTD_TRF1_24-01_2649_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_2649 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_TRF1_24-1_2649 |  | GTD_TRF1_24-01_2649_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2058 | FALSE | FALSE | 5 | SingleCoord | 2010;2010 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TRF1_24-1_51N1 |  | 51N 1 | GTD_TRF1_24-01_51N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_51N1 |  | GTD_TRF1_24-01_51N1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2036 | FALSE
GTD_AL15_52-15_81E3 |  | 81 ESTAGIO 3 | GTD_AL15_52-15_81E3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_81E3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_81E3 |  | GTD_AL15_52-15_81E3_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1946 | FALSE
GTD_AL25_52-25_CCMO |  | VCC MOT | GTD_AL25_52-25_CCMO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_CCMO |  | GTD_AL25_52-25_CCMO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2806 | FALSE
GTD_AL25_52-25_79_1 |  | 79 LIGA | GTD_AL25_52-25_79_1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_79_1 |  | GTD_AL25_52-25_79_1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2850 | FALSE
GTD_AL12_52-12_46 |  | 46 | GTD_AL12_52-12_46_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_46 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_46 |  | GTD_AL12_52-12_46_UTR_GTD_1 | 20251121 | Status |  |  | SingleBit | 1636 | FALSE
GTD_AL15_52-15_50EF |  | 50EF - END FAULT | 8b85df5a-88af-4996-85d1-05d042cac18f | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_50EF |  | f35098b1-1d70-4a70-908f-a8a58de475cf | 20260327 | Status |  |  | SingleBit | 3238 | FALSE
GTD_AL15_52-15_81E2 |  | 81 ESTAGIO 2 | GTD_AL15_52-15_81E2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_81E2 |  | GTD_AL15_52-15_81E2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1945 | FALSE
GTD_AL12_52-12_50N1 |  | 50N 1 | GTD_AL12_52-12_50N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_50N1 |  | GTD_AL12_52-12_50N1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1631 | FALSE
GTD_AL25_52-25_DR |  | RELE | GTD_AL25_52-25_DR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_DR |  | GTD_AL25_52-25_DR_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2820 | FALSE
GTD_TRF1_24-1_79LO |  | 79 BLOQUEADO | GTD_TRF1_24-01_79LO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_79LO |  | GTD_TRF1_24-01_79LO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2055 | FALSE
GTD_AL21_52-21_79_1 |  | 79 LIGA | 5a7fdc24-4f7e-4122-b7a9-fdc94a28fda3 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_79_1 |  | 347f8d7f-7e52-4c67-bd23-ef15a5340780 | 20230330 | Status |  |  | SingleBit | 2450 | FALSE
GTD_LTGTA_LTGTA_A_21Z1 |  | 21 - TRIP ZONA 1 | b16e94e8-9ad7-4c20-9bde-2756f4869505 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_21Z1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_21Z1 |  | GTD_DS_00080 | 20260113 | Status |  |  | SingleBit | 139 | FALSE
GTD_LTKGC_LTKGC_P_81E1 |  | 81 - TRIP SUB FREQUENCIA E1 | 888c7ac0-b769-417a-a2e0-d5e1c80f6dee | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_81E1 |  | GTD_DS_00158 | 20260126 | Status |  |  | SingleBit | 282 | FALSE
GTD_LTKGC_LTKGC_A_FSIN |  | FALHA SINCRONISMO IRIG B | 4b041d73-d23d-4d71-8205-5e75c6d4cc75 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_FSIN |  | GTD_DS_00170 | 20260126 | Status |  |  | SingleBit | 324 | FALSE
GTD_AL24_52-24_79_1 |  | 79 LIGA | GTD_AL24_52-24_79_1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_79_1 |  | GTD_AL24_52-24_79_1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2750 | FALSE
GTD_AL12_52-12_2649 |  | 26 49 - FUNCAO TEMPERATURA | GTD_AL12_52-12_2649_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_2649 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL12_52-12_2649 |  | GTD_AL12_52-12_2649_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1655 | FALSE | FALSE | 5 | SingleCoord | 1610;1610 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_AL25_52-25_CCCO |  | VCC CMD | GTD_AL25_52-25_CCCO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_CCCO |  | GTD_AL25_52-25_CCCO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2807 | FALSE
GTD_AL25_52-25_50F1 |  | 50F 1 | GTD_AL25_52-25_50F1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_50F1 |  | GTD_AL25_52-25_50F1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2827 | FALSE
GTD_AL21_52-21_CCCO |  | VCC CMD | fb2cb3f5-b50b-473b-8636-7874362efd9b | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_CCCO |  | d39d70ca-7a57-4596-9f65-a43d2842c03e | 20230330 | Status |  |  | SingleBit | 2407 | FALSE
GTD_LTGTA_LTGTA_A_81E2 |  | 81 - TRIP SUB FREQUENCIA E2 | 5ed45596-8f24-42cb-a271-b3121e1f7d20 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_81E2 |  | GTD_DS_00094 | 20260113 | Status |  |  | SingleBit | 153 | FALSE
GTD_AL13_52-13_62BF |  | 62BF | GTD_AL13_52-13_62BF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_62BF |  | GTD_AL13_52-13_62BF_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1722 | FALSE
GTD_LTKGC_LTKGC_A_FC |  | FASE C | be0d7b1b-76b5-4823-95f0-7f8f01f70b96 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_FC |  | GTD_DS_00174 | 20260126 | Status |  |  | SingleBit | 330 | FALSE
GTD_TRF2_24-2_79 |  | 79 | GTD_TRF2_24-02_79_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_TRF2_24-2_79 |  | GTD_TRF2_24-02_79_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2952 | FALSE | FALSE | 15 | SingleCoord | 2909;2909 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_LTGTA_LTGTA_A_59_T |  | 59 - TRIP SOBRETENSAO | 2a23a656-6f79-4df7-8df9-ecc88712cdf4 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | Unknown | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_59_T |  | GTD_DS_00092 | 20260113 | Status |  |  | SingleBit | 151 | FALSE
GTD_TRF1_24-1_MOLA |  | MOLA | GTD_TRF1_24-01_MOLA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_MOLA |  | GTD_TRF1_24-01_MOLA_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2003 | FALSE
GTD_BP1_BP1_87_87 |  | 87 | 5c0b5c2f-b050-41c8-beb1-c8dd0e54fd5b | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_PROT_87 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_BP1_BP1_87_87 |  | 52b44ff7-5859-4e39-9f3b-a5cb77a17888 | 20260402 | Status | 30 | DirectOperate | SingleBit | 3204 | FALSE | FALSE | 5 | SingleCoord | 3200;3200 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_LTKGC_LTKGC_A_FVLT |  | FALTA POTENCIAL LT | b5c923a8-8a44-45fb-8ab7-0f681ac23ed7 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_FVLT |  | GTD_DS_00209 | 20260126 | Status |  |  | SingleBit | 366 | FALSE
GTD_LTGTA_LTGTA_A_51F |  | 51 FASE | a9a43e35-c102-4e4c-a337-3517056820eb | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_51F |  | GTD_DS_00075 | 20260113 | Status |  |  | SingleBit | 134 | FALSE
GTD_LTGTA_LTGTA_P_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | 088d22ff-9926-41fd-ba52-144e734c9088 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_67NT |  | GTD_DS_00043 | 20260113 | Status |  |  | SingleBit | 79 | FALSE
GTD_LTGTA_LTGTA_P_FSIN |  | FALHA SINCRONISMO IRIG B | e2fa9f06-8f64-4f64-81e4-122d35fa7b3b | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_FSIN |  | GTD_DS_00018 | 20260113 | Status |  |  | SingleBit | 54 | FALSE
GTD_TRF2_24-2_43TC |  | 43TC | GTD_TRF2_24-02_43TC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_43TC |  | GTD_TRF2_24-02_43TC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2915 | FALSE
GTD_LTKGC_LTKGC_P_21 |  | 21 - FUNCAO DISTANCIA | 4d62c967-bacb-41c4-aeae-a998801784a2 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_21 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_21 |  | GTD_DS_00135 | 20260126 | Status |  |  | SingleBit | 268 | FALSE
GTD_AL15_52-15_81 |  | 81 | GTD_AL15_52-15_81_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL15_52-15_81 |  | GTD_AL15_52-15_81_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 1937 | FALSE | FALSE | 15 | SingleCoord | 1903;1903 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL25_52-25_TOED |  | TEMPERATURA OLEO ENROLAMENTO TRIP | GTD_AL25_52-25_TOED_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_TOED |  | GTD_AL25_52-25_TOED_UTR_GTD_1 | 20251121 | Status |  |  | SingleBit | 2856 | FALSE
GTD_LTGTA_LTGTA_A_FUTP |  | FALHA FUSIVEL TP | 80a098e9-5b17-40a9-b5f4-1e6b7a8d402d | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_FUTP |  | GTD_DS_00104 | 20260113 | Status |  |  | SingleBit | 165 | FALSE
GTD_AL15_52-15_FSIN |  | FALHA SINCRONISMO IRIG-B | GTD_AL15_52-15_FSIN_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_FSIN |  | GTD_AL15_52-15_FSIN_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1918 | FALSE
GTD_LTGTA_LTGTA_P_FUTP |  | FALHA FUSIVEL TP | 4609ea6b-881c-4a79-9705-63681636951d | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_FUTP |  | GTD_DS_00059 | 20260113 | Status |  |  | SingleBit | 95 | FALSE
GTD_LTGTA_LTGTA_OI |  | OPERACAO INDEVIDA SEC | 96c3dcb6-1631-4e52-b4d7-d38da1f5bdc1 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_OI |  | GTD_DS_00014 | 20260113 | Status |  |  | SingleBit | 37 | FALSE
GTD_AL23_52-23_81U5 |  | AJUSTE PARA 81 ESTAGIO 5 | GTD_AL23_52-23_81U5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_81U5 |  | GTD_AL23_52-23_81U5_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2643 | FALSE | FALSE | 5 | SingleCoord | 2608 | ClosePulseOn | 0.25
GTD_TRF1_24-1_FSIN |  | FALHA SINCRONISMO IRIG-B | GTD_TRF1_24-01_FSIN_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_FSIN |  | GTD_TRF1_24-01_FSIN_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2018 | FALSE
GTD_AL24_52-24_BBA2 |  | BOB AB 2 | GTD_AL24_52-24_BBA2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_BBA2 |  | GTD_AL24_52-24_BBA2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2710 | FALSE
GTD_AL24_52-24_BBA1 |  | BOB AB 1 | GTD_AL24_52-24_BBA1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_BBA1 |  | GTD_AL24_52-24_BBA1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2709 | FALSE
GTD_AL15_52-15_51N |  | 51N | GTD_AL15_52-15_51N_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL15_52-15_51N |  | GTD_AL15_52-15_51N_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 1930 | FALSE | FALSE | 15 | SingleCoord | 1901;1901 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL14_52-14_FCOM |  | COMUNIC | GTD_AL14_52-14_FCOM_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_FCOM |  | GTD_AL14_52-14_FCOM_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1821 | FALSE
GTD_AL23_52-23_79LO |  | 79 BLOQUEADO | GTD_AL23_52-23_79LO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_79LO |  | GTD_AL23_52-23_79LO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2652 | FALSE
GTD_AL14_52-14_81U4 |  | AJUSTE PARA 81 ESTAGIO 4 | GTD_AL14_52-14_81U4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_81U4 |  | GTD_AL14_52-14_81U4_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1842 | FALSE | FALSE | 5 | SingleCoord | 1807 | ClosePulseOn | 0.25
GTD_LTGTA_52-1_43LR |  | 43LR | 9d29cc15-ab49-4aa8-9483-afbbc78e2d30 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom___INV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_LTGTA_52-1_43LR |  | GTD_DS_00004 | 20260113 | Status |  |  | SingleBit | 6 | FALSE
GTD_TRF1_24-1_81E4 |  | 81 ESTAGIO 4 | GTD_TRF1_24-01_81E4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_81E4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-01_81E4 |  | GTD_TRF1_24-01_81E4_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2050 | FALSE
GTD_AL24_52-24_79 |  | 79 | GTD_AL24_52-24_79_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL24_52-24_79 |  | GTD_AL24_52-24_79_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2749 | FALSE | FALSE | 15 | SingleCoord | 2709;2709 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TRF1_24-1_50N1 |  | 50N 1 | GTD_TRF1_24-01_50N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_50N1 |  | GTD_TRF1_24-01_50N1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2034 | FALSE
GTD_LTKGC_LTKGC_P_FB |  | FASE B | c722f228-6dd5-4767-9214-ab6ba12c6f98 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_FB |  | GTD_DS_00122 | 20260126 | Status |  |  | SingleBit | 259 | FALSE
GTD_AL23_52-23_79 |  | 79 | GTD_AL23_52-23_79_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL23_52-23_79 |  | GTD_AL23_52-23_79_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2649 | FALSE | FALSE | 15 | SingleCoord | 2609;2609 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_LTGTA_LTGTA_P_27_T |  | 27 - TRIP SUBTENSAO | e701c2db-0bc8-4c32-9ab4-e49ccc7193ca | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_27_T |  | GTD_DS_00044 | 20260113 | Status |  |  | SingleBit | 80 | FALSE
GTD_TRF2_24-2_FCOM |  | COMUNIC | GTD_TRF2_24-02_FCOM_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_FCOM |  | GTD_TRF2_24-02_FCOM_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2924 | FALSE
GTD_AL15_52-15_FA |  | FASE A | GTD_AL15_52-15_FA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_FA |  | GTD_AL15_52-15_FA_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1923 | FALSE
GTD_AL25_52-25_GOOS |  | FALHA GOOSE | GTD_AL25_52-25_GOOS_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_GOOS |  | GTD_AL25_52-25_GOOS_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2816 | FALSE
GTD_AL12_52-12_GOOS |  | FALHA GOOSE | GTD_AL12_52-12_GOOS_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_GOOS |  | GTD_AL12_52-12_GOOS_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1616 | FALSE
GTD_LTGTA_LTGTA_A_21Z3 |  | 21 - TRIP ZONA 3 | 446eecca-491c-410e-96a4-cfa9f936a41c | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_21Z3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_21Z3 |  | GTD_DS_00082 | 20260113 | Status |  |  | SingleBit | 141 | FALSE
GTD_TR2_TR2_50CD |  | 50 - SOBRECORRENTE CDC | 1be50a34-2028-4372-bd2a-c8e1e74e54d0 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_50CD |  | f72e43b4-91b3-4ee8-9931-bf8ca6fb6228 | 20260407 | Status |  |  | SingleBit | 1169 | FALSE
GTD_LTKGC_LTKGC_A_GOOS |  | FALHA GOOSE | 7a425303-9ffd-4f55-8c25-272c8caf21d5 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_GOOS |  | GTD_DS_00168 | 20260126 | Status |  |  | SingleBit | 322 | FALSE
GTD_TRF1_24-1_51F |  | 51F | GTD_TRF1_24-01_51F_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_51F |  | GTD_TRF1_24-01_51F_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2032 | FALSE
GTD_AL21_52-21_79OK |  | 79 OK | a5bbb476-3908-412d-a313-28f43b373438 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_79OK |  | c6242586-4992-410d-a9be-dbe9e4cb6422 | 20230330 | Status |  |  | SingleBit | 2451 | FALSE
GTD_AL23_52-23_81 |  | 81 | GTD_AL23_52-23_81_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL23_52-23_81 |  | GTD_AL23_52-23_81_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2637 | FALSE | FALSE | 15 | SingleCoord | 2603;2603 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL15_52-15_79_1 |  | 79 LIGA | GTD_AL15_52-15_79_1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_79_1 |  | GTD_AL15_52-15_79_1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1950 | FALSE
GTD_AL25_52-25_TRIP |  | TRIP EXTERNO | GTD_AL25_52-25_TRIP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_TRIP |  | GTD_AL25_52-25_TRIP_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2857 | FALSE
GTD_AL12_52-12_TOED |  | TEMPERATURA OLEO ENROLAMENTO TRIP | GTD_AL12_52-12_TOED_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_TOED |  | GTD_AL12_52-12_TOED_UTR_GTD_1 | 20251121 | Status |  |  | SingleBit | 1656 | FALSE
GTD_LTGTA_LTGTA_A_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | 6df1fae4-11e2-4859-8c87-bffedf145e45 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_67NT |  | GTD_DS_00090 | 20260113 | Status |  |  | SingleBit | 149 | FALSE
GTD_LTKGC_LTKGC_P_25ER |  | 25 FALHA SINCRONISMO | 092036c2-7291-4a4e-9030-68caf14a25c9 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_25ER |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_25ER |  | GTD_DS_00154 | 20260126 | Status |  |  | SingleBit | 291 | FALSE
GTD_LTKGC_LTKGC_P_TEXT |  | TRIP EXTERNO | 3a35893d-1bc5-4ba4-b35c-bb8042233317 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_TEXT |  | GTD_DS_00164 | 20260126 | Status |  |  | SingleBit | 298 | FALSE
GTD_AL12_52-12_79OK |  | 79 OK | GTD_AL12_52-12_79OK_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_79OK |  | GTD_AL12_52-12_79OK_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1651 | FALSE
GTD_AL25_52-25_81U5 |  | AJUSTE PARA 81 ESTAGIO 5 | GTD_AL25_52-25_81U5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_81U5 |  | GTD_AL25_52-25_81U5_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2843 | FALSE | FALSE | 5 | SingleCoord | 2808 | ClosePulseOn | 0.25
GTD_AL24_52-24_2649 |  | 26 49 - FUNCAO TEMPERATURA | GTD_AL24_52-24_2649_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_2649 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL24_52-24_2649 |  | GTD_AL24_52-24_2649_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2755 | FALSE | FALSE | 5 | SingleCoord | 2710;2710 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_AL21_52-21_TRIP |  | TRIP EXTERNO | c02259a5-f63f-4a19-bb6c-3ca149c51cf2 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_TRIP |  | d2463ff8-28d3-4f0a-85b1-f5cc99866155 | 20230330 | Status |  |  | SingleBit | 2457 | FALSE
GTD_LTGTA_LTGTA_P_79RE |  | 79 RESET | cf6b7585-057b-4928-b145-c0fd20be970b | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_79RE |  | GTD_DS_00053 | 20260113 | Status |  |  | SingleBit | 89 | FALSE
GTD_AL15_52-15_50F2 |  | 50F 2 | GTD_AL15_52-15_50F2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_50F2 |  | GTD_AL15_52-15_50F2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1928 | FALSE
GTD_TRF2_24-2_81 |  | 81 | GTD_TRF2_24-02_81_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_TRF2_24-2_81 |  | GTD_TRF2_24-02_81_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2940 | FALSE | FALSE | 15 | SingleCoord | 2903;2903 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_LTGTA_LTGTA_A_27_T |  | 27 - TRIP SUBTENSAO | 0cbcb535-9c3d-44d1-8d50-cef850160908 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | Unknown | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_27_T |  | GTD_DS_00091 | 20260113 | Status |  |  | SingleBit | 150 | FALSE
GTD_AL24_52-24_DR |  | RELE | GTD_AL24_52-24_DR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_DR |  | GTD_AL24_52-24_DR_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2720 | FALSE
GTD_AL24_52-24_46 |  | 46 | GTD_AL24_52-24_46_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_46 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_46 |  | GTD_AL24_52-24_46_UTR_GTD_1 | 20251121 | Status |  |  | SingleBit | 2736 | FALSE
GTD_LTKGC_LTKGC_A_67N2 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E2 | 7d0c02cc-3c0d-49dc-b2db-9fbe9645f692 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_67N2 |  | GTD_DS_00190 | 20260126 | Status |  |  | SingleBit | 348 | FALSE
GTD_TRF1_24-1_79 |  | 79 | GTD_TRF1_24-01_79_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_TRF1_24-1_79 |  | GTD_TRF1_24-01_79_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2052 | FALSE | FALSE | 15 | SingleCoord | 2009;2009 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL25_52-25_79LO |  | 79 BLOQUEADO | GTD_AL25_52-25_79LO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_79LO |  | GTD_AL25_52-25_79LO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2852 | FALSE
GTD_LTGTA_LTGTA_P_81O1 |  | 81 - TRIP SOBRE FREQUENCIA E1 | b187dd35-685f-4082-9443-d665a5318d35 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_81O1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_81O1 |  | GTD_DS_00048 | 20260113 | Status |  |  | SingleBit | 84 | FALSE
GTD_LTGTA_LTGTA_P_N |  | NEUTRO | b43a6727-b04b-423d-94c5-88ecf4e03028 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_N |  | GTD_DS_00025 | 20260113 | Status |  |  | SingleBit | 61 | FALSE
GTD_LTKGC_LTKGC_A_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | b1bf67af-c39c-407a-bbd4-8c668bab10f9 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_67NT |  | GTD_DS_00218 | 20260126 | Status |  |  | SingleBit | 349 | FALSE
GTD_LTGTA_LTGTA_P_81E1 |  | 81 - TRIP SUB FREQUENCIA E1 | 6ea7870c-e43e-48b1-a74a-0eb5e8f97f6b | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_81E1 |  | GTD_DS_00046 | 20260113 | Status |  |  | SingleBit | 82 | FALSE
GTD_IB_52-18_FA |  | FASE A | 8f79889a-78df-4a64-849e-01e0c6adf3aa | Status | GTD Trans | [6 empty] | GTD_IB_52-160_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_FA |  | 592f66d5-2d29-4dda-a92e-b068f87effdd |  | Status |  |  | SingleBit | 2323 | FALSE
GTD_AL25_52-25_50N1 |  | 50N 1 | GTD_AL25_52-25_50N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_50N1 |  | GTD_AL25_52-25_50N1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2831 | FALSE
GTD_LTGTA_LTGTA_P_25AT |  | 25 - TRIP DIFERENCA DE ANGULO | 6a55b3ef-551b-43ca-af96-83b313bc0f3b | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_25AT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_25AT |  | GTD_DS_00058 | 20260113 | Status |  |  | SingleBit | 94 | FALSE
GTD_LTKGC_LTKGC_A_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | 7553e630-212e-41bd-9c17-f4f2e0d75317 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_67FT |  | GTD_DS_00187 | 20260126 | Status |  |  | SingleBit | 346 | FALSE
GTD_AL23_52-23_SGF |  | SGF | GTD_AL23_52-23_SGF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_SGF |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL23_52-23_SGF |  | GTD_AL23_52-23_SGF_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2634 | FALSE | FALSE | 15 | SingleCoord | 2602;2602 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_LTKGC_29-3_SECG |  | LAMINA DE TERRA | 28f52326-e1da-44b3-a3f2-e15d19c54de4 | SwitchStatus | GTD Trans | [6 empty] | 29-03_GTD |  | SwitchStatus | ABC | None | Read |  | null@null___ABERTO@FECHADO___SwitchStatus_D_TS_SO_terra | 1 |  | UTR_GTD_1 | GTD_LTKGC_29-3_SECG |  | GTD_DS_00211 | 20260126 | Status |  |  | MultiCoord | 228;229 | FALSE
GTD_TR2_TR2_RTD3_DPT1 |  | DEFEITO PT100 | 80651507-39d7-4e87-858b-9f3dfcce6752 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_RTD3_DPT1 |  | 8ee53bda-4da5-4b97-b402-3b8e2cc7e526 | 20260407 | Status |  |  | SingleBit | 1168 | FALSE
GTD_LTGTA_89-4_DSEC |  | SECCIONADORA | 8feee2c5-2a7d-4690-9cac-616d83bb500a | Status | GTD Trans | [6 empty] | GTD_LTGTA_89-4_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_89-4_DSEC |  | GTD_DS_00009 | 20260113 | Status |  |  | SingleBit | 21 | FALSE
GTD_LTGTA_LTGTA_P_67F1 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E1 | 8a044408-9f05-4632-bc5f-d0d9a7beee6f | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_67F1 |  | GTD_DS_00038 | 20260113 | Status |  |  | SingleBit | 74 | FALSE
GTD_TRF2_24-2_51N1 |  | 51N 1 | GTD_TRF2_24-02_51N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_51N1 |  | GTD_TRF2_24-02_51N1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2936 | FALSE
GTD_AL25_52-25_SGF |  | SGF | GTD_AL25_52-25_SGF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_SGF |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL25_52-25_SGF |  | GTD_AL25_52-25_SGF_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2834 | FALSE | FALSE | 15 | SingleCoord | 2802;2802 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL24_52-24_50F2 |  | 50F 2 | GTD_AL24_52-24_50F2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_50F2 |  | GTD_AL24_52-24_50F2_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2728 | FALSE
GTD_AL24_52-24_81E5 |  | 81 ESTAGIO 5 | GTD_AL24_52-24_81E5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_81E5 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_81E5 |  | GTD_AL24_52-24_81E5_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2748 | FALSE
GTD_AL15_52-15_2649 |  | 26 49 - FUNCAO TEMPERATURA | GTD_AL15_52-15_2649_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_2649 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL15_52-15_2649 |  | GTD_AL15_52-15_2649_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 1955 | FALSE | FALSE | 5 | SingleCoord | 1910;1910 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TRF2_24-2_DR |  | RELE | GTD_TRF2_24-02_DR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_DR |  | GTD_TRF2_24-02_DR_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2923 | FALSE
GTD_AL12_52-12_79RE |  | 79 RESET | GTD_AL12_52-12_79RE_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_79RE |  | GTD_AL12_52-12_79RE_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 1653 | FALSE
GTD_AL23_52-23_FCOM |  | COMUNIC | GTD_AL23_52-23_FCOM_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_FCOM |  | GTD_AL23_52-23_FCOM_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2621 | FALSE
GTD_LTGTA_LTGTA_A_FSIN |  | FALHA SINCRONISMO IRIG B | f4ddc8a8-daf7-4a90-a83c-a9569e581c05 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_FSIN |  | GTD_DS_00065 | 20260113 | Status |  |  | SingleBit | 124 | FALSE
GTD_TRF1_24-1_81E1 |  | 81 ESTAGIO 1 | GTD_TRF1_24-01_81E1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-01_81E1 |  | GTD_TRF1_24-01_81E1_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2047 | FALSE
GTD_AL25_52-25_DJF1 |  | DJ | GTD_AL25_52-25_DJF1_UTR_GTD_1_SwitchStatus | SwitchStatus | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_GTD_1 | GTD_AL25_52-25_DJF1 |  | GTD_AL25_52-25_DJF1_UTR_GTD_1 | 20230330 | Status | 30 | DirectOperate | MultiCoord | 2800;2801 | FALSE | FALSE | 15 | SingleCoord | 2800;2800 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_LTKGC_LTKGC_P_25VT |  | 25 - TRIP DIFERENCA TENSAO | ad5977da-c478-418b-9695-74b6679898d8 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_25VT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_25VT |  | GTD_DS_00156 | 20260126 | Status |  |  | SingleBit | 292 | FALSE
GTD_BC2_52-17_50EF |  | 50EF - END FAULT | c41081b8-f6d6-4100-9544-a693d49578bd | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_50EF |  | 6894c359-34f3-4a6c-a0c0-5779dd1f0f41 | 20260327 | Status |  |  | SingleBit | 3241 | FALSE
GTD_LTKGC_LTKGC_A_25ER |  | 25 FALHA SINCRONISMO | 07a06f50-08e8-4858-8fa1-3e1b6a63ae6c | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_25ER |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_25ER |  | GTD_DS_00203 | 20260126 | Status |  |  | SingleBit | 361 | FALSE
GTD_AL25_52-25_50EF |  | 50EF - END FAULT | f2fef0dd-38c7-4fe1-87ae-3e36e3dad8c4 | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_50EF |  | 7356c205-01a8-4141-bb64-2e4192e2d412 | 20260327 | Status |  |  | SingleBit | 3338 | FALSE
GTD_AL21_52-21_FB |  | FASE B | c3db3e79-545c-4f13-9acd-529a2c11aa36 | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_FB |  | ee252bf1-e8eb-4ab8-9186-9dd586941e51 | 20230330 | Status |  |  | SingleBit | 2424 | FALSE
GTD_AL15_52-15_46 |  | 46 | GTD_AL15_52-15_46_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_46 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_46 |  | GTD_AL15_52-15_46_UTR_GTD_1 | 20251121 | Status |  |  | SingleBit | 1936 | FALSE
GTD_LTGTA_LTGTA_P_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | c774e614-7c29-47e5-9b85-3ddc40540f2f | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_67FT |  | GTD_DS_00040 | 20260113 | Status |  |  | SingleBit | 76 | FALSE
GTD_TR2_TR2_59CD |  | 59 - BLOQUEIO CDC SOBRETENSAO | d22e10c4-44b5-45dd-aa5e-a62186b5b330 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_59CD |  | abf5749f-9053-4737-8457-b1183cc76631 | 20260407 | Status |  |  | SingleBit | 1170 | FALSE
GTD_TRF2_24-2_CCMO |  | VCC MOT | GTD_TRF2_24-02_CCMO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_CCMO |  | GTD_TRF2_24-02_CCMO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2906 | FALSE
GTD_TR1_TR1_59CD |  | 59 - BLOQUEIO CDC SOBRETENSAO | 5bf884d7-8b06-4d11-bf26-c3899d29bcd5 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_59CD |  | 5f6b6f80-6e9c-45a8-b46c-62c57e51326e | 20260407 | Status |  |  | SingleBit | 854 | FALSE
GTD_LTKGC_LTKGC_P_21Z4 |  | 21 - TRIP ZONA 4 | 8cc04d96-b78d-4b65-b46f-011576a60300 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_21Z4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_21Z4 |  | GTD_DS_00140 | 20260126 | Status |  |  | SingleBit | 272 | FALSE
GTD_TRF1_24-1_CCMO |  | VCC MOT | GTD_TRF1_24-01_CCMO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_CCMO |  | GTD_TRF1_24-01_CCMO_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2006 | FALSE
GTD_AL25_52-25_81U4 |  | AJUSTE PARA 81 ESTAGIO 4 | GTD_AL25_52-25_81U4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_81U4 |  | GTD_AL25_52-25_81U4_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2842 | FALSE | FALSE | 5 | SingleCoord | 2807 | ClosePulseOn | 0.25
GTD_LTGTA_LTGTA_P_50N1 |  | 50 NEUTRO ESTAGIO 1 | e010b49e-ac67-4f3d-a407-534f01e13f85 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_50N1 |  | GTD_DS_00029 | 20260113 | Status |  |  | SingleBit | 65 | FALSE
GTD_LTKGC_LTKGC_A_50F1 |  | 50 FASE ESTAGIO 1 | 94be95c3-ddc2-41a2-99f9-a8d4461f8fe3 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_50F1 |  | GTD_DS_00216 | 20260126 | Status |  |  | SingleBit | 332 | FALSE
GTD_TR1_TR1_FCTM |  | FALHA COMUNICACAO RELE MONITORAMENTO DE TEMPERATURA | 3ff4af1a-624d-4c9c-9f82-a0de62222214 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_FCTM |  | 77177498-87b6-42c4-aef3-928e97dc9aef | 20260407 | Status |  |  | SingleBit | 857 | FALSE
GTD_AL21_52-21_MOLA |  | MOLA | 7d71f8ca-4396-4d11-a440-6aef669c06fa | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_MOLA |  | 89a67ec0-a8b1-47b0-b671-943e80eae427 | 20230330 | Status |  |  | SingleBit | 2403 | FALSE
GTD_LTGTA_LTGTA_A_21Z4 |  | 21 - TRIP ZONA 4 | 8cdd1101-6992-4bd2-8845-68bb717d2576 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_21Z4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_21Z4 |  | GTD_DS_00083 | 20260113 | Status |  |  | SingleBit | 142 | FALSE
GTD_AL21_52-21_FA |  | FASE A | 5c26b70a-7b8b-46c7-8e59-c7e78f4e4ed5 | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_FA |  | 8d776abc-9555-4d06-9171-94341f5c906e | 20230330 | Status |  |  | SingleBit | 2423 | FALSE
GTD_LTGTA_LTGTA_A_21Z2 |  | 21 - TRIP ZONA 2 | 35ca13fe-7031-4f24-ba11-f3f0c8e3649c | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_21Z2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_A_21Z2 |  | GTD_DS_00081 | 20260113 | Status |  |  | SingleBit | 140 | FALSE
GTD_AL23_52-23_81U3 |  | AJUSTE PARA 81 ESTAGIO 3 | GTD_AL23_52-23_81U3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_81U3 |  | GTD_AL23_52-23_81U3_UTR_GTD_1 |  | Status | 30 | DirectOperate | SingleBit | 2641 | FALSE | FALSE | 5 | SingleCoord | 2606 | ClosePulseOn | 0.25
GTD_LTGTA_LTGTA_P_79_1 |  | 79 PARTIDA | c31ff2b9-85c7-41fb-8200-9e7dc7f3dd5f | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_79_1 |  | GTD_DS_00050 | 20260113 | Status |  |  | SingleBit | 86 | FALSE
GTD_BP1_BP1_FSIN |  | FALHA SINCRONISMO IRIG B | fdb7cddd-0191-4682-b19b-031ac2c649f1 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BP1_BP1_FSIN |  | d80fdca2-ecce-4eb1-bd0d-f2a6b3e94949 | 20260327 | Status |  |  | SingleBit | 3203 | FALSE
GTD_LTGTA_LTGTA_P_TEXT |  | TRIP EXTERNO | 693cbd7f-6370-48eb-afff-9192d84b81f7 | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_P_TEXT |  | GTD_DS_00062 | 20260113 | Status |  |  | SingleBit | 98 | FALSE
GTD_TRF2_24-2_BBFC |  | BOB FEC | GTD_TRF2_24-02_BBFC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_BBFC |  | GTD_TRF2_24-02_BBFC_UTR_GTD_1 | 20230330 | Status |  |  | SingleBit | 2908 | FALSE
GTD_LTKGC_LTKGC_P_50N1 |  | 50 NEUTRO ESTAGIO 1 | 9d0f64ca-ba8a-429a-8b92-14c988abb887 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_50N1 |  | GTD_DS_00136 | 20260126 | Status |  |  | SingleBit | 265 | FALSE
GTD_TR1BT_52-10_MOLA |  | MOLA | b0ecaf2e-5860-47fb-a037-53c7dbbc519c | Status | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1BT_52-10_MOLA |  | GTD_DS_00243 | 20260204 | Status |  |  | SingleBit | 631 | FALSE
GTD_LTKGC_LTKGC_P_50N2 |  | 50 NEUTRO ESTAGIO 2 | a0fc8625-2e50-4cf8-8334-e4bf009df546 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_50N2 |  | GTD_DS_00134 | 20260126 | Status |  |  | SingleBit | 266 | FALSE
GTD_LTKGC_89-16_SECF |  | SECCIONADORA FONTE | c2a1d929-0877-464b-80b9-cf303b7c974e | SwitchStatus | GTD Trans | [6 empty] | 89-16_GTD |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 2 |  | UTR_GTD_1 | GTD_LTKGC_89-16_SECF |  | GTD_DS_00227 | 20260126 | Status | 30 | AutoSelectWithValue | MultiCoord | 218;219 | FALSE | FALSE | 15 | SingleCoord | 202;202 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TR1_TR1_CAFL |  | FALTA VCA | f3930f68-a772-4054-9730-f85a4d26da62 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_CAFL |  | GTD_DS_00277 | 20260204 | Status |  |  | SingleBit | 684 | FALSE
GTD_TR1AT_TR1AT_P_67 |  | 67 - FUNCAO DIRECIONAL SOBRECORRENTE | 450f5581-66c5-4062-8967-58bd3461bbdf | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_P_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_P_67 |  | GTD_DS_00297 | 20260204 | Status |  |  | SingleBit | 710 | FALSE
GTD_TR1_TR1_P_N |  | NEUTRO | 8663a796-4b61-4921-b02d-a2f0e6fd6d17 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT_N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_P_N |  | GTD_DS_00289 | 20260204 | Status |  |  | SingleBit | 702 | FALSE
GTD_TR1AT_TR1AT_TED |  | 49 - TRIP TEMPERATURA ENROLAMENTO | 2e49dd71-3440-4c09-8d48-23bf67e2fcbf | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_TED |  | GTD_DS_00274 | 20260204 | Status |  |  | SingleBit | 681 | FALSE
GTD_LTKGC_LTKGC_A_50N1 |  | 50 NEUTRO ESTAGIO 1 | 2b51cdc7-52fb-46cb-a104-737e95afc21c | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_50N1 |  | GTD_DS_00185 | 20260126 | Status |  |  | SingleBit | 335 | FALSE
GTD_AL21_52-21_DJF1 |  | DJ | fc00bdc0-cfd1-4f63-8490-981b2110e434 | SwitchStatus | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_GTD_1 | GTD_AL11_52-21_DJF1 |  | 297a469f-a7e6-45ed-a925-cff257bdba5e | 20230330 | Status | 30 | DirectOperate | MultiCoord | 2400;2401 | FALSE | FALSE | 15 | SingleCoord | 2400;2400 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TR1_TR1_71TH |  | 71 - NIVEL ALTO OLEO TRAFO | ba256ef8-19a1-43c1-8024-20d9e4102841 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_71TH |  | GTD_DS_00261 | 20260204 | Status |  |  | SingleBit | 668 | FALSE
GTD_TR1AT_P_52-2_62BF |  | 62BF | 4d8754fd-7030-442c-b422-9fae0a9b592a | Status | GTD Trans | [6 empty] | GTD_TR1AT_P_52-2_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_P_52-2_62BF |  | GTD_DS_00290 | 20260204 | Status |  |  | SingleBit | 703 | FALSE
GTD_TR1_TR1_71CH |  | 71 - NIVEL ALTO OLEO CDC | 1b2d9b79-411e-49b3-baea-af89f8dd51fd | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_71CH |  | GTD_DS_00265 | 20260204 | Status |  |  | SingleBit | 672 | FALSE
GTD_TR1BT_TR1BT_TEA |  | 49 - ALARME TEMPERATURA ENROLAMENTO | 659e6795-042c-43fa-aa90-b6aeb4083e8a | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_TEA |  | GTD_DS_00272 | 20260204 | Status |  |  | SingleBit | 678 | FALSE
GTD_LTKGC_52-3_BBA2 |  | BOBINA ABERTURA 2 | 0b51bf20-178a-4773-9343-b1e920dd00a0 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_52-3_BBA2 |  | GTD_DS_00123 | 20260126 | Status |  |  | SingleBit | 209 | FALSE
GTD_TR1_TR1_63TD |  | 63T DESL | 07039c97-ba24-4ec7-afe5-6420daf3413e | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_63TD |  | GTD_DS_00260 | 20260204 | Status |  |  | SingleBit | 667 | FALSE
GTD_TR1AT_52-2_SF6A |  | BAIXA PRESSAO SF6 ALARME | 6e968af1-3dde-4af8-b8a5-ac83c316e8ce | Status | GTD Trans | [6 empty] | GTD_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1AT_52-2_SF6A |  | GTD_DS_00233 | 20260204 | Status |  |  | SingleBit | 603 | FALSE
GTD_TR1_TR1_P_DR |  | DEFEITO RELE | 3f58e5d4-5167-4713-8a7c-da5de3db473d | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_P_DR |  | GTD_DS_00256 | 20260204 | Status |  |  | SingleBit | 663 | FALSE
GTD_TR1AT_52-2_MOLA |  | MOLA | df566862-7673-4196-b231-bd554a8c795a | Status | GTD Trans | [6 empty] | GTD_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1AT_52-2_MOLA |  | GTD_DS_00235 | 20260204 | Status |  |  | SingleBit | 605 | FALSE
GTD_TR1AT_89-8_DSEC |  | DEFEITO SECCIONADORA | 66c29216-b7f2-4dbb-b4ed-69846be75f6f | Status | GTD Trans | [6 empty] | GTD_TR1AT_89-8_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1AT_89-8_DSEC |  | GTD_DS_00240 | 20260204 | Status |  |  | SingleBit | 616 | FALSE
GTD_TR1_CDC_SCAR |  | SECADOR DE AR | d09b3e5b-7c2f-40d5-9121-e82e185d6ae4 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_CDC_SCAR |  | GTD_DS_00268 | 20260204 | Status |  |  | SingleBit | 675 | FALSE
GTD_LTKGC_89-18_SECB |  | SECCIONADORA BYPASS | 323ec8b0-3d1e-4bec-8c0c-738e522543a7 | SwitchStatus | GTD Trans | [6 empty] | 89-18_GTD |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 1 |  | UTR_GTD_1 | GTD_LTKGC_89-18_SECB |  | GTD_DS_00228 | 20260126 | Status | 30 | AutoSelectWithValue | MultiCoord | 223;224 | FALSE | FALSE | 15 | SingleCoord | 203;203 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TR1_TR1_FVF |  | FALHA VF | 1ac2e9ef-8337-45a4-9b4f-b34a4e32a30c | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_FVF |  | GTD_DS_00276 | 20260204 | Status |  |  | SingleBit | 683 | FALSE
GTD_TR1AT_52-2_BBFC |  | BOBINA DE FECHAMENTO | 29598798-2a2e-4e85-97e7-ce3cd404813c | Status | GTD Trans | [6 empty] | GTD_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR1AT_52-2_BBFC |  | GTD_DS_00237 | 20260204 | Status |  |  | SingleBit | 607 | FALSE
GTD_TR1AT_TR1AT_P_50N2 |  | 50 NEUTRO ESTAGIO 2 | 613834b8-5d43-4450-81fa-f0ad12bd7f9b | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_P_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_P_50N2 |  | GTD_DS_00295 | 20260204 | Status |  |  | SingleBit | 708 | FALSE
GTD_TR1_TR1_TOD |  | 26 - TRIP TEMPERATURA OLEO | 93c28576-cc03-4297-b711-4bb5cb823986 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_TOD |  | GTD_DS_00270 | 20260204 | Status |  |  | SingleBit | 677 | FALSE
GTD_TR1AT_TR1AT_OI |  | OPERAÇÃO INDEVIDA SECCIONADORA | 1675ce6d-6f33-4573-8121-4f4d16548363 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_OI |  | GTD_DS_00252 | 20260204 | Status |  |  | SingleBit | 653 | FALSE
GTD_TR1BT_TR1BT_TED |  | 49 - TRIP TEMPERATURA ENROLAMENTO | f05fb60b-f1ef-4a52-98cc-2c098738db0a | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_TED |  | GTD_DS_00271 | 20260204 | Status |  |  | SingleBit | 679 | FALSE
GTD_LTKGC_LTKGC_P_50F2 |  | 50 FASE ESTAGIO 2 | 97dbb03f-0f69-4e70-9770-18cd2daca395 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_50F2 |  | GTD_DS_00129 | 20260126 | Status |  |  | SingleBit | 263 | FALSE
GTD_TR1_TR1_SCAR |  | SECADOR DE AR | 170c3517-7a79-43e3-a455-0910bd969789 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_SCAR |  | GTD_DS_00267 | 20260204 | Status |  |  | SingleBit | 674 | FALSE
GTD_TR1_TR1_DRTM |  | DEFEITO RELE MONITORAMENTO DE TEMPERATURA | 8c4217b9-155e-4642-997a-60a995dbbb43 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_DRTM |  | GTD_DS_00281 | 20260204 | Status |  |  | SingleBit | 691 | FALSE
GTD_TR1_TR1_63CA |  | 63C ALARME | 42d54633-647c-4be3-ac92-1fac27c6cce3 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_63CA |  | GTD_DS_00264 | 20260204 | Status |  |  | SingleBit | 671 | FALSE
GTD_TR1AT_89-10_DSEC |  | DEFEITO SECCIONADORA | ec791831-f745-4db0-8fdf-c4d0b728d247 | Status | GTD Trans | [6 empty] | GTD_TR1AT_89-10_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1AT_89-10_DSEC |  | GTD_DS_00241 | 20260204 | Status |  |  | SingleBit | 621 | FALSE
GTD_LTKGC_LTKGC_A_79OK |  | 79 COM SUCESSO | ee93fb64-33a5-4822-a014-ba56465dd346 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_79OK |  | GTD_DS_00198 | 20260126 | Status |  |  | SingleBit | 357 | FALSE
GTD_LTKGC_LTKGC_P_67 |  | 67 - FUNCAO DIRECIONAL SOBRECORRENTE | 7731935e-7623-4418-9c18-256515c4d349 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_67 |  | GTD_DS_00139 | 20260126 | Status |  |  | SingleBit | 273 | FALSE
GTD_LTKGC_89-16_DSEC |  | SECCIONADORA | 1847b63a-bfc3-4139-909b-7b5ad9e4ec7e | Status | GTD Trans | [6 empty] | 89-16_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_89-16_DSEC |  | GTD_DS_00137 | 20260126 | Status |  |  | SingleBit | 221 | FALSE
GTD_LTKGC_52-3_DJF1 |  | DISJUNTOR NF | 2c332b70-c089-4f75-b963-373c5a3442bd | SwitchStatus | GTD Trans | [6 empty] | 52-3_GTD |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_GTD_1 | GTD_LTKGC_52-3_DJF1 |  | GTD_DS_00226 | 20260126 | Status | 30 | AutoSelectWithValue | MultiCoord | 200;201 | FALSE | FALSE | 15 | SingleCoord | 200;200 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_LTKGC_LTKGC_AJG2 |  | AJUSTE PARA GRUPO 2 | f8933f0e-8cd1-47d8-8d7c-026e792d20d8 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_AJG2 |  | GTD_DS_00229 | 20260126 | Status | 30 | AutoSelectWithValue | SingleBit | 251 | FALSE | FALSE | 15 | SingleCoord | 205;205 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TR1_TR1_71TL |  | 71 - NIVEL BAIXO OLEO TRAFO | 36c560c4-4589-46c9-bc90-8178900e5319 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_71TL |  | GTD_DS_00262 | 20260204 | Status |  |  | SingleBit | 669 | FALSE
GTD_TR1BT_52-10_BBA2 |  | BOBINA DE ABERTURA 2 | 0b0d736f-5f34-4113-82c6-672dceb01a1f | Status | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR1BT_52-10_BBA2 |  | GTD_DS_00249 | 20260204 | Status |  |  | SingleBit | 639 | FALSE
GTD_TR1_TR1_P_FSIN |  | FALHA SINCRONISMO IRIG B | 3bbfe96f-f90e-4ce1-b0a9-f1ceddd6f7be | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_P_FSIN |  | GTD_DS_00255 | 20260204 | Status |  |  | SingleBit | 662 | FALSE
GTD_B69_B69_CCPN |  | FALTA VCC PAINEL | 20e406ef-b3da-4ae1-917a-66e476f4b7fa | Status | GTD Trans | [6 empty] | ARV_B69_B69_BP |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_B69_B69_CCPN |  | 49cdc185-576e-4a61-8bd6-8b20b3fd07c6 | 20260327 | Status |  |  | SingleBit | 1305 | FALSE
GTD_LTKGC_LTKGC_P_50F1 |  | 50 FASE ESTAGIO 1 | 21fe98fc-8ca4-4d55-b6cf-7317ae92293d | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_50F1 |  | GTD_DS_00130 | 20260126 | Status |  |  | SingleBit | 262 | FALSE
GTD_TR1_TR1_VFMA |  | CHAVE VENTILACAO FORCADA MANUAL | 5aa377a4-c10a-4490-9319-7d98ff4797e7 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___DESABILITOU@HABILITOU___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_VFMA |  | GTD_DS_00278 | 20260204 | Status |  |  | SingleBit | 686 | FALSE
GTD_LTKGC_LTKGC_TPIN |  | TRANSFERENCIA DE PROTECAO | 7d29d29b-39d3-40c5-b2e1-295528b3bd59 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___COMPLETA@INCOMPLETA___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_TPIN |  | GTD_DS_00126 | 20260126 | Status |  |  | SingleBit | 236 | FALSE
GTD_TR1AT_TR1AT_P_50F2 |  | 50 FASE ESTAGIO 2 | 05f61b14-b98b-4c85-a4c9-b6fbf2757d23 | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_P_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_P_50F2 |  | GTD_DS_00292 | 20260204 | Status |  |  | SingleBit | 705 | FALSE
GTD_LTKGC_89-14_SECC |  | SECCIONADORA CARGA | a27ea220-bda7-43f5-b004-722e2b2283bc | SwitchStatus | GTD Trans | [6 empty] | 89-14_GTD |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 2 |  | UTR_GTD_1 | GTD_LTKGC_89-14_SECC |  | GTD_DS_00230 | 20260126 | Status | 30 | AutoSelectWithValue | MultiCoord | 213;214 | FALSE | FALSE | 15 | SingleCoord | 201;201 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_LTKGC_LTKGC_P_51F |  | 51 FASE | 990bb32e-128b-4082-a755-711beb2c461c | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_51F |  | GTD_DS_00128 | 20260126 | Status |  |  | SingleBit | 264 | FALSE
GTD_TR1AT_89-12_DSEC |  | DEFEITO SECCIONADORA | 68c97027-2a4c-4e80-8d62-60b5808bf203 | Status | GTD Trans | [6 empty] | GTD_TR1AT_89-12_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1AT_89-12_DSEC |  | GTD_DS_00242 | 20260204 | Status |  |  | SingleBit | 626 | FALSE
GTD_TR1_TR1_TOA |  | 26 - ALARME TEMPERATURA OLEO | d756cdde-e6ef-4afb-8223-313f5c456544 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_TOA |  | GTD_DS_00269 | 20260204 | Status |  |  | SingleBit | 676 | FALSE
GTD_TR1_TR1_P_FB |  | FASE B | 1cff9ac2-c507-47fd-898a-7be78fdd823d | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_P_FB |  | GTD_DS_00287 | 20260204 | Status |  |  | SingleBit | 700 | FALSE
GTD_TR1_TR1_PERP |  | PERMISSAO PARALELISMO | 4b02c640-f457-4510-b536-c6bbf03c611b | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NÃO PERMITIDO@PERMITIDO___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_PERP |  | GTD_DS_00283 | 20260204 | Status |  |  | SingleBit | 693 | FALSE
GTD_LTKGC_LTKGC_MTRF |  | MODULO TRANSFERIDO | b5f018ad-c1f9-4f56-8219-111085780f2f | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@TRANSFERIDA___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_MTRF |  | GTD_DS_00131 | 20260126 | Status |  |  | SingleBit | 235 | FALSE
GTD_AL21_52-21_51N |  | 51N | d0e4a62a-128f-4c8e-bc60-2da2ac14152f | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL21_52-21_51N |  | 76207d98-38f9-403e-919b-c3f71439fc3f | 20230330 | Status | 30 | DirectOperate | SingleBit | 2430 | FALSE | FALSE | 15 | SingleCoord | 2401;2401 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TR1_TR1_P_FA |  | FASE A | b0b51d27-3386-4d8e-b317-520dc2c02dac | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_P_FA |  | GTD_DS_00286 | 20260204 | Status |  |  | SingleBit | 699 | FALSE
GTD_TR1_TR1_BCDC |  | BLOQUEIO CDC | c3f4ee48-7f82-4649-b0a1-be0f630770c5 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_BCDC |  | GTD_DS_00282 | 20260204 | Status |  |  | SingleBit | 692 | FALSE
GTD_TR1AT_TR1AT_P_50N1 |  | 50 NEUTRO ESTAGIO 1 | f3630f80-0437-44f7-98ff-9a29d6c519a1 | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_P_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_P_50N1 |  | GTD_DS_00294 | 20260204 | Status |  |  | SingleBit | 707 | FALSE
GTD_LTKGC_LTKGC_P_67N2 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E2 | cd08ca85-3e6e-4e1f-8fdf-8b4eb489b986 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_67N2 |  | GTD_DS_00150 | 20260126 | Status |  |  | SingleBit | 278 | FALSE
GTD_TR1_TR1_MDCD |  | MINI DISJUNTOR CDC | 1fc25d78-07fd-40b3-91b7-057c7db3f1f0 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_MDCD |  | GTD_DS_00280 | 20260204 | Status |  |  | SingleBit | 687 | FALSE
GTD_LTKGC_89-14_DSEC |  | SECCIONADORA | ad9c7ccf-59d1-4ae6-900c-246afb1c2fca | Status | GTD Trans | [6 empty] | 89-14_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_89-14_DSEC |  | GTD_DS_00220 | 20260126 | Status |  |  | SingleBit | 216 | FALSE
GTD_TR1AT_52-2_SF6B |  | BAIXA PRESSAO SF6 BLOQUEIO | 82653f5e-228e-43bc-8303-16b0a7065c53 | Status | GTD Trans | [6 empty] | GTD_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1AT_52-2_SF6B |  | GTD_DS_00234 | 20260204 | Status |  |  | SingleBit | 604 | FALSE
GTD_AL21_52-21_SGF |  | SGF | 240db8aa-53b5-4afe-b448-5b398e0720da | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_SGF |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL21_52-21_SGF |  | 16464ffc-f3f7-49d6-a55e-ff8de973e1d2 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2434 | FALSE | FALSE | 15 | SingleCoord | 2402;2402 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_LTKGC_LTKGC_P_62BF |  | 62BF | 97b11097-97f2-4cc0-b618-46d0a9967751 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_62BF |  | GTD_DS_00225 | 20260126 | Status |  |  | SingleBit | 257 | FALSE
GTD_AL21_52-21_79 |  | 79 | 2d1d0e3c-0bc0-4f43-82e7-88f8f2a614a1 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL21_52-21_79 |  | a4c39b21-f1d5-46ef-ac4a-91dbea8afcba | 20230330 | Status | 30 | DirectOperate | SingleBit | 2449 | FALSE | FALSE | 15 | SingleCoord | 2409;2409 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TR1BT_52-10_CCCO |  | FALTA VCC COMANDO | 30cdb1c5-1d66-46e5-b774-fee98e3757d6 | Status | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1BT_52-10_CCCO |  | GTD_DS_00246 | 20260204 | Status |  |  | SingleBit | 635 | FALSE
GTD_LTKGC_LTKGC_P_FSIN |  | FALHA SINCRONISMO IRIG B | a194120d-c575-422e-aa33-e802ea74cfe1 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_FSIN |  | GTD_DS_00223 | 20260126 | Status |  |  | SingleBit | 254 | FALSE
GTD_TR1BT_89-104_DSEC |  | DEFEITO SECCIONADORA | 0229d5d5-18d4-47c4-a021-b8b5861e81e0 | Status | GTD Trans | [6 empty] | GTD_TR1BT_89-104_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1BT_89-104_DSEC |  | GTD_DS_00250 | 20260204 | Status |  |  | SingleBit | 646 | FALSE
GTD_TR1_TR1_P_FC |  | FASE C | a3678386-7774-49ff-acd2-e76ecf24e982 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_P_FC |  | GTD_DS_00288 | 20260204 | Status |  |  | SingleBit | 701 | FALSE
GTD_TR1BT_52-10_43LR |  | 43LR | 87c8dd54-ea2b-4ad9-adc0-62d72e8916e9 | Status | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TR1BT_52-10_43LR |  | GTD_DS_00244 | 20260204 | Status |  |  | SingleBit | 632 | FALSE
GTD_LTKGC_LTKGC_A_FB |  | FASE B | a96a8374-a030-4218-a157-624f9e375718 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_A_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_A_FB |  | GTD_DS_00173 | 20260126 | Status |  |  | SingleBit | 329 | FALSE
GTD_TR1AT_TR1AT_P_50F1 |  | 50 FASE ESTAGIO 1 | 7f32edff-dc76-405f-910c-f64f061eeeb3 | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_P_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_P_50F1 |  | GTD_DS_00291 | 20260204 | Status |  |  | SingleBit | 704 | FALSE
GTD_LTKGC_LTKGC_79 |  | 79 - RELIGAMENTO | 203bbb5f-4256-427c-8a01-4ccfbead39ff | Status | GTD Trans | [6 empty] | 52-3_GTD |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_79 |  | GTD_DS_00232 | 20260126 | Status | 30 | AutoSelectWithValue | SingleBit | 285 | FALSE | FALSE | 15 | SingleCoord | 204;204 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_LTKGC_LTKGC_25 |  | 25 RELE SINCRONISMO | 2fbff8c7-73c4-437b-9a73-9ad6c834ce93 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_25 |  | GTD_DS_00231 | 20260126 | Status | 30 | AutoSelectWithValue | SingleBit | 290 | FALSE | FALSE | 15 | SingleCoord | 206;206 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TR1_TR1_43TC |  | 43TC | 68a79f74-bf3d-43de-a87f-089ecf3c8f97 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_43TC |  | GTD_DS_00251 | 20260204 | Status |  |  | SingleBit | 648 | FALSE
GTD_LTKGC_LTKGC_P_51N1 |  | 51 NEUTRO | 805b073f-d941-4bd9-a470-84c45e7567e4 | Status | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_P_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_P_51N1 |  | GTD_DS_00133 | 20260126 | Status |  |  | SingleBit | 267 | FALSE
GTD_AL21_52-21_81 |  | 81 | f1895238-d8f4-432b-8c0d-a528bc4d0d73 | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL21_52-21_81 |  | eeedd8c2-b8c3-4bb6-9d90-1f321a7b0f84 | 20230330 | Status | 30 | DirectOperate | SingleBit | 2437 | FALSE | FALSE | 15 | SingleCoord | 2403;2403 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TR1_TR1_43VF |  | 43 - CHAVE LOCAL REMOTO VENTILACAO FORCADA | 93008b4e-ef53-4792-85fb-6cd3ff81db45 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom___INV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_43VF |  | GTD_DS_00279 | 20260204 | Status |  |  | SingleBit | 685 | FALSE
GTD_AL21_52-21_46 |  | 46 | f334d7a1-ec82-46d3-aad9-0e7ffa496c27 | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_46 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_46 |  | 2b844796-e5c2-4775-a10e-b13574051652 | 20251121 | Status |  |  | SingleBit | 2436 | FALSE
GTD_AL21_52-21_81E5 |  | 81 ESTAGIO 5 | a22c58e3-da2b-436f-96be-cc5d430901d0 | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_81E5 |  | 8fc609cc-0b6d-4f35-9d7a-0ac552222a83 | 20230330 | Status |  |  | SingleBit | 2448 | FALSE
GTD_AL21_52-21_81E4 |  | 81 ESTAGIO 4 | f65e517c-72eb-46b5-89a4-207e97791a20 | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_81E4 |  | d0515852-955c-48e9-b402-3c7467448395 | 20230330 | Status |  |  | SingleBit | 2447 | FALSE
GTD_AL21_52-21_FSIN |  | FALHA SINCRONISMO IRIG-B | 6f552463-aa0d-4e6d-94bf-9f40e9457d75 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_FSIN |  | 3138da1a-2c49-44e2-ba4b-f3a7656cdcec | 20230330 | Status |  |  | SingleBit | 2418 | FALSE
GTD_AL21_52-21_TOED |  | TEMPERATURA OLEO ENROLAMENTO TRIP | abd2770b-b1bb-4622-b6a9-d9cfb197496f | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_TOED |  | 1d712e52-1375-404a-aa6e-9a4e70206d56 | 20251121 | Status |  |  | SingleBit | 2456 | FALSE
GTD_AL24_52-24_50EF |  | 50EF - END FAULT | 8a2d4e46-b69e-4260-a9e7-75706d917024 | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_50EF |  | 4ca0e5da-b636-414a-a958-817ffb248393 | 20260327 | Status |  |  | SingleBit | 3337 | FALSE
GTD_AL21_52-21_GOOS |  | FALHA GOOSE | cca95163-dd13-484e-9c43-30e510882630 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_GOOS |  | 59b04de8-f749-496a-9811-0712ce3acc86 | 20230330 | Status |  |  | SingleBit | 2416 | FALSE
GTD_BP2_BP2_87_87_T |  | 87_T | 73f306f9-3853-4b65-b162-9374251150dd | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT_87_T |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BP2_BP2_87_87_T |  | ca3899fe-d460-4857-98d1-f9d3abcd7dcd | 20260402 | Status |  |  | SingleBit | 3322 | FALSE
GTD_AL21_52-21_81E3 |  | 81 ESTAGIO 3 | 6dabca5b-1953-4a71-b289-38fc078a48d3 | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_81E3 |  | 0b09e167-ef97-4f48-8eb9-40c004c9d3aa | 20230330 | Status |  |  | SingleBit | 2446 | FALSE
GTD_BP1_BP1_87_87_T |  | 87_T | f42323f9-eaf1-4250-a062-423ff99ecf97 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT_87_T |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BP1_BP1_87_87_T |  | 96cb3741-b277-4009-a8bf-8e9fa35ee447 | 20260402 | Status |  |  | SingleBit | 3222 | FALSE
GTD_AL21_52-21_2649 |  | 26 49 - FUNCAO TEMPERATURA | ec5d6f73-416d-4421-a679-e1e199dd722b | Status | GTD Distr | [6 empty] | IVB_AL21_52-21_PROT_2649 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL21_52-21_2649 |  | 52c4de68-47f4-4c63-bb41-5241be746f87 |  | Status | 30 | DirectOperate | SingleBit | 2455 | FALSE | FALSE | 5 | SingleCoord | 2410;2410 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_AL21_52-21_81U2 |  | AJUSTE PARA 81 ESTAGIO 2 | aad9dcde-5f91-473d-a30e-9dcc30a17a16 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_81U2 |  | d818a867-17f6-4adc-a686-50ecdcba1ab1 |  | Status | 30 | DirectOperate | SingleBit | 2440 | FALSE | FALSE | 5 | SingleCoord | 2405 | ClosePulseOn | 0.25
GTD_AL21_52-21_81U5 |  | AJUSTE PARA 81 ESTAGIO 5 | a3855165-5342-4b19-8d36-456cb6ffe52d | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_81U5 |  | d116654f-34cf-42a5-b649-14b51276550c |  | Status | 30 | DirectOperate | SingleBit | 2443 | FALSE | FALSE | 5 | SingleCoord | 2408 | ClosePulseOn | 0.25
GTD_AL21_52-21_81U1 |  | AJUSTE PARA 81 ESTAGIO 1 | f9415c08-052f-4de5-bf85-f8fdcf41e72a | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_81U1 |  | dafe488b-d3ff-4f51-ba7b-7f03c453bf01 |  | Status | 30 | DirectOperate | SingleBit | 2439 | FALSE | FALSE | 5 | SingleCoord | 2404 | ClosePulseOn | 0.25
GTD_AL21_52-21_81U3 |  | AJUSTE PARA 81 ESTAGIO 3 | 34388b27-89df-42c7-8677-b2529a157fb2 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_81U3 |  | 84b5edc1-142b-40b1-91e7-9592a98c2662 |  | Status | 30 | DirectOperate | SingleBit | 2441 | FALSE | FALSE | 5 | SingleCoord | 2406 | ClosePulseOn | 0.25
GTD_AL21_52-21_81U4 |  | AJUSTE PARA 81 ESTAGIO 4 | ce6d1ec6-1236-4673-b59f-66a6554b173a | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_81U4 |  | ad19b21a-d359-4fdf-a03e-3250fd20df71 |  | Status | 30 | DirectOperate | SingleBit | 2442 | FALSE | FALSE | 5 | SingleCoord | 2407 | ClosePulseOn | 0.25
GTD_TR1AT_TR1AT_P_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | 114c6285-d7a7-4de5-9d8c-0d4c153276b1 | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_P_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_P_67FT |  | GTD_DS_00300 | 20260204 | Status |  |  | SingleBit | 713 | FALSE
GTD_TR1AT_TR1AT_P_67N1 |  | 67 NEUTRO ESTAGIO 1 | 78d16845-e882-4273-b42f-2aa48722c197 | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_P_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_P_67N1 |  | GTD_DS_00301 | 20260204 | Status |  |  | SingleBit | 714 | FALSE
GTD_TR1AT_TR1AT_P_67F1 |  | 67 FASE ESTAGIO 1 | e47d2f22-5cbc-4300-a9fc-16170e790db4 | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_P_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_P_67F1 |  | GTD_DS_00298 | 20260204 | Status |  |  | SingleBit | 711 | FALSE
GTD_TR1AT_TR1AT_P_51N1 |  | 51 NEUTRO | 5ca82c5e-9816-450a-8a6d-d9f1e9eb2a19 | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_P_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_P_51N1 |  | GTD_DS_00296 | 20260204 | Status |  |  | SingleBit | 709 | FALSE
GTD_TR1AT_TR1AT_TEA |  | 49 - ALARME TEMPERATURA ENROLAMENTO | 528a2877-1dee-4bbb-8e03-94742cc00efb | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_TEA |  | GTD_DS_00273 | 20260204 | Status |  |  | SingleBit | 680 | FALSE
GTD_TR1AT_TR1AT_P_59N1 |  | 59 NEUTRO ESTAGIO 1 | 11c4ed11-2488-45bd-8d44-81f6211616bd | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_P_PROT_59N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_P_59N1 |  | GTD_DS_00304 | 20260204 | Status |  |  | SingleBit | 717 | FALSE
GTD_TR1AT_TR1AT_P_59N2 |  | 59 NEUTRO ESTAGIO 2 | f1184c54-6cab-4cb5-9ca0-8c6cd73af94b | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_P_PROT_59N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_P_59N2 |  | GTD_DS_00305 | 20260204 | Status |  |  | SingleBit | 718 | FALSE
GTD_TR1AT_TR1AT_P_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | 9f6b936e-5bd0-4076-9772-943410b99f5a | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_P_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_P_67NT |  | GTD_DS_00303 | 20260204 | Status |  |  | SingleBit | 716 | FALSE
GTD_TR1AT_TR1AT_P_FUTP |  | FALHA FUSIVEL TP | c827a297-8153-4890-a51f-b21bc63eefbf | Status | GTD Trans | [6 empty] | GTD_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_P_FUTP |  | GTD_DS_00309 | 20260204 | Status |  |  | SingleBit | 722 | FALSE
GTD_TR1BT_TR1BT_P_50F1 |  | 50 FASE ESTAGIO 1 | 8fcb8339-03bb-4720-ae13-7a11f6dbfed4 | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_P_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_P_50F1 |  | GTD_DS_00312 | 20260204 | Status |  |  | SingleBit | 725 | FALSE
GTD_TR1BT_P_52-10_62BF |  | 62BF | 178f92e6-03fe-49a5-8530-ed0e030e27c0 | Status | GTD Trans | [6 empty] | GTD_TR1BT_P_52-10_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_P_52-10_62BF |  | GTD_DS_00311 | 20260204 | Status |  |  | SingleBit | 724 | FALSE
GTD_TR1BT_TR1BT_P_51F |  | 51 FASE | 63206d70-71ea-4702-a2e2-392e0644baaa | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_P_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_P_51F |  | GTD_DS_00314 | 20260204 | Status |  |  | SingleBit | 727 | FALSE
GTD_TR1BT_TR1BT_P_50F2 |  | 50 FASE ESTAGIO 2 | 64036965-87e5-4f31-a8d7-fee60b033863 | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_P_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_P_50F2 |  | GTD_DS_00313 | 20260204 | Status |  |  | SingleBit | 726 | FALSE
GTD_TR1BT_TR1BT_P_50N2 |  | 50 NEUTRO ESTAGIO 2 | a0d0e201-1d31-4b78-9667-7afda2b11964 | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_P_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_P_50N2 |  | GTD_DS_00316 | 20260204 | Status |  |  | SingleBit | 729 | FALSE
GTD_TR1AT_52-2_43LR |  | 43LR | 15349daf-513e-47c6-85ef-64ad736a1695 | Status | GTD Trans | [6 empty] | GTD_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom___INV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TR1AT_52-2_43LR |  | GTD_DS_00236 | 20260204 | Status |  |  | SingleBit | 606 | FALSE
GTD_TR1BT_TR1BT_P_TEXT |  | TRIP EXTERNO | 56d68b9a-6c56-4517-9bfd-dbc330856ee9 | Status | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_P_TEXT |  | GTD_DS_00318 | 20260204 | Status |  |  | SingleBit | 731 | FALSE
GTD_TR1BT_TR1BT_P_50N1 |  | 50 NEUTRO ESTAGIO 1 | 19bcf2cf-a82b-405b-912a-8da1178677e5 | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_P_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_P_50N1 |  | GTD_DS_00315 | 20260204 | Status |  |  | SingleBit | 728 | FALSE
GTD_TR1_TR1_A_FSIN |  | FALHA SINCRONISMO IRIG B | 546f84ca-7058-4a60-8ab8-e33b0e0c7fea | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_A_FSIN |  | GTD_DS_00320 | 20260204 | Status |  |  | SingleBit | 784 | FALSE
GTD_TR1_TR1_A_GOOS |  | FALHA GOOSE | 88f9891f-8637-4b21-ae6f-725af96d4e69 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_A_GOOS |  | GTD_DS_00319 | 20260204 | Status |  |  | SingleBit | 782 | FALSE
GTD_TR1_TR1_A_FCOM |  | FALHA COMUNICACAO | cbe81b35-022e-4007-8c7c-4e20b0689adc | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_A_FCOM |  | GTD_DS_00322 | 20260204 | Status |  |  | SingleBit | 786 | FALSE
GTD_TR1_TR1_A_DR |  | DEFEITO RELE | 57e0c8f8-5de5-4501-a6ae-db4b050f5347 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_A_DR |  | GTD_DS_00321 | 20260204 | Status |  |  | SingleBit | 785 | FALSE
GTD_TR1_TR1_A_FA |  | FASE A | eb8491ff-64a8-4a21-931b-08be3da8435c | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_A_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_A_FA |  | GTD_DS_00325 | 20260204 | Status |  |  | SingleBit | 789 | FALSE
GTD_TR1AT_TR1AT_P_TEXT |  | TRIP EXTERNO | 2a80bff1-cffb-475c-9bf8-8cbb378a79f2 | Status | GTD Trans | [6 empty] | GTD_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_P_TEXT |  | GTD_DS_00310 | 20260204 | Status |  |  | SingleBit | 723 | FALSE
GTD_TR1_TR1_A_FB |  | FASE B | d466ed20-33eb-4781-912f-1b88dbcbcd16 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_A_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_A_FB |  | GTD_DS_00326 | 20260204 | Status |  |  | SingleBit | 790 | FALSE
GTD_TR1_TR1_A_87_T |  | 87_T | 99d4dfd6-bf72-43d2-b36c-9c06e9ffc9ee | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_A_PROT_87_T |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_A_87_T |  | GTD_DS_00324 | 20260204 | Status |  |  | SingleBit | 788 | FALSE
GTD_TR1AT_TR1AT_P_67F2 |  | 67 FASE ESTAGIO 2 | fc4a2b01-4ddc-42c3-92be-ae4496960f9d | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_P_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_P_67F2 |  | GTD_DS_00299 | 20260204 | Status |  |  | SingleBit | 712 | FALSE
GTD_B69_B69_FA |  | FASE A | e2f7431b-86dc-4e3b-899b-4f01aa7df290 | Status | GTD Trans | [6 empty] | ARV_B69_B69_BP |  | Custom | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_B69_B69_FA |  | 761d34a1-57c1-43a8-b487-332414bb9d53 | 20260327 | Status |  |  | SingleBit | 1314 | FALSE
GTD_TR1AT_TR1AT_P_51F |  | 51 FASE | 2f0d0784-525d-4798-871a-a3b884ca234f | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_P_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_P_51F |  | GTD_DS_00293 | 20260204 | Status |  |  | SingleBit | 706 | FALSE
GTD_TR1AT_A_52-2_62BF |  | 62BF | 26469d16-11f9-49a9-bc5c-85c549a7d5e9 | Status | GTD Trans | [6 empty] | GTD_TR1AT_A_52-2_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_A_52-2_62BF |  | GTD_DS_00329 | 20260204 | Status |  |  | SingleBit | 793 | FALSE
GTD_TR1AT_TR1AT_A_50F1 |  | 50 FASE ESTAGIO 1 | 2285493c-f9d6-4123-b05f-3e3faebf2ba9 | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_A_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_A_50F1 |  | GTD_DS_00330 | 20260204 | Status |  |  | SingleBit | 794 | FALSE
GTD_TR1AT_TR1AT_A_50F2 |  | 50 FASE ESTAGIO 2 | 2da44efd-65cd-4a16-ac47-c1c34ff7bde1 | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_A_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_A_50F2 |  | GTD_DS_00331 | 20260204 | Status |  |  | SingleBit | 795 | FALSE
GTD_TR1AT_TR1AT_A_50N1 |  | 50 NEUTRO ESTAGIO 1 | 6675da3b-b006-49da-b275-e68d6d5f7333 | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_A_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_A_50N1 |  | GTD_DS_00333 | 20260204 | Status |  |  | SingleBit | 797 | FALSE
GTD_TR1AT_TR1AT_A_51F |  | 51 FASE | 53aeb801-52f8-424c-a5aa-5d3613087ce2 | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_A_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_A_51F |  | GTD_DS_00332 | 20260204 | Status |  |  | SingleBit | 796 | FALSE
GTD_TR1_TR1_A_FC |  | FASE C | dfb0ae4a-dfda-45f2-a1fd-21979c710152 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_A_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_A_FC |  | GTD_DS_00327 | 20260204 | Status |  |  | SingleBit | 791 | FALSE
GTD_TR1AT_TR1AT_A_50N2 |  | 50 NEUTRO ESTAGIO 2 | d761ee8a-80f2-44c9-83e9-a868baadfc56 | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_A_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_A_50N2 |  | GTD_DS_00334 | 20260204 | Status |  |  | SingleBit | 798 | FALSE
GTD_TR1_TR1_A_N |  | NEUTRO | bd6f56de-6a9e-4281-9b24-be10a3adf819 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_A_PROT_N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_A_N |  | GTD_DS_00328 | 20260204 | Status |  |  | SingleBit | 792 | FALSE
GTD_TR1AT_TR1AT_A_51N1 |  | 51 NEUTRO | b8b90b61-878c-49f0-b104-1ad5a13a501a | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_A_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_A_51N1 |  | GTD_DS_00335 | 20260204 | Status |  |  | SingleBit | 799 | FALSE
GTD_TR1AT_TR1AT_A_TEXT |  | TRIP EXTERNO | d6111c8a-ed00-4097-a8bd-f9cf81926753 | Status | GTD Trans | [6 empty] | GTD_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_A_TEXT |  | GTD_DS_00336 | 20260204 | Status |  |  | SingleBit | 800 | FALSE
GTD_TR1BT_TR1BT_A_50N1 |  | 50 NEUTRO ESTAGIO 1 | 487eef5a-c2f4-4084-940a-b3b01edfdf50 | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_50N1 |  | GTD_DS_00341 | 20260204 | Status |  |  | SingleBit | 805 | FALSE
GTD_TR1BT_A_52-10_62BF |  | 62BF | 3f3ef73a-2fc4-472e-aae0-6683a9aca849 | Status | GTD Trans | [6 empty] | GTD_TR1BT_A_52-10_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_A_52-10_62BF |  | GTD_DS_00337 | 20260204 | Status |  |  | SingleBit | 801 | FALSE
GTD_TR1BT_TR1BT_A_50N2 |  | 50 NEUTRO ESTAGIO 2 | 74565bd1-0eee-45f6-abe7-e9d46e6b9210 | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_50N2 |  | GTD_DS_00342 | 20260204 | Status |  |  | SingleBit | 806 | FALSE
GTD_TR1BT_TR1BT_A_51N1 |  | 51 NEUTRO | a2d79f3f-459c-49e2-8de0-3e898bb24ed0 | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_51N1 |  | GTD_DS_00343 | 20260204 | Status |  |  | SingleBit | 807 | FALSE
GTD_TR1BT_TR1BT_A_67 |  | 67 - FUNCAO DIRECIONAL SOBRECORRENTE | 013b963b-6d15-4cf2-89a4-a1853e9a24cb | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_67 |  | GTD_DS_00344 | 20260204 | Status |  |  | SingleBit | 808 | FALSE
GTD_TR1AT_52-2_BBA1 |  | BOBINA DE ABERTURA 1 | 889d6da8-903b-4a12-9b1f-0f1596d77fc6 | Status | GTD Trans | [6 empty] | GTD_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR1AT_52-2_BBA1 |  | GTD_DS_00238 | 20260204 | Status |  |  | SingleBit | 608 | FALSE
GTD_TR1BT_TR1BT_A_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | e4e27448-c533-4ddd-bb9d-352aa917c30e | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_67FT |  | GTD_DS_00347 | 20260204 | Status |  |  | SingleBit | 811 | FALSE
GTD_TR1BT_TR1BT_A_67N2 |  | 67 NEUTRO ESTAGIO 2 | 82fd6684-c97f-4a75-9744-4aa996eca2ff | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_67N2 |  | GTD_DS_00349 | 20260204 | Status |  |  | SingleBit | 813 | FALSE
GTD_TR1BT_TR1BT_A_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | eb9d0dca-eb63-4051-8576-96764cfb8f8a | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_67NT |  | GTD_DS_00350 | 20260204 | Status |  |  | SingleBit | 814 | FALSE
GTD_TR1BT_TR1BT_A_50F2 |  | 50 FASE ESTAGIO 2 | fa21fdfd-593c-4b05-979f-b5ea719495f2 | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_50F2 |  | GTD_DS_00339 | 20260204 | Status |  |  | SingleBit | 803 | FALSE
GTD_TR1BT_TR1BT_A_59N2 |  | 59 NEUTRO ESTAGIO 2 | 371c8806-1b2c-459f-a280-2d9eccf4953e | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_59N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_59N2 |  | GTD_DS_00352 | 20260204 | Status |  |  | SingleBit | 816 | FALSE
GTD_TR1BT_TR1BT_A_51F |  | 51 FASE | c457f4eb-8ec5-4b8b-9ef8-7f5978a99cc2 | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_51F |  | GTD_DS_00340 | 20260204 | Status |  |  | SingleBit | 804 | FALSE
GTD_TR1_TR1_P_GOOS |  | FALHA GOOSE | 754fc416-5039-4231-a2cf-e77a101448b3 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_P_GOOS |  | GTD_DS_00254 | 20260204 | Status |  |  | SingleBit | 660 | FALSE
GTD_TR1BT_TR1BT_A_81E3 |  | 81 - TRIP SUB FREQUENCIA E3 | 8dfa33a0-b07d-4ebe-aed3-84730a750f85 | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_81E3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_81E3 |  | GTD_DS_00357 | 20260204 | Status |  |  | SingleBit | 826 | FALSE
GTD_TR1BT_TR1BT_A_81E1 |  | 81 - TRIP SUB FREQUENCIA E1 | 5a350a30-bc91-40d4-a71e-8a08209c9358 | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_81E1 |  | GTD_DS_00355 | 20260204 | Status |  |  | SingleBit | 824 | FALSE
GTD_TR1BT_TR1BT_A_67F2 |  | 67 FASE ESTAGIO 2 | dd9d695f-ed1f-417b-afd0-b3b89c03df23 | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_67F2 |  | GTD_DS_00346 | 20260204 | Status |  |  | SingleBit | 810 | FALSE
GTD_TR1BT_TR1BT_A_59N1 |  | 59 NEUTRO ESTAGIO 1 | 66fd89bf-0c29-40cb-9ff6-aadb8cf5f7ee | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_59N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_59N1 |  | GTD_DS_00351 | 20260204 | Status |  |  | SingleBit | 815 | FALSE
GTD_TR1BT_TR1BT_A_81E2 |  | 81 - TRIP SUB FREQUENCIA E2 | 9afc2f4e-8051-4b57-baf1-7999f281b8a9 | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_81E2 |  | GTD_DS_00356 | 20260204 | Status |  |  | SingleBit | 825 | FALSE
GTD_TR1BT_TR1BT_A_81E4 |  | 81 - TRIP SUB FREQUENCIA E4 | d343540c-a44c-4673-bb1b-a910b6d71f2f | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_81E4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_81E4 |  | GTD_DS_00358 | 20260204 | Status |  |  | SingleBit | 827 | FALSE
GTD_B69_B69_87_T |  | 87_T | 874453f7-2c43-4b0f-a1b3-3844009b2a14 | Status | GTD Trans | [6 empty] | ARV_B69_B69_BP |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_B69_B69_87_T |  | 4c668acf-a91a-44d8-aa48-75e99cbe8b92 | 20260327 | Status |  |  | SingleBit | 1317 | FALSE
GTD_TR1BT_TR1BT_A_67N1 |  | 67 NEUTRO ESTAGIO 1 | 5f79824a-692c-4c53-9c99-0fe0bf6a99f3 | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_67N1 |  | GTD_DS_00348 | 20260204 | Status |  |  | SingleBit | 812 | FALSE
GTD_TR1BT_TR1BT_A_81O1 |  | 81 - TRIP SOBRE FREQUENCIA E1 | ef9fe85c-7017-4f93-9db2-b0056e4e015a | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_81O1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_81O1 |  | GTD_DS_00365 | 20260204 | Status |  |  | SingleBit | 829 | FALSE
GTD_TR1BT_52-10_BBA1 |  | BOBINA DE ABERTURA 1 | 56e7cb0d-fc69-4044-bc0c-27242ee6aa04 | Status | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR1BT_52-10_BBA1 |  | GTD_DS_00248 | 20260204 | Status |  |  | SingleBit | 638 | FALSE
GTD_TRF03_TRF03_50EF |  | 50EF - END FAULT | 629c0fc4-a4d0-4557-b8aa-e50ddd330e2c | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_50EF |  | 495dfc22-aca4-46af-9be2-51cad3d202e0 | 20260327 | Status |  |  | SingleBit | 1325 | FALSE
GTD_TR2AT_TR2AT_50EF |  | 50EF - END FAULT | 8f1e7ef7-3ddb-4fd3-b66a-93a4f2382ef0 | Status | GTD Trans | [6 empty] | GTD_TR2AT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_50EF |  | 6608e565-abea-4c5c-9bb9-1f82f817528d | 20260327 | Status |  |  | SingleBit | 1327 | FALSE
GTD_TR1BT_TR1BT_A_FUTP |  | FALHA FUSIVEL TP | 686b7795-f3d5-4183-82da-b05fd016e45f | Status | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_FUTP |  | GTD_DS_00366 | 20260204 | Status |  |  | SingleBit | 830 | FALSE
GTD_TR1BT_TR1BT_A_TEXT |  | TRIP EXTERNO | ea112807-42f0-4035-a628-166f8bffd2fa | Status | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_TEXT |  | GTD_DS_00367 | 20260204 | Status |  |  | SingleBit | 831 | FALSE
GTD_TR1_TR1_COMA |  | COMANDADO | a89c88be-cba2-4d69-98f5-413c3a08360e | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TAP_REG |  | Parallel | ABC | None | Read |  | null@null___DESATIVADO@ATIVADO___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_COMA |  | GTD_DS_00369 | 20260204 | Status |  |  | SingleBit | 861 | FALSE
GTD_TR12_TR12_FCSP |  | FALHA COMUNICACAO SPS | 90bf1da4-20e0-4b6e-8b9b-17ce78839601 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR12_TR12_FCSP |  | GTD_DS_00373 | 20260204 | Status |  |  | SingleBit | 889 | FALSE
GTD_TR1_TR1_90LR |  | 43LR RELE 90 | fe2ac313-e5fe-4872-89c1-71e3dcf78a87 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TAP_REG |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom___INV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_TR1_TR1_90LR |  | GTD_DS_00370 | 20260204 | Status |  |  | SingleBit | 862 | FALSE
GTD_B69_B69_87 |  | 87 | a34ce8ff-9944-4b15-b661-a7cdd71a38e1 | Status | GTD Trans | [6 empty] | ARV_B69_B69_BP |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_B69_B69_87 |  | 848acc85-c4d7-42f3-aed4-6ba62f8c776e | 20260327 | Status | 30 | DirectOperate | SingleBit | 1304 | FALSE | FALSE | 5 | SingleCoord | 1300;1300 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TR1_TR1_FPAR |  | SINCRONISMO DO PARALELISMO | 5c7bb09e-2c32-43ef-95e8-676753d9b89f | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_FPAR |  | GTD_DS_00372 | 20260204 | Status |  |  | SingleBit | 864 | FALSE
GTD_TR1AT_TR1AT_P_81E2 |  | 81 - TRIP SUB FREQUENCIA E2 | d6e4a436-85ee-4e95-9b04-6f6645cba36f | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_P_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_P_81E2 |  | GTD_DS_00307 | 20260204 | Status |  |  | SingleBit | 720 | FALSE
GTD_TR1AT_TR1AT_P_81O1 |  | 81 - TRIP SOBRE FREQUENCIA E1 | 725c42c6-163f-4a4c-b2ea-131d297a6ca7 | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_P_PROT_81O1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_P_81O1 |  | GTD_DS_00308 | 20260204 | Status |  |  | SingleBit | 721 | FALSE
GTD_B69_B69_DR |  | DEFEITO RELE | 14ed7f33-2448-4c3a-bf45-7fb466f09b29 | Status | GTD Trans | [6 empty] | ARV_B69_B69_BP |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_B69_B69_DR |  | ab8da451-a490-4311-bedf-cd7e39956128 | 20260327 | Status |  |  | SingleBit | 1312 | FALSE
GTD_TR1AT_TR1AT_P_81E1 |  | 81 - TRIP SUB FREQUENCIA E1 | 095eb1c6-c383-45e0-99f4-1dbec26e927e | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_P_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_P_81E1 |  | GTD_DS_00306 | 20260204 | Status |  |  | SingleBit | 719 | FALSE
GTD_TR1BT_TR1BT_A_50F1 |  | 50 FASE ESTAGIO 1 | 161b8f19-5697-4259-aead-3aa042a37264 | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_50F1 |  | GTD_DS_00338 | 20260204 | Status |  |  | SingleBit | 802 | FALSE
GTD_TR1AT_52-2_BBA2 |  | BOBINA DE ABERTURA 2 | 344e8a45-63cd-41ad-b6a8-8645a4cb2016 | Status | GTD Trans | [6 empty] | GTD_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR1AT_52-2_BBA2 |  | GTD_DS_00239 | 20260204 | Status |  |  | SingleBit | 609 | FALSE
GTD_TR1BT_52-10_BBFC |  | BOBINA DE FECHAMENTO | be67e754-0288-4925-ba39-d4db02d4f3d3 | Status | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR1BT_52-10_BBFC |  | GTD_DS_00247 | 20260204 | Status |  |  | SingleBit | 637 | FALSE
GTD_TR1BT_TR1BT_A_81BLOQ |  | 81 BLOQUEIO DINAMICO | c6b4f940-c69a-4882-ac1c-a9389072f62d | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_81BLOQ |  | GTD_DS_00354 | 20260204 | Status |  |  | SingleBit | 818 | FALSE
GTD_TR1_TR1_P_FCOM |  | FALHA COMUNICACAO | f562a31a-22af-4a51-9a20-2561af4f0177 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_P_FCOM |  | GTD_DS_00257 | 20260204 | Status |  |  | SingleBit | 664 | FALSE
GTD_TR1BT_TR1BT_A_81E5 |  | 81 - TRIP SUB FREQUENCIA E5 | 11940795-7817-49c9-ac62-c9a915293842 | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_81E5 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_81E5 |  | GTD_DS_00359 | 20260204 | Status |  |  | SingleBit | 828 | FALSE
GTD_B69_B69_43TC |  | 43TC | 8b00c95f-2210-49cc-97aa-235ae3403575 | Status | GTD Trans | [6 empty] | ARV_B69_B69_BP |  | Custom | Unknown | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_B69_B69_43TC |  | 8853c291-014a-435b-9e4c-85618845e38d | 20260327 | Status |  |  | SingleBit | 1300 | FALSE
GTD_TR1AT_TR1AT_P_67N2 |  | 67 NEUTRO ESTAGIO 2 | 8b811409-f060-4b9f-bfca-ba6ef36a5ce4 | Status | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_P_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_P_67N2 |  | GTD_DS_00302 | 20260204 | Status |  |  | SingleBit | 715 | FALSE
GTD_TR1BT_TR1BT_P_51N1 |  | 51 NEUTRO | 734619ce-6d11-425e-ad87-57b1cc65d1c2 | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_P_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_P_51N1 |  | GTD_DS_00317 | 20260204 | Status |  |  | SingleBit | 730 | FALSE
GTD_TR1BT_TR1BT_A_67F1 |  | 67 FASE ESTAGIO 1 | 6cf7dd4a-de1e-4a55-a213-43d0c298ecb0 | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_67F1 |  | GTD_DS_00345 | 20260204 | Status |  |  | SingleBit | 809 | FALSE
GTD_TR1BT_52-10_CCMO |  | FALTA VCC MOTOR | 3aff23c0-e3fa-4d90-89c6-1985dbd44006 | Status | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1BT_52-10_CCMO |  | GTD_DS_00245 | 20260204 | Status |  |  | SingleBit | 634 | FALSE
GTD_TR1_TR1_86 |  | 86 BLOQUEIO | 92895e0c-22a6-4956-a5c3-794c38694487 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_86 |  | GTD_DS_00258 | 20260204 | Status |  |  | SingleBit | 665 | FALSE
GTD_TR1_TR1_63TA |  | 63T ALARME | d90226eb-f2b7-48d4-a4a4-fca0a18c8141 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_63TA |  | GTD_DS_00259 | 20260204 | Status |  |  | SingleBit | 666 | FALSE
GTD_TR1_TR1_20TD |  | 20T DESL | 9b6a8db7-ed87-4fdf-95ca-d38854f56928 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_20TD |  | GTD_DS_00263 | 20260204 | Status |  |  | SingleBit | 670 | FALSE
GTD_TR1_TR1_71CL |  | 71 - NIVEL BAIXO OLEO CDC | 45e46149-e0cd-47de-9fc7-be10c715767e | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_71CL |  | GTD_DS_00266 | 20260204 | Status |  |  | SingleBit | 673 | FALSE
GTD_TR1_TR1_P_87_T |  | 87_T | 10ea4a96-5f72-4758-8b8d-cc3cccf669eb | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT_87_T |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_P_87_T |  | GTD_DS_00285 | 20260204 | Status |  |  | SingleBit | 698 | FALSE
GTD_TR1_TR1_AJG2 |  | AJUSTE PARA GRUPO 2 | 6a428029-cc9c-42d0-8c85-7127dfa9f59f | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_AJG2 |  | GTD_DS_00253 | 20260204 | Status | 30 | DirectOperate | SingleBit | 659 | FALSE | FALSE | 15 | SingleCoord | 606;606 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TR1_TR1_MEST |  | MESTRE | 7f9a0371-ff59-4364-be0c-d7b4331dea85 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TAP_REG |  | Custom | ABC | None | ReadWrite |  | null@INDIVIDUAL___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_MEST |  | GTD_DS_00368 | 20260204 | Status | 30 | DirectOperate | SingleBit | 860 | FALSE | FALSE | 15 | SingleCoord | 654 | ClosePulseOn | 0.25
GTD_TR1_TR1_INDI |  | INDIVIDUAL | 3f62ce0d-988d-46f1-9180-c230301ea70c | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TAP_REG |  | Custom | ABC | None | ReadWrite |  | null@MESTRE___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_INDI |  | GTD_DS_00374 | 20260204 | Status | 30 | DirectOperate | SingleBit | 865 | FALSE | FALSE | 15 | SingleCoord | 652 | ClosePulseOn | 0.25
GTD_TR1AT_89-8_SECF |  | SECCIONADORA FONTE | c332a542-833e-4a56-a8c4-9ace9dc5bb42 | SwitchStatus | GTD Trans | [6 empty] | GTD_TR1AT_89-8_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 2 |  | UTR_GTD_1 | GTD_TR1AT_89-8_SECF |  | GTD_DS_00377 | 20260204 | Status | 30 | DirectOperate | MultiCoord | 613;614 | FALSE | FALSE | 15 | SingleCoord | 601;601 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TR1_TR1_CDC |  | CDC | 76dd6e27-dc96-405c-ad38-0386c44051f1 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_COMTAP |  | TapIncrement | ABC | None | Write |  | AUMENTAR@DIMINUIR___null@null___INV_TapIncrement_S_TC_SS_VF | 2 |  | UTR_GTD_1 | GTD_TR1_TR1_CDC |  | GTD_DS_00382 | 20260204 | Status | 0 | DirectOperate | DoubleBit |  | FALSE | FALSE | 15 | MultiCoord | 650;651 | ClosePulseOn;ClosePulseOn | 0.25;0.25
GTD_TR1BT_89-104_SECB |  | SECCIONADORA BYPASS | 09223eb1-a0bc-4fe0-8b9b-598c3641ecbc | SwitchStatus | GTD Trans | [6 empty] | GTD_TR1BT_89-104_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 1 |  | UTR_GTD_1 | GTD_TR1BT_89-104_SECB |  | GTD_DS_00381 | 20260204 | Status | 30 | DirectOperate | MultiCoord | 643;644 | FALSE | FALSE | 15 | SingleCoord | 605;605 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TR1AT_89-10_SECB |  | SECCIONADORA BYPASS | 9b6c0335-c64d-45dc-9d60-faf727df8835 | SwitchStatus | GTD Trans | [6 empty] | GTD_TR1AT_89-10_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 2 |  | UTR_GTD_1 | GTD_TR1AT_89-10_SECB |  | GTD_DS_00378 | 20260204 | Status | 30 | DirectOperate | MultiCoord | 618;619 | FALSE | FALSE | 15 | SingleCoord | 602;602 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TR1AT_52-2_DJF1 |  | DISJUNTOR NF | 959c4ffe-e2f6-4ef8-b285-d9aecc591ddf | SwitchStatus | GTD Trans | [6 empty] | GTD_TR1AT_52-2_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_GTD_1 | GTD_TR1AT_52-2_DJF1 |  | GTD_DS_00376 | 20260204 | Status | 30 | DirectOperate | MultiCoord | 600;601 | FALSE | FALSE | 15 | SingleCoord | 600;600 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TR1_TR1_VF |  | VF | 25216fdf-4b61-4e54-a871-0316c8121a9f | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TC_SV | 2 |  | UTR_GTD_1 | GTD_TR1_TR1_VF |  | GTD_DS_00275 | 20260204 | Status | 30 | DirectOperate | SingleBit | 682 | FALSE | FALSE | 15 | SingleCoord | 999;999 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TR1_TR1_R90 |  | RELE 90 | 320ff677-0129-42f2-9bbb-a970ec54c99c | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TAP_REG |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_TR1_TR1_R90 |  | GTD_DS_00371 | 20260204 | Status | 30 | DirectOperate | SingleBit | 863 | FALSE | FALSE | 15 | MultiCoord | 656;655 | ClosePulseOn;ClosePulseOn | 0.25;0.25
GTD_TR1AT_89-12_SECC |  | SECCIONADORA CARGA | 66242dae-4982-4d5f-9ef0-e3e597916a20 | SwitchStatus | GTD Trans | [6 empty] | GTD_TR1AT_89-12_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 1 |  | UTR_GTD_1 | GTD_TR1AT_89-12_SECC |  | GTD_DS_00379 | 20260204 | Status | 30 | DirectOperate | MultiCoord | 623;624 | FALSE | FALSE | 15 | SingleCoord | 603;603 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TR1BT_52-10_DJF1 |  | DISJUNTOR NF | 57153682-1257-4e2b-8a84-6b0effb6e4b4 | SwitchStatus | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_GTD_1 | GTD_TR1BT_52-10_DJF1 |  | GTD_DS_00380 | 20260204 | Status | 30 | DirectOperate | MultiCoord | 628;629 | FALSE | FALSE | 15 | SingleCoord | 604;604 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TR2AT_52-6_SF6A |  | BAIXA PRESSAO SF6 ALARME | fcd72022-0d70-48f4-b30c-5e8f0786bb86 | Status | GTD Trans | [6 empty] | GTD_TR2AT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2AT_52-6_SF6A |  | GTD_DS_00383 | 20260210 | Status |  |  | SingleBit | 903 | FALSE
GTD_TR2AT_52-6_MOLA |  | MOLA | cc404894-d6fe-49f1-a14d-40c800cfdf8d | Status | GTD Trans | [6 empty] | GTD_TR2AT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2AT_52-6_MOLA |  | GTD_DS_00385 | 20260210 | Status |  |  | SingleBit | 905 | FALSE
GTD_TR2AT_89-40_DSEC |  | DEFEITO SECCIONADORA | 92d77c33-35c0-4f4a-ba8a-f8868a8cf765 | Status | GTD Trans | [6 empty] | GTD_TR2AT_89-40_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2AT_89-40_DSEC |  | GTD_DS_00391 | 20260210 | Status |  |  | SingleBit | 921 | FALSE
GTD_TR2BT_52-20_MOLA |  | MOLA | b41933d0-28b9-4075-a4a8-c91d3326b25b | Status | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2BT_52-20_MOLA |  | GTD_DS_00393 | 20260210 | Status |  |  | SingleBit | 931 | FALSE
GTD_TR2_TR2_P_DR |  | DEFEITO RELE | 7a6ef8f9-8960-4043-bdbf-f287395db9e4 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_P_DR |  | GTD_DS_00406 | 20260210 | Status |  |  | SingleBit | 963 | FALSE
GTD_TR2AT_52-6_SF6B |  | BAIXA PRESSAO SF6 BLOQUEIO | 08d76280-821a-40e3-8022-944e976a3093 | Status | GTD Trans | [6 empty] | GTD_TR2AT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2AT_52-6_SF6B |  | GTD_DS_00384 | 20260210 | Status |  |  | SingleBit | 904 | FALSE
GTD_TR2_TR2_86 |  | 86 BLOQUEIO | 5e65bf84-5e6f-4a28-a657-ac32f5ea5858 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_86 |  | GTD_DS_00408 | 20260210 | Status |  |  | SingleBit | 965 | FALSE
GTD_TR2AT_52-6_BBA2 |  | BOBINA DE ABERTURA 2 | a15fb948-81da-49f6-9bcf-7deeb38390ea | Status | GTD Trans | [6 empty] | GTD_TR2AT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR2AT_52-6_BBA2 |  | GTD_DS_00389 | 20260210 | Status |  |  | SingleBit | 909 | FALSE
GTD_TR2_TR2_63TA |  | 63T ALARME | d4eae7d8-9912-4a38-9e17-d50cb0e036f7 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_63TA |  | GTD_DS_00409 | 20260210 | Status |  |  | SingleBit | 966 | FALSE
GTD_TR2AT_52-6_43LR |  | 43LR | 407b8a99-3464-4d8a-bc8e-ef9b8dc87096 | Status | GTD Trans | [6 empty] | GTD_TR2AT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom___INV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TR2AT_52-6_43LR |  | GTD_DS_00386 | 20260210 | Status |  |  | SingleBit | 906 | FALSE
GTD_TR2_TR2_71TH |  | 71 - NIVEL ALTO OLEO TRAFO | 74481ccd-e01a-4847-8308-2aa6802bd216 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_71TH |  | GTD_DS_00411 | 20260210 | Status |  |  | SingleBit | 968 | FALSE
GTD_TR2BT_52-20_BBFC |  | BOBINA DE FECHAMENTO | de7420fe-f683-40b8-8450-5912e1a28567 | Status | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR2BT_52-20_BBFC |  | GTD_DS_00397 | 20260210 | Status |  |  | SingleBit | 937 | FALSE
GTD_TR2_TR2_63CA |  | 63C ALARME | 4805963a-3bde-40b1-97c5-eb32930d9951 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_63CA |  | GTD_DS_00414 | 20260210 | Status |  |  | SingleBit | 971 | FALSE
GTD_TR2_TR2_P_GOOS |  | FALHA GOOSE | 3e19ddb5-06df-411b-99d4-28c4f7ff79e3 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_P_GOOS |  | GTD_DS_00404 | 20260210 | Status |  |  | SingleBit | 960 | FALSE
GTD_TR2_TR2_SCAR |  | SECADOR DE AR | 987321cc-d036-48a1-88cc-f8f7b0134395 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_SCAR |  | GTD_DS_00417 | 20260210 | Status |  |  | SingleBit | 974 | FALSE
GTD_TR2AT_TR2AT_OI |  | OPERAÇÃO INDEVIDA SECCIONADORA | 868a0659-1057-4b06-8e59-efd93fe4e956 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_OI |  | GTD_DS_00402 | 20260210 | Status |  |  | SingleBit | 953 | FALSE
GTD_TR2_TR2_P_FSIN |  | FALHA SINCRONISMO IRIG B | 551e2e67-445a-4749-bb41-9a8378055724 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_P_FSIN |  | GTD_DS_00405 | 20260210 | Status |  |  | SingleBit | 962 | FALSE
GTD_TR2_TR2_71CH |  | 71 - NIVEL ALTO OLEO CDC | 201777a2-a225-47b2-9f03-623b54256fa4 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_71CH |  | GTD_DS_00415 | 20260210 | Status |  |  | SingleBit | 972 | FALSE
GTD_TR2_TR2_TOA |  | 26 - ALARME TEMPERATURA OLEO | e0d97abb-5131-4e5d-ae56-de821cc432ac | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_TOA |  | GTD_DS_00419 | 20260210 | Status |  |  | SingleBit | 976 | FALSE
GTD_TR2BT_52-20_CCCO |  | FALTA VCC COMANDO | 2d862227-887c-4acb-a01b-4a66e54edd1f | Status | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2BT_52-20_CCCO |  | GTD_DS_00396 | 20260210 | Status |  |  | SingleBit | 935 | FALSE
GTD_TR2_TR2_TOD |  | 26 - TRIP TEMPERATURA OLEO | 91646e35-0861-448f-bdbd-b2501dca6fa3 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_TOD |  | GTD_DS_00420 | 20260210 | Status |  |  | SingleBit | 977 | FALSE
GTD_TR2BT_TR2BT_TEA |  | 49 - ALARME TEMPERATURA ENROLAMENTO | 70c5ad74-56f7-460a-90ff-b3dc584da956 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_TEA |  | GTD_DS_00425 | 20260210 | Status |  |  | SingleBit | 978 | FALSE
GTD_TR2AT_TR2AT_TEA |  | 49 - ALARME TEMPERATURA ENROLAMENTO | 03a7fd08-ebc7-44b2-93f5-62de19cd57a9 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_TEA |  | GTD_DS_00427 | 20260210 | Status |  |  | SingleBit | 980 | FALSE
GTD_TR2_TR2_CAFL |  | FALTA VCA | bea6aa87-1f25-474e-9242-1d01fd8e2f42 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_CAFL |  | GTD_DS_00424 | 20260210 | Status |  |  | SingleBit | 984 | FALSE
GTD_TR2BT_TR2BT_TED |  | 49 - TRIP TEMPERATURA ENROLAMENTO | 833d3c03-482d-4602-b8d4-6b22c36b4b04 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_TED |  | GTD_DS_00423 | 20260210 | Status |  |  | SingleBit | 979 | FALSE
GTD_TR2_CDC_SCAR |  | SECADOR DE AR | 140b5869-ac6f-4c0d-9b4e-120281913e19 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_CDC_SCAR |  | GTD_DS_00418 | 20260210 | Status |  |  | SingleBit | 975 | FALSE
GTD_TR2_TR2_VFMA |  | CHAVE VENTILACAO FORCADA MANUAL | b1664af5-a18d-4b26-91ae-e6b2abfff0a8 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___DESABILITOU@HABILITOU___Custom_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_TR2_TR2_VFMA |  | GTD_DS_00428 | 20260210 | Status |  |  | SingleBit | 986 | FALSE
GTD_TR2AT_TR2AT_TED |  | 49 - TRIP TEMPERATURA ENROLAMENTO | 5b96d8db-d80c-4cd8-8cdc-32845351b33c | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_TED |  | GTD_DS_00429 | 20260210 | Status |  |  | SingleBit | 981 | FALSE
GTD_TR2_TR2_FVF |  | FALHA VF | 655f36e0-d146-4ec6-a9d6-25feab49ac21 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_FVF |  | GTD_DS_00422 | 20260210 | Status |  |  | SingleBit | 983 | FALSE
GTD_TR2_TR2_MDCD |  | MINI DISJUNTOR CDC | 2102dce8-b991-4be9-b14b-a4f8b39a2635 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_MDCD |  | GTD_DS_00430 | 20260210 | Status |  |  | SingleBit | 987 | FALSE
GTD_TR2_TR2_PERP |  | PERMISSAO PARALELISMO | f8420932-3aec-4299-bd1e-95e55cb9aa04 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NÃO PERMITIDO@PERMITIDO___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_PERP |  | GTD_DS_00433 | 20260210 | Status |  |  | SingleBit | 993 | FALSE
GTD_B69_B69_FCOM |  | FALHA COMUNICACAO | ed2136af-ddd8-40aa-9971-6a09c316e9ec | Status | GTD Trans | [6 empty] | ARV_B69_B69_BP |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom___INV_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_B69_B69_FCOM |  | 8e735123-390d-4ac1-82e8-04a30a054a36 | 20260327 | Status |  |  | SingleBit | 1313 | FALSE
GTD_TR2_TR2_DRTM |  | DEFEITO RELE MONITORAMENTO DE TEMPERATURA | c6d4ae0e-0e10-4ae2-ab29-91f731b4f6c5 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_DRTM |  | GTD_DS_00431 | 20260210 | Status |  |  | SingleBit | 991 | FALSE
GTD_TR2_TR2_P_87_T |  | 87_T | f25db3cc-baee-4cc8-95dc-604a3af780ec | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_P_PROT_87_T |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_P_87_T |  | GTD_DS_00435 | 20260210 | Status |  |  | SingleBit | 998 | FALSE
GTD_TR2_TR2_P_FA |  | FASE A | 235ae8c7-7c61-4805-b6c5-f5e278c16ee8 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_P_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_P_FA |  | GTD_DS_00436 | 20260210 | Status |  |  | SingleBit | 999 | FALSE
GTD_TR2_TR2_P_FB |  | FASE B | 3a627945-3aa0-4df5-bf04-3e6097cfeb4f | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_P_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_P_FB |  | GTD_DS_00437 | 20260210 | Status |  |  | SingleBit | 1000 | FALSE
GTD_TR2_TR2_P_FC |  | FASE C | a26daff2-ec32-47ef-b62e-5b669fd789fd | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_P_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_P_FC |  | GTD_DS_00438 | 20260210 | Status |  |  | SingleBit | 1001 | FALSE
GTD_TR2AT_52-6_BBA1 |  | BOBINA DE ABERTURA 1 | ee87935b-17ad-43e4-a454-c9503b08b87d | Status | GTD Trans | [6 empty] | GTD_TR2AT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR2AT_52-6_BBA1 |  | GTD_DS_00388 | 20260210 | Status |  |  | SingleBit | 908 | FALSE
GTD_TR2AT_TR2AT_62BF |  | 62BF | c6a7bf37-feea-4763-a2fe-1b4342a18efd | Status | GTD Trans | [6 empty] | GTD_TR2AT_P_52-6_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_62BF |  | GTD_DS_00440 | 20260210 | Status |  |  | SingleBit | 1003 | FALSE
GTD_TR2AT_TR2AT_P_50F1 |  | 50 FASE ESTAGIO 1 | 58e594a4-564f-440d-a5c5-a03784e648b2 | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_P_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_P_50F1 |  | GTD_DS_00441 | 20260210 | Status |  |  | SingleBit | 1004 | FALSE
GTD_TR2AT_TR2AT_P_51F |  | 51 FASE | bc84d241-d467-4f3d-bca0-80c0fe65d0a2 | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_P_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_P_51F |  | GTD_DS_00443 | 20260210 | Status |  |  | SingleBit | 1006 | FALSE
GTD_TR2_TR2_63TD |  | 63T DESL | 89d9563f-ab22-4734-a8fb-06dbbc765e82 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_63TD |  | GTD_DS_00410 | 20260210 | Status |  |  | SingleBit | 967 | FALSE
GTD_TR2AT_TR2AT_P_50N2 |  | 50 NEUTRO ESTAGIO 2 | c7ff3730-d43b-46a2-b358-834ebe01c7bc | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_P_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_P_50N2 |  | GTD_DS_00445 | 20260210 | Status |  |  | SingleBit | 1008 | FALSE
GTD_TR2_TR2_71CL |  | 71 - NIVEL BAIXO OLEO CDC | 90177949-93c8-4ce8-87d7-82ac0262e23e | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_71CL |  | GTD_DS_00416 | 20260210 | Status |  |  | SingleBit | 973 | FALSE
GTD_TR2AT_TR2AT_P_51N1 |  | 51 NEUTRO | 75f343e8-5b59-4421-b580-de1db0e591ee | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_P_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_P_51N1 |  | GTD_DS_00446 | 20260210 | Status |  |  | SingleBit | 1009 | FALSE
GTD_TR2AT_TR2AT_P_50N1 |  | 50 NEUTRO ESTAGIO 1 | ae504d71-1991-417e-9f7d-3c6039ca2587 | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_P_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_P_50N1 |  | GTD_DS_00444 | 20260210 | Status |  |  | SingleBit | 1007 | FALSE
GTD_TR2AT_TR2AT_P_67 |  | 67 - FUNCAO DIRECIONAL SOBRECORRENTE | c4900b93-87cd-4893-b4cb-8fbe92c39925 | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_P_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_P_67 |  | GTD_DS_00447 | 20260210 | Status |  |  | SingleBit | 1010 | FALSE
GTD_TR2AT_TR2AT_P_67F1 |  | 67 FASE ESTAGIO 1 | 2617bd59-b76e-4a50-bbb1-9886fd46899b | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_P_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_P_67F1 |  | GTD_DS_00448 | 20260210 | Status |  |  | SingleBit | 1011 | FALSE
GTD_TR2AT_TR2AT_P_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | b5527870-d840-4569-8d24-1ae3a439b170 | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_P_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_P_67FT |  | GTD_DS_00450 | 20260210 | Status |  |  | SingleBit | 1013 | FALSE
GTD_TR2AT_TR2AT_P_67N1 |  | 67 NEUTRO ESTAGIO 1 | 9ce3e5a4-d896-4a81-834a-0e34573a7924 | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_P_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_P_67N1 |  | GTD_DS_00451 | 20260210 | Status |  |  | SingleBit | 1014 | FALSE
GTD_TR2AT_TR2AT_P_67N2 |  | 67 NEUTRO ESTAGIO 2 | 9da6d622-d7c8-4220-8d81-8bd51281ae98 | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_P_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_P_67N2 |  | GTD_DS_00452 | 20260210 | Status |  |  | SingleBit | 1015 | FALSE
GTD_TR2AT_TR2AT_P_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | bf868893-5f8f-4635-a63b-ffffc4aabaf1 | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_P_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_P_67NT |  | GTD_DS_00453 | 20260210 | Status |  |  | SingleBit | 1016 | FALSE
GTD_TR2AT_TR2AT_P_67F2 |  | 67 FASE ESTAGIO 2 | 8c799d84-a2c9-4494-bf8b-378a48c0225a | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_P_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_P_67F2 |  | GTD_DS_00449 | 20260210 | Status |  |  | SingleBit | 1012 | FALSE
GTD_TR2AT_TR2AT_P_59N1 |  | 59 NEUTRO ESTAGIO 1 | 8efbeb53-77aa-43f2-a3b6-3b2ea00e4d5f | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_P_PROT_59N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_P_59N1 |  | GTD_DS_00454 | 20260210 | Status |  |  | SingleBit | 1017 | FALSE
GTD_TR2AT_TR2AT_P_81E2 |  | 81 - TRIP SUB FREQUENCIA E2 | 64bad476-549d-4faa-99e8-ee6b9a08c0f5 | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_P_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_P_81E2 |  | GTD_DS_00457 | 20260210 | Status |  |  | SingleBit | 1020 | FALSE
GTD_TR2AT_TR2AT_P_81E1 |  | 81 - TRIP SUB FREQUENCIA E1 | a0a2ef26-2076-4032-9935-d777d524ec7e | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_P_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_P_81E1 |  | GTD_DS_00456 | 20260210 | Status |  |  | SingleBit | 1019 | FALSE
GTD_TR2AT_TR2AT_P_81O1 |  | 81 - TRIP SOBRE FREQUENCIA E1 | 63408131-333b-400a-a828-c47a0fcacd2a | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_P_PROT_81O1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_P_81O1 |  | GTD_DS_00458 | 20260210 | Status |  |  | SingleBit | 1021 | FALSE
GTD_TR2AT_TR2AT_P_59N2 |  | 59 NEUTRO ESTAGIO 2 | c2117156-d6ea-476a-8ae6-e56a28dd9a49 | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_P_PROT_59N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_P_59N2 |  | GTD_DS_00455 | 20260210 | Status |  |  | SingleBit | 1018 | FALSE
GTD_TR2BT_P_52-20_62BF |  | 62BF | f561ebf1-b75d-4326-aba9-ed4680a3bf19 | Status | GTD Trans | [6 empty] | GTD_TR2BT_P_52-20_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_P_52-20_62BF |  | GTD_DS_00461 | 20260210 | Status |  |  | SingleBit | 1024 | FALSE
GTD_TR2AT_TR2AT_P_TEXT |  | TRIP EXTERNO | 2cf74dd6-cfed-4fa4-8304-ed07fc491f32 | Status | GTD Trans | [6 empty] | GTD_TR2AT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_P_TEXT |  | GTD_DS_00460 | 20260210 | Status |  |  | SingleBit | 1023 | FALSE
GTD_TR2BT_TR2BT_P_50F1 |  | 50 FASE ESTAGIO 1 | 5814d06f-5733-478e-be4c-1d798166b45e | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_P_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_P_50F1 |  | GTD_DS_00462 | 20260210 | Status |  |  | SingleBit | 1025 | FALSE
GTD_TR2AT_TR2AT_P_FUTP |  | FALHA FUSIVEL TP | 6d49f02b-6473-4239-b447-6cf548ae9bf4 | Status | GTD Trans | [6 empty] | GTD_TR2AT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_P_FUTP |  | GTD_DS_00459 | 20260210 | Status |  |  | SingleBit | 1022 | FALSE
GTD_TR2BT_TR2BT_P_50F2 |  | 50 FASE ESTAGIO 2 | 608a0ae9-bb67-4cee-9697-8022de076b91 | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_P_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_P_50F2 |  | GTD_DS_00463 | 20260210 | Status |  |  | SingleBit | 1026 | FALSE
GTD_TR2BT_TR2BT_P_51F |  | 51 FASE | ec1ce93b-41c7-4e85-a84d-baeec9df0305 | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_P_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_P_51F |  | GTD_DS_00464 | 20260210 | Status |  |  | SingleBit | 1027 | FALSE
GTD_TR2BT_TR2BT_P_51N1 |  | 51 NEUTRO | b485c7ba-55fe-489d-8db0-e5d7c3cd9fd6 | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_P_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_P_51N1 |  | GTD_DS_00467 | 20260210 | Status |  |  | SingleBit | 1030 | FALSE
GTD_TR2BT_TR2BT_P_50N1 |  | 50 NEUTRO ESTAGIO 1 | ecc9cd26-4c3a-4b32-b70c-11025cba45ec | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_P_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_P_50N1 |  | GTD_DS_00465 | 20260210 | Status |  |  | SingleBit | 1028 | FALSE
GTD_TR2BT_TR2BT_P_TEXT |  | TRIP EXTERNO | e84db6de-1eff-43f8-a7ec-4c976064652c | Status | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_P_TEXT |  | GTD_DS_00468 | 20260210 | Status |  |  | SingleBit | 1031 | FALSE
GTD_TR2_TR2_A_GOOS |  | FALHA GOOSE | cb8c1a1b-2fc1-4be3-a9ca-a340daab0e4a | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_A_GOOS |  | GTD_DS_00469 | 20260210 | Status |  |  | SingleBit | 1052 | FALSE
GTD_TR2_TR2_COMA |  | COMANDADO | 9d3d71c4-9b04-454f-95c0-de306d67e93a | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TAP_REG |  | Parallel | ABC | None | Read |  | null@null___DESATIVADO@ATIVADO___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_COMA |  | GTD_DS_00479 | 20260210 | Status |  |  | SingleBit | 1161 | FALSE
GTD_TR2_TR2_A_DR |  | DEFEITO RELE | 75bd3691-c9e3-43f2-bd8f-8f313605ca4e | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_A_DR |  | GTD_DS_00471 | 20260210 | Status |  |  | SingleBit | 1055 | FALSE
GTD_TR2_TR2_A_FCOM |  | FALHA COMUNICACAO | 98b83559-2bf2-4cd9-a3a8-869f40d3225a | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_A_FCOM |  | GTD_DS_00472 | 20260210 | Status |  |  | SingleBit | 1056 | FALSE
GTD_B69_B69_FC |  | FASE C | 457d1033-5a19-44be-a971-6f0815b0920a | Status | GTD Trans | [6 empty] | ARV_B69_B69_BP |  | Custom | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_B69_B69_FC |  | 7a57af95-da61-49f0-b5e1-06f625f31ca4 | 20260327 | Status |  |  | SingleBit | 1316 | FALSE
GTD_TR2_TR2_A_87_T |  | 87_T | 53c5bbf1-c6b9-47c7-9a55-04184c11a00b | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_A_PROT_87_T |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_A_87_T |  | GTD_DS_00474 | 20260210 | Status |  |  | SingleBit | 1058 | FALSE
GTD_TR2_TR2_A_FA |  | FASE A | 44ca9af8-fb7b-4050-b7ea-2ec98a2469c0 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_A_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_A_FA |  | GTD_DS_00475 | 20260210 | Status |  |  | SingleBit | 1059 | FALSE
GTD_TR2_TR2_A_FB |  | FASE B | c0bc0034-b046-4b0b-910a-4549f970fd15 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_A_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_A_FB |  | GTD_DS_00476 | 20260210 | Status |  |  | SingleBit | 1060 | FALSE
GTD_TR2BT_TR2BT_P_50N2 |  | 50 NEUTRO ESTAGIO 2 | 47351358-a3d6-4bdc-b367-b1f3db3197ea | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_P_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_P_50N2 |  | GTD_DS_00466 | 20260210 | Status |  |  | SingleBit | 1029 | FALSE
GTD_TR2_TR2_A_N |  | NEUTRO | 8c69cf6a-d41b-4b09-9083-74c8dfd1c597 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_A_PROT_N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_A_N |  | GTD_DS_00480 | 20260210 | Status |  |  | SingleBit | 1062 | FALSE
GTD_TR2AT_A_52-6_62BF |  | 62BF | f9095ab3-5795-439c-a713-bf99c60145ff | Status | GTD Trans | [6 empty] | GTD_TR2AT_A_52-6_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_A_62BF |  | GTD_DS_00490 | 20260210 | Status |  |  | SingleBit | 1063 | FALSE
GTD_TR2_TR2_FPAR |  | SINCRONISMO DO PARALELISMO | 7c8c701f-b12e-4fcd-b510-0a646e5f6bd3 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_FPAR |  | GTD_DS_00483 | 20260210 | Status |  |  | SingleBit | 1164 | FALSE
GTD_TR2AT_TR2AT_A_50F2 |  | 50 FASE ESTAGIO 2 | 32869768-009e-4247-b83e-a7a31cd44c57 | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_A_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_A_50F2 |  | GTD_DS_00484 | 20260210 | Status |  |  | SingleBit | 1065 | FALSE
GTD_TR2AT_TR2AT_A_51F |  | 51 FASE | 4341ff20-b22a-4607-b1c2-e22c4a957dc2 | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_A_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_A_51F |  | GTD_DS_00485 | 20260210 | Status |  |  | SingleBit | 1066 | FALSE
GTD_TR2AT_TR2AT_P_50F2 |  | 50 FASE ESTAGIO 2 | 4957d0de-a632-40da-a162-fc63b755986d | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_P_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_P_50F2 |  | GTD_DS_00442 | 20260210 | Status |  |  | SingleBit | 1005 | FALSE
GTD_TR2AT_TR2AT_A_50N1 |  | 50 NEUTRO ESTAGIO 1 | 263275a1-8e39-47f6-a756-c2722687641e | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_A_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_A_50N1 |  | GTD_DS_00486 | 20260210 | Status |  |  | SingleBit | 1067 | FALSE
GTD_TR2AT_TR2AT_A_51N1 |  | 51 NEUTRO | 1ed330e7-ec1c-4a58-9034-74a82565025c | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_A_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_A_51N1 |  | GTD_DS_00488 | 20260210 | Status |  |  | SingleBit | 1069 | FALSE
GTD_TR2_TR2_A_FC |  | FASE C | e5f79495-0351-4723-8eec-f188674855be | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_A_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_A_FC |  | GTD_DS_00478 | 20260210 | Status |  |  | SingleBit | 1061 | FALSE
GTD_TR2AT_TR2AT_A_TEXT |  | TRIP EXTERNO | 9c0a19b1-1911-428c-b751-16ad54af362d | Status | GTD Trans | [6 empty] | GTD_TR2AT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_A_TEXT |  | GTD_DS_00489 | 20260210 | Status |  |  | SingleBit | 1070 | FALSE
GTD_TR2BT_TR2BT_A_50F1 |  | 50 FASE ESTAGIO 1 | d78843b2-6973-4266-ba47-82327f095d96 | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_50F1 |  | GTD_DS_00492 | 20260210 | Status |  |  | SingleBit | 1072 | FALSE
GTD_TR2BT_TR2BT_A_50F2 |  | 50 FASE ESTAGIO 2 | 26d6e2b6-19f6-418a-aaae-afff64345b7a | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_50F2 |  | GTD_DS_00493 | 20260210 | Status |  |  | SingleBit | 1073 | FALSE
GTD_TR2AT_89-38_DSEC |  | DEFEITO SECCIONADORA | afab4ada-930b-456a-a836-fae8a57e5f91 | Status | GTD Trans | [6 empty] | GTD_TR2AT_89-38_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2AT_89-38_DSEC |  | GTD_DS_00390 | 20260210 | Status |  |  | SingleBit | 916 | FALSE
GTD_TR2BT_TR2BT_A_50N1 |  | 50 NEUTRO ESTAGIO 1 | 72a13b2b-6a70-44f8-855d-ecb56f365c85 | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_50N1 |  | GTD_DS_00495 | 20260210 | Status |  |  | SingleBit | 1075 | FALSE
GTD_TR2BT_TR2BT_A_51F |  | 51 FASE | 2d73f4d0-6934-4409-9b2c-585db2cd754f | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_51F |  | GTD_DS_00494 | 20260210 | Status |  |  | SingleBit | 1074 | FALSE
GTD_TR2BT_TR2BT_A_50N2 |  | 50 NEUTRO ESTAGIO 2 | 48388c0c-e505-4553-b4eb-88f2e09f200f | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_50N2 |  | GTD_DS_00496 | 20260210 | Status |  |  | SingleBit | 1076 | FALSE
GTD_TR2BT_TR2BT_A_67F2 |  | 67 FASE ESTAGIO 2 | 3aba5d9c-b96b-4f4b-90e2-4bdf2729065a | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_67F2 |  | GTD_DS_00500 | 20260210 | Status |  |  | SingleBit | 1080 | FALSE
GTD_TR2BT_TR2BT_A_67F1 |  | 67 FASE ESTAGIO 1 | 9277a760-9773-47a6-bbe9-c25dbf1e08a3 | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_67F1 |  | GTD_DS_00499 | 20260210 | Status |  |  | SingleBit | 1079 | FALSE
GTD_TR2AT_89-42_DSEC |  | DEFEITO SECCIONADORA | 63075029-dc44-4a52-9461-30894006c6f9 | Status | GTD Trans | [6 empty] | GTD_TR2AT_89-42_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2AT_89-42_DSEC |  | GTD_DS_00392 | 20260210 | Status |  |  | SingleBit | 926 | FALSE
GTD_TR2BT_A_52-20_62BF |  | 62BF | 1d095da8-8fa4-4c9e-82bd-424a5fc31b3e | Status | GTD Trans | [6 empty] | GTD_TR2BT_A_52-20_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_A_52-20_62BF |  | GTD_DS_00491 | 20260210 | Status |  |  | SingleBit | 1071 | FALSE
GTD_TR2BT_TR2BT_A_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | 92767191-efbf-4987-9fa4-0b6d8cf75e8b | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_67FT |  | GTD_DS_00501 | 20260210 | Status |  |  | SingleBit | 1081 | FALSE
GTD_TR2BT_TR2BT_A_67N1 |  | 67 NEUTRO ESTAGIO 1 | e46c6b5a-ce2a-4b72-9b20-c7b8d487e8d3 | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_67N1 |  | GTD_DS_00502 | 20260210 | Status |  |  | SingleBit | 1082 | FALSE
GTD_TR2BT_TR2BT_A_59N1 |  | 59 NEUTRO ESTAGIO 1 | 4bd816e2-5ec4-4657-b881-56e99e641cf9 | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_59N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_59N1 |  | GTD_DS_00505 | 20260210 | Status |  |  | SingleBit | 1085 | FALSE
GTD_TR2BT_TR2BT_A_59N2 |  | 59 NEUTRO ESTAGIO 2 | b149b9f7-dbf7-4195-9e77-9d2c10703769 | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_59N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_59N2 |  | GTD_DS_00506 | 20260210 | Status |  |  | SingleBit | 1086 | FALSE
GTD_TR2BT_TR2BT_A_67 |  | 67 - FUNCAO DIRECIONAL SOBRECORRENTE | 96695c85-aa85-42e3-bfdf-943750f792f2 | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_67 |  | GTD_DS_00498 | 20260210 | Status |  |  | SingleBit | 1078 | FALSE
GTD_TR2BT_TR2BT_A_51N1 |  | 51 NEUTRO | 6bcb3b02-f702-40c4-afe7-2ea86f80ab7c | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_51N1 |  | GTD_DS_00497 | 20260210 | Status |  |  | SingleBit | 1077 | FALSE
GTD_TR2BT_TR2BT_A_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | 44f7cad0-9166-49f1-8f96-e5a4c62aa595 | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_67NT |  | GTD_DS_00504 | 20260210 | Status |  |  | SingleBit | 1084 | FALSE
GTD_TR1AT_TR1AT_50EF |  | 50EF - END FAULT | 4d28eecf-fc7c-41bd-90a4-945ba4fb4ef4 | Status | GTD Trans | [6 empty] | GTD_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_50EF |  | b1b87536-8a2a-4940-9f83-eb0e837f2dc2 | 20260327 | Status |  |  | SingleBit | 1326 | FALSE
GTD_TR2BT_TR2BT_A_81BLOQ |  | 81 BLOQUEIO DINAMICO | 899f0685-7fe4-4b18-b589-7c5e14e42320 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_81BLOQ |  | GTD_DS_00508 | 20260210 | Status |  |  | SingleBit | 1088 | FALSE
GTD_LTKGC_LTKGC_50EF |  | 50EF - END FAULT | 31f41c0e-f46c-4c86-a38f-3c0b2a74eac8 | Status | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTKGC_LTKGC_50EF |  | aec2e51e-98f5-4241-a0de-095525160e64 | 20260327 | Status |  |  | SingleBit | 1324 | FALSE
GTD_B69_B69_FB |  | FASE B | a50ca82b-33c1-4c71-b01b-b69be6ce522b | Status | GTD Trans | [6 empty] | ARV_B69_B69_BP |  | Custom | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_B69_B69_FB |  | ce5d2975-2cc0-44c7-9265-fd818cec6f98 | 20260327 | Status |  |  | SingleBit | 1315 | FALSE
GTD_LTGTA_LTGTA_50EF |  | 50EF - END FAULT | 250c09b1-1718-4444-a429-990b15a3d5aa | Status | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_LTGTA_LTGTA_50EF |  | 3dc7ba3c-4c61-49ae-9b1f-2eed0f9a7810 | 20260327 | Status |  |  | SingleBit | 1323 | FALSE
GTD_B69_B69_GOOS |  | FALHA GOOSE | 569b1d16-1701-4b74-bf9b-3b32c7bc7435 | Status | GTD Trans | [6 empty] | ARV_B69_B69_BP |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_B69_B69_GOOS |  | a884c2ae-4c8f-49db-8a45-f6203c55c7da | 20260327 | Status |  |  | SingleBit | 1301 | FALSE
GTD_TR2_TR2_P_FCOM |  | FALHA COMUNICACAO | 98e95b19-6bcb-41d5-a887-f3acd2612684 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_P_FCOM |  | GTD_DS_00407 | 20260210 | Status |  |  | SingleBit | 964 | FALSE
GTD_TR2BT_TR2BT_A_81E2 |  | 81 - TRIP SUB FREQUENCIA E2 | 6c5b1c90-ca1f-46ed-a8ef-5e8805d60fd1 | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_81E2 |  | GTD_DS_00515 | 20260210 | Status |  |  | SingleBit | 1095 | FALSE
GTD_TR2BT_TR2BT_A_81E3 |  | 81 - TRIP SUB FREQUENCIA E3 | f7923a4a-9453-4490-bda4-dd83ed3d4c73 | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_81E3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_81E3 |  | GTD_DS_00516 | 20260210 | Status |  |  | SingleBit | 1096 | FALSE
GTD_TR2BT_TR2BT_A_81E4 |  | 81 - TRIP SUB FREQUENCIA E4 | b9b688d3-4711-469f-a3a9-3e21624f0d6a | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_81E4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_81E4 |  | GTD_DS_00517 | 20260210 | Status |  |  | SingleBit | 1097 | FALSE
GTD_TR2BT_TR2BT_A_81E5 |  | 81 - TRIP SUB FREQUENCIA E5 | 743e4f8b-7a29-48f9-b851-027bf4aa15bc | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_81E5 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_81E5 |  | GTD_DS_00518 | 20260210 | Status |  |  | SingleBit | 1098 | FALSE
GTD_TR2BT_TR2BT_A_81O1 |  | 81 - TRIP SOBRE FREQUENCIA E1 | 45fcb1e7-cfdf-4d72-ada4-b3b7f38656f2 | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_81O1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_81O1 |  | GTD_DS_00519 | 20260210 | Status |  |  | SingleBit | 1099 | FALSE
GTD_TR2_TR2_43TC |  | 43TC | 4c3c6442-7e8d-4256-a389-2e4f9f558ce1 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_43TC |  | GTD_DS_00401 | 20260210 | Status |  |  | SingleBit | 948 | FALSE
GTD_TR2BT_TR2BT_A_TEXT |  | TRIP EXTERNO | de3165f3-d9f6-4d83-a0ac-97c19dc34ebe | Status | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_TEXT |  | GTD_DS_00521 | 20260210 | Status |  |  | SingleBit | 1101 | FALSE
GTD_TR2AT_TR2AT_A_50F1 |  | 50 FASE ESTAGIO 1 | cd0ae369-8a50-4ed3-85ff-6c249def3125 | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_A_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_A_50F1 |  | GTD_DS_00482 | 20260210 | Status |  |  | SingleBit | 1064 | FALSE
GTD_TR2_TR2_90LR |  | 43LR RELE 90 | ba7a7b73-ce85-4e6e-b661-f47f0bb4e712 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TAP_REG |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom___INV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_TR2_TR2_90LR |  | GTD_DS_00524 | 20260210 | Status |  |  | SingleBit | 1162 | FALSE
GTD_B69_B69_FSIN |  | FALHA SINCRONISMO IRIG B | e9e165bd-b648-45a5-a645-2982cad567e9 | Status | GTD Trans | [6 empty] | ARV_B69_B69_BP |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_B69_B69_FSIN |  | ca558969-89f8-4161-a8a4-ef75dcd4115a | 20260327 | Status |  |  | SingleBit | 1303 | FALSE
GTD_TR2_TR2_71TL |  | 71 - NIVEL BAIXO OLEO TRAFO | 7bbf113f-48f5-410b-a228-0d3b3a4f3c3c | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_71TL |  | GTD_DS_00412 | 20260210 | Status |  |  | SingleBit | 969 | FALSE
GTD_TR2BT_TR2BT_A_FUTP |  | FALHA FUSIVEL TP | 4617140f-6cc2-4ae7-96ea-6be96c9f7f62 | Status | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_FUTP |  | GTD_DS_00520 | 20260210 | Status |  |  | SingleBit | 1100 | FALSE
GTD_TR2_TR2_20TD |  | 20T DESL | 41150fc5-e6a0-4234-8afd-01a33199d60d | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_20TD |  | GTD_DS_00413 | 20260210 | Status |  |  | SingleBit | 970 | FALSE
GTD_TR2BT_TR2BT_A_67N2 |  | 67 NEUTRO ESTAGIO 2 | 9c8a0664-ea0c-4189-82b9-a767c4ffe11e | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_67N2 |  | GTD_DS_00503 | 20260210 | Status |  |  | SingleBit | 1083 | FALSE
GTD_TR2BT_TR2BT_A_81E1 |  | 81 - TRIP SUB FREQUENCIA E1 | 5a63c076-25ea-41e2-afa6-0e79eb660dd1 | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_81E1 |  | GTD_DS_00514 | 20260210 | Status |  |  | SingleBit | 1094 | FALSE
GTD_TR2_TR2_P_N |  | NEUTRO | 6440de1a-fc59-4c5f-b462-3788f3492071 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_P_PROT_N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_P_N |  | GTD_DS_00439 | 20260210 | Status |  |  | SingleBit | 1002 | FALSE
GTD_TR2AT_TR2AT_A_50N2 |  | 50 NEUTRO ESTAGIO 2 | 786eaa18-7404-4d90-adca-e23fbe6383d0 | Status | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_A_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_A_50N2 |  | GTD_DS_00487 | 20260210 | Status |  |  | SingleBit | 1068 | FALSE
GTD_TR2_TR2_A_FSIN |  | FALHA SINCRONISMO IRIG B | 6cbd77ac-124f-48c5-ab12-e244ab26a504 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_A_FSIN |  | GTD_DS_00470 | 20260210 | Status |  |  | SingleBit | 1054 | FALSE
GTD_TR2BT_52-20_BBA1 |  | BOBINA DE ABERTURA 1 | c8e61ea8-f583-4515-a7c3-4cc77569cb36 | Status | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR2BT_52-20_BBA1 |  | GTD_DS_00398 | 20260210 | Status |  |  | SingleBit | 938 | FALSE
GTD_TR2BT_52-20_CCMO |  | FALTA VCC MOTOR | d4ab9f6e-a7a8-421e-9e4d-02c59a9ccd29 | Status | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2BT_52-20_CCMO |  | GTD_DS_00395 | 20260210 | Status |  |  | SingleBit | 934 | FALSE
GTD_TR2AT_52-6_BBFC |  | BOBINA DE FECHAMENTO | 0a0248e3-97f8-43ef-bb02-f1cc2bec2691 | Status | GTD Trans | [6 empty] | GTD_TR2AT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR2AT_52-6_BBFC |  | GTD_DS_00387 | 20260210 | Status |  |  | SingleBit | 907 | FALSE
GTD_TR2BT_89-204_DSEC |  | DEFEITO SECCIONADORA | 87d0f0cc-98ea-456c-90bb-d9a24f38cd9c | Status | GTD Trans | [6 empty] | GTD_TR2BT_89-204_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2BT_89-204_DSEC |  | GTD_DS_00400 | 20260210 | Status |  |  | SingleBit | 946 | FALSE
GTD_TR2BT_52-20_BBA2 |  | BOBINA DE ABERTURA 2 | 223b7ef4-3840-4d02-ac60-89399dc7979b | Status | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TR2BT_52-20_BBA2 |  | GTD_DS_00399 | 20260210 | Status |  |  | SingleBit | 939 | FALSE
GTD_TR2_TR2_BCDC |  | BLOQUEIO CDC | 88ca5264-5742-4a55-9e99-c0610dd26e94 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_BCDC |  | GTD_DS_00432 | 20260210 | Status |  |  | SingleBit | 992 | FALSE
GTD_TR2_TR2_43VF |  | 43 - CHAVE LOCAL REMOTO VENTILACAO FORCADA | cf86de65-5ae2-49e5-b660-52c34412dede | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom___INV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_TR2_TR2_43VF |  | GTD_DS_00426 | 20260210 | Status |  |  | SingleBit | 985 | FALSE
GTD_TR2BT_52-20_43LR |  | 43LR | 69d3816c-e8c0-4b9a-8392-a7de8c7579dc | Status | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TR2BT_52-20_43LR |  | GTD_DS_00394 | 20260210 | Status |  |  | SingleBit | 932 | FALSE
GTD_TR2_TR2_AJG2 |  | AJUSTE PARA GRUPO 2 | 41c6899b-c9f3-40d3-af50-fdf459551988 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_AJG2 |  | GTD_DS_00403 | 20260210 | Status | 30 | DirectOperate | SingleBit | 959 | FALSE | FALSE | 15 | SingleCoord | 906;906 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TR2_TR2_R90 |  | RELE 90 | 57c4b718-69a5-4eab-a55a-18f523149afe | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TAP_REG |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___INV___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_TR2_TR2_R90 |  | GTD_DS_00481 | 20260210 | Status | 30 | DirectOperate | SingleBit | 1163 | FALSE | FALSE | 15 | MultiCoord | 1056;1055 | ClosePulseOn;ClosePulseOn | 0.25;0.25
GTD_TR2_TR2_VF |  | VF | 2ac4d100-0591-44b1-a585-d98bc571a13f | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___Custom_S_TC_SV | 2 |  | UTR_GTD_1 | GTD_TR2_TR2_VF |  | GTD_DS_00421 | 20260210 | Status | 30 | DirectOperate | SingleBit | 982 | FALSE | FALSE | 15 | SingleCoord | 10001;10001 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TR2_TR2_MEST |  | MESTRE | ef035335-96da-434a-85f5-12188d2f8ece | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TAP_REG |  | Custom | ABC | None | ReadWrite |  | null@INDIVIDUAL___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_MEST |  | GTD_DS_00477 | 20260210 | Status | 30 | DirectOperate | SingleBit | 1160 | FALSE | FALSE | 15 | SingleCoord | 1054 | ClosePulseOn | 0.25
GTD_TR2AT_89-42_SECC |  | SECCIONADORA CARGA | dde9faf1-6c7d-4c1f-8dfc-1a1474e154af | SwitchStatus | GTD Trans | [6 empty] | GTD_TR2AT_89-42_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 1 |  | UTR_GTD_1 | GTD_TR2AT_89-42_SECC |  | GTD_DS_00528 | 20260210 | Status | 30 | DirectOperate | MultiCoord | 923;924 | FALSE | FALSE | 15 | SingleCoord | 903;903 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TR2BT_52-20_DJF1 |  | DISJUNTOR NF | 14233656-1923-4d39-ad15-8c0a38d4e74f | SwitchStatus | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_GTD_1 | GTD_TR2BT_52-20_DJF1 |  | GTD_DS_00529 | 20260210 | Status | 30 | DirectOperate | MultiCoord | 928;929 | FALSE | FALSE | 15 | SingleCoord | 904;904 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TR2AT_89-38_SECF |  | SECCIONADORA FONTE | 54caa58b-234e-4072-9994-66007a5cc198 | SwitchStatus | GTD Trans | [6 empty] | GTD_TR2AT_89-38_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 2 |  | UTR_GTD_1 | GTD_TR2AT_89-38_SECF |  | GTD_DS_00526 | 20260210 | Status | 30 | DirectOperate | MultiCoord | 913;914 | FALSE | FALSE | 15 | SingleCoord | 901;901 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TR2_TR2_CDC |  | CDC | 391cb75e-3312-4c19-9174-d5c191063369 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_COMTAP |  | TapIncrement | ABC | None | Write |  | AUMENTAR@DIMINUIR___null@null___INV_TapIncrement_S_TC_SS_VF | 2 |  | UTR_GTD_1 | GTD_TR2_TR2_CDC |  | GTD_DS_00531 | 20260210 | Status | 0 | DirectOperate | DoubleBit |  | FALSE | FALSE | 15 | MultiCoord | 1050;1051 | ClosePulseOn;ClosePulseOn | 0.25;0.25
GTD_TR2_TR2_INDI |  | INDIVIDUAL | 19e1b055-f119-42c8-ba55-c2fed3465d18 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TAP_REG |  | Custom | ABC | None | ReadWrite |  | null@MESTRE___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_INDI |  | GTD_DS_00522 | 20260210 | Status | 30 | DirectOperate | SingleBit | 1165 | FALSE | FALSE | 15 | SingleCoord | 1052 | ClosePulseOn | 0.25
GTD_TR2AT_89-40_SECB |  | SECCIONADORA BYPASS | e136a2bb-8718-4e23-a7d3-a81971ae9dd8 | SwitchStatus | GTD Trans | [6 empty] | GTD_TR2AT_89-40_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 2 |  | UTR_GTD_1 | GTD_TR2AT_89-40_SECB |  | GTD_DS_00527 | 20260210 | Status | 30 | DirectOperate | MultiCoord | 918;919 | FALSE | FALSE | 15 | SingleCoord | 902;902 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TR2AT_52-6_DJF1 |  | DISJUNTOR NF | 8648fee9-60c6-45ec-bc02-10bb5b057969 | SwitchStatus | GTD Trans | [6 empty] | GTD_TR2AT_52-6_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_GTD_1 | GTD_TR2AT_52-6_DJF1 |  | GTD_DS_00525 | 20260210 | Status | 30 | DirectOperate | MultiCoord | 900;901 | FALSE | FALSE | 15 | SingleCoord | 900;900 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TR2BT_89-204_SECB |  | SECCIONADORA BYPASS | 4391aafa-ba16-45cf-aaf3-2d6eb2373b66 | SwitchStatus | GTD Trans | [6 empty] | GTD_TR2BT_89-204_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 1 |  | UTR_GTD_1 | GTD_TR2BT_89-204_SECB |  | GTD_DS_00530 | 20260210 | Status | 30 | DirectOperate | MultiCoord | 943;944 | FALSE | FALSE | 15 | SingleCoord | 905;905 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TRF03_TRF03_P_67N2 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E2 | 63ae0ebb-d18f-4bd4-8f9e-3af559912cfa | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_67N2 |  | ba468877-49e1-4c56-9728-7837daa81d58 | 20260113 | Status |  |  | SingleBit | 470 | FALSE
GTD_TRF03_TRF03_A_25ER |  | 25 FALHA SINCRONISMO | 9d6da3c2-47cd-41a9-91fe-8f76273cf11a | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_25ER |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_25ER |  | e48f5b9a-08b9-4a57-b49f-7480f3036610 | 20260113 | Status |  |  | SingleBit | 563 | FALSE
GTD_TRF03_TRF03_P_TEXT |  | TRIP EXTERNO | 929a6564-4c9e-4e1a-bebf-984409882cce | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_TEXT |  | 96128927-2d6f-47ce-988d-f1bd9367b31a | 20260113 | Status |  |  | SingleBit | 490 | FALSE
GTD_TRF03_TRF03_P_50F2 |  | 50 FASE ESTAGIO 2 | 9d9baef6-594b-405a-ad08-be185ce66483 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_50F2 |  | 0aa031e6-7f2a-49e4-a2aa-0cb60e10ddd5 | 20260113 | Status |  |  | SingleBit | 455 | FALSE
GTD_TRF03_TRF03_A_50N2 |  | 50 NEUTRO ESTAGIO 2 | 5c7f5a4d-3cf7-4d4f-bc5f-c5dcc6700905 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_50N2 |  | 8d157f39-b7ad-4c36-80d6-5cb395488511 | 20260113 | Status |  |  | SingleBit | 538 | FALSE
GTD_TRF03_TRF03_P_51F |  | 51 FASE | 7ff5bea3-bae1-49a7-bde6-3b7f033b388b | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_51F |  | fa89102f-0896-421c-b76a-89ed99380c3e | 20260113 | Status |  |  | SingleBit | 456 | FALSE
GTD_TRF03_TRF03_A_50N1 |  | 50 NEUTRO ESTAGIO 1 | c7ee68a2-47b9-4358-9cb5-66b2b6985815 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_50N1 |  | c8651569-c891-4d81-be28-a7bc71a11644 | 20260113 | Status |  |  | SingleBit | 537 | FALSE
GTD_TRF03_24-3_BBA2 |  | BOBINA ABERTURA 2 | 15c91bd5-d6d4-42d1-bbee-c50a2ede1dcb | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_24-3_BBA2 |  | 64f0a33e-9b8a-4795-9d9c-6d49aeb5c8ed | 20260113 | Status |  |  | SingleBit | 414 | FALSE
GTD_TRF03_TRF03_A_FC |  | FASE C | 843970fd-7f7a-493e-ab11-a097bed74220 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_FC |  | 282c41f3-db0e-4f6c-a61f-77970c36aa32 | 20260113 | Status |  |  | SingleBit | 532 | FALSE
GTD_TRF03_TRF03_A_FCOM |  | FALHA COMUNICACAO | da0ad120-8986-4f02-8ce0-4c4b18cb66e2 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom___INV_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_FCOM |  | 53fd9da2-3ceb-44ae-82ec-add17b02964d | 20260113 | Status |  |  | SingleBit | 528 | FALSE
GTD_TRF03_TRF03_P_79OK |  | 79 COM SUCESSO | 73f32a2f-effd-414e-b51b-5980af5f482b | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_79OK |  | 00190d7a-4749-4cc7-9d9b-946a5ae2547a | 20260113 | Status |  |  | SingleBit | 479 | FALSE
GTD_TRF03_24-3_SF6B |  | BAIXA PRESSAO SF6 BLOQUEIO | 3c46b6c2-cad3-4871-9dca-94972137bbaa | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_24-3_SF6B |  | 9422cf65-0ac2-4935-ba57-80909c14e5e7 | 20260113 | Status |  |  | SingleBit | 409 | FALSE
GTD_TRF03_TRF03_P_FA |  | FASE A | 0ad6b5f9-89c0-4c97-a022-ed832f03472b | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_FA |  | 0185680d-f6dc-4eb3-90cb-b3b64608e678 | 20260113 | Status |  |  | SingleBit | 450 | FALSE
GTD_TRF03_TRF03_P_21Z4 |  | 21 - TRIP ZONA 4 | e0fc934b-1234-495b-b9cf-3dc79cbc6316 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_21Z4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_21Z4 |  | bfb46193-a05e-41f6-b724-a3716922b319 | 20260113 | Status |  |  | SingleBit | 464 | FALSE
GTD_TRF03_TRF03_P_GOOS |  | FALHA GOOSE | 57beafcc-535a-40d1-8a0a-0406af7e1979 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_GOOS |  | bbcd21bc-72a5-4ec2-bbf8-3cd1345109a0 | 20260113 | Status |  |  | SingleBit | 444 | FALSE
GTD_TRF03_TRF03_A_81O1 |  | 81 - TRIP SOBRE FREQUENCIA E1 | cc92974d-9a86-43dc-80f3-112156325673 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_81O1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_81O1 |  | 7e66be2a-22db-41a2-9999-5c3a99149458 | 20260113 | Status |  |  | SingleBit | 556 | FALSE
GTD_TRF03_TRF03_P_51N1 |  | 51 NEUTRO | 51e09bdc-a9ff-458f-afbb-7e19c90e5802 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_51N1 |  | eb941bec-9561-47f5-b574-4bc4d0a79415 | 20260113 | Status |  |  | SingleBit | 459 | FALSE
GTD_TRF03_TRF03_A_81E2 |  | 81 - TRIP SUB FREQUENCIA E2 | 412708f6-b3cb-46ce-bfe7-65b7763587dc | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_81E2 |  | 289c28bc-2805-486d-8cf9-3a6f0ec20af0 | 20260113 | Status |  |  | SingleBit | 555 | FALSE
GTD_TRF03_TRF03_A_DR |  | DEFEITO RELE | 06bfb940-4618-4b7e-a0fc-d176a76532f5 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_DR |  | e6b7dc86-a7a1-4e3d-b0a7-796cc7f34175 | 20260113 | Status |  |  | SingleBit | 527 | FALSE
GTD_TRF03_TRF03_P_59_T |  | 59 - TRIP SOBRETENSAO | 8d3d843a-e16d-4929-853c-294011e2ed10 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | Unknown | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_59_T |  | 58e05c5e-febf-4e1b-bce7-3744d28bcfdd | 20260113 | Status |  |  | SingleBit | 473 | FALSE
GTD_TRF03_TRF03_43TC |  | 43TC | 0c407d50-c066-46a8-bba5-38f445982287 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_43TC |  | e4c46067-07ee-4049-9158-42971fafc54c | 20260113 | Status |  |  | SingleBit | 428 | FALSE
GTD_TRF03_TRF03_A_51F |  | 51 FASE | 1884fb6f-7b81-441f-90f4-c28ef0704ffd | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_51F |  | 7d6ceb8b-e320-4bd7-baaf-ae1ee35d3aa6 | 20260113 | Status |  |  | SingleBit | 536 | FALSE
GTD_TRF03_TRF03_P_50F1 |  | 50 FASE ESTAGIO 1 | dae589a5-eadb-421d-8f04-4c01fabbcabe | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_50F1 |  | eee696ec-5d00-4274-a812-041153af7f0f | 20260113 | Status |  |  | SingleBit | 454 | FALSE
GTD_TRF03_TRF03_P_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | 7b594b67-9449-4b2b-bee0-3e8313c71100 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_67FT |  | ebf94cd2-e957-4a98-a14c-878384a38790 | 20260113 | Status |  |  | SingleBit | 468 | FALSE
GTD_TRF03_TRF03_A_21Z1 |  | 21 - TRIP ZONA 1 | f425d11a-b9d3-44cd-a3f2-5d75c97c97f6 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_21Z1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_21Z1 |  | 2d648421-3ed9-4aab-a7ff-6397680a2174 | 20260113 | Status |  |  | SingleBit | 541 | FALSE
GTD_TRF03_TRF03_A_25AT |  | 25 - TRIP DIFERENCA DE ANGULO | 1cb55619-8c6c-408a-b068-b04cbcfe824f | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_25AT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_25AT |  | 212b216d-46bc-4f73-bce7-8810375a0802 | 20260113 | Status |  |  | SingleBit | 566 | FALSE
GTD_TRF03_TRF03_P_67 |  | 67 - FUNCAO DIRECIONAL SOBRECORRENTE | c3e08195-d667-4fcd-935c-1499ab102fa1 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_67 |  | 831d6d75-b9d0-4ee1-9b39-0535634fc0be | 20260113 | Status |  |  | SingleBit | 465 | FALSE
GTD_TRF03_24-3_BBA1 |  | BOBINA ABERTURA 1 | 7ee69e83-2d67-4420-ae03-33286da78056 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_24-3_BBA1 |  | d1147586-5307-442b-a9d3-871c47a82a5f | 20260113 | Status |  |  | SingleBit | 413 | FALSE
GTD_TRF03_TRF03_P_25VT |  | 25 - TRIP DIFERENCA TENSAO | a8df69cf-48ae-4cdc-8e7a-28b6d12af5a1 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_25VT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_25VT |  | 72f026a3-1ad9-4ee3-883f-54699a7f40b6 | 20260113 | Status |  |  | SingleBit | 484 | FALSE
GTD_TRF03_TRF03_A_FB |  | FASE B | e6c54c3e-129d-44ff-90f2-e059d332e294 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_FB |  | 23d0d4e6-56eb-43ad-85c6-b183b69803d1 | 20260113 | Status |  |  | SingleBit | 531 | FALSE
GTD_TRF03_TRF03_P_21Z3 |  | 21 - TRIP ZONA 3 | 94247754-50eb-474d-b9e1-4b04f1fd5ced | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_21Z3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_21Z3 |  | c458a2f0-6f63-4b86-ad0e-aff482b0ec8d | 20260113 | Status |  |  | SingleBit | 463 | FALSE
GTD_TRF03_TRF03_P_FSIN |  | FALHA SINCRONISMO IRIG B | 61b30041-81a7-4a6a-b47c-b1057100d1a7 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_FSIN |  | bc205d71-4062-4deb-9a22-bf69d79fe4d3 | 20260113 | Status |  |  | SingleBit | 446 | FALSE
GTD_TRF03_TRF03_A_79LO |  | 79 BLOQUEADO | 34005bb9-8bdc-4c92-b284-c14787fb9fc6 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_79LO |  | 40af1238-3cd2-4889-a4fc-d773767d6b6c | 20260113 | Status |  |  | SingleBit | 560 | FALSE
GTD_TRF03_TRF03_P_79_1 |  | 79 PARTIDA | ff18016f-48df-458c-961e-bf503c9074e1 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_79_1 |  | 2183a34f-b465-4441-8bc1-dd93b37a9b71 | 20260113 | Status |  |  | SingleBit | 478 | FALSE
GTD_TRF03_TRF03_A_21 |  | 21 - FUNCAO DISTANCIA | e687e4df-1bbf-4fac-8a56-287eec12a507 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_21 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_21 |  | 45152798-6f73-4775-a166-a63c366d895c | 20260113 | Status |  |  | SingleBit | 540 | FALSE
GTD_TRF03_TRF03_A_79RE |  | 79 RESET | 6b17688b-eb06-4438-9791-a98336169fa3 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_79RE |  | 876caa17-1845-4d0e-9514-286ebecc83fd | 20260113 | Status |  |  | SingleBit | 561 | FALSE
GTD_TRF03_24-3_SF6A |  | BAIXA PRESSAO SF6 ALARME | aeeb8c0d-aaca-4de3-883d-318935aeba10 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_24-3_SF6A |  | d0ac7a37-407a-4e6f-8040-9c72e59faa78 | 20260113 | Status |  |  | SingleBit | 408 | FALSE
GTD_TRF03_TRF03_A_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | bbdfcbf3-ba91-49d4-9dc6-f3fe1e542d97 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_67NT |  | 141e691e-b7cf-40e9-9eb7-aab93d92e518 | 20260113 | Status |  |  | SingleBit | 551 | FALSE
GTD_TRF03_TRF03_P_50N2 |  | 50 NEUTRO ESTAGIO 2 | 4c0ed3d1-7fb5-425c-9edf-b46631686a54 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_50N2 |  | 4e541259-e50a-49bf-b224-4c9d1f09ed7d | 20260113 | Status |  |  | SingleBit | 458 | FALSE
GTD_TRF03_TRF03_P_62BF |  | 62BF | 308ffd8d-b924-4585-be37-8479ab057f9e | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_62BF |  | 8afb1b47-b27c-47d6-8b89-cabda1a91642 | 20260113 | Status |  |  | SingleBit | 449 | FALSE
GTD_TRF03_TRF03_A_81E1 |  | 81 - TRIP SUB FREQUENCIA E1 | a01fdda6-3075-46c7-8c13-f034a0dbe0ee | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_81E1 |  | 52365f1f-4835-4f0d-8b5b-bf02283c010e | 20260113 | Status |  |  | SingleBit | 554 | FALSE
GTD_TRF03_TRF03_P_27_T |  | 27 - TRIP SUBTENSAO | d5f8790d-2d39-43ca-baaa-a9ee8e10f220 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_27_T |  | 326d2535-67bd-4507-8ee6-0cc7169ce863 | 20260113 | Status |  |  | SingleBit | 472 | FALSE
GTD_TRF03_TRF03_A_TEXT |  | TRIP EXTERNO | 405608e5-2e51-494f-aca6-76450664e1e3 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_TEXT |  | 9bb62b72-32b0-49d6-8e4b-28ba57b40c20 | 20260113 | Status |  |  | SingleBit | 570 | FALSE
GTD_TRF03_TRF03_A_50F2 |  | 50 FASE ESTAGIO 2 | 5478b31f-2b95-4b78-8cfe-a6020f53310a | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_50F2 |  | 7da42822-b3b7-4518-81f0-c60272f8a592 | 20260113 | Status |  |  | SingleBit | 535 | FALSE
GTD_TRF03_TRF03_A_67N1 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E1 | 97b6da2c-b76d-499b-8663-c6b938d5166c | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_67N1 |  | 79320a85-9539-496f-b62a-a04ea6fe85cf | 20260113 | Status |  |  | SingleBit | 549 | FALSE
GTD_TRF03_TRF03_A_25FT |  | 25 - TRIP DIFERENCA FREQUENCIA | 639bb140-85a3-4f50-b489-0fb3b32f3562 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_25FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_25FT |  | 32d30c15-16e0-4120-aa14-5f0e9a3130e1 | 20260113 | Status |  |  | SingleBit | 565 | FALSE
GTD_TRF03_TRF03_P_79LO |  | 79 BLOQUEADO | c7d0c2bc-08d7-48af-a97b-4c768c9c1685 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_79LO |  | 32ca5c4a-17b6-4b04-a756-beb3b0bda09c | 20260113 | Status |  |  | SingleBit | 480 | FALSE
GTD_TRF03_TRF03_P_67F2 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E2 | 14269942-d8e2-41ae-8c05-531d14b131f2 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_67F2 |  | 1e07a78f-27c7-4cdf-a727-fcdfa17ed078 | 20260113 | Status |  |  | SingleBit | 467 | FALSE
GTD_TRF03_24-3_BBFC |  | BOBINA FECHAMENTO | 00e8d7c7-58d5-4b2d-945e-e394f38f8274 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_24-3_BBFC |  | 9989864d-52dd-497d-bcd5-213e9103fb3a | 20260113 | Status |  |  | SingleBit | 412 | FALSE
GTD_TRF03_TRF03_P_25ER |  | 25 FALHA SINCRONISMO | df2d78f7-1a3d-40ce-b890-85e14449b6df | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_25ER |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_25ER |  | 9c5a03e6-b818-4f0c-9514-ace8244d47f5 | 20260113 | Status |  |  | SingleBit | 483 | FALSE
GTD_TRF03_TRF03_A_FA |  | FASE A | 701d7a31-87f3-4329-9297-88e5dc621913 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_FA |  | 42d13f3a-3d67-44e5-9bdf-7ca53094cf77 | 20260113 | Status |  |  | SingleBit | 530 | FALSE
GTD_TRF03_TRF03_P_FCOM |  | FALHA COMUNICACAO | ab0b4357-9827-400f-9644-1651fcac7f64 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom___INV_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_FCOM |  | 2bfdf5de-4512-442a-8943-e55304c33bfd | 20260113 | Status |  |  | SingleBit | 448 | FALSE
GTD_TRF03_TRF03_A_21Z4 |  | 21 - TRIP ZONA 4 | 09224859-e7af-4168-ad98-c974c7ab6395 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_21Z4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_21Z4 |  | 9f59e0e6-a0f2-451a-9c25-7f15eb3bceb5 | 20260113 | Status |  |  | SingleBit | 544 | FALSE
GTD_TRF03_TRF03_P_FCSF |  | FECHAMENTO SOB FALTA | 02cdb307-d3a3-459e-9ddf-2d28221bed6f | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_FCSF |  | 281923c9-93dc-40ce-86d1-43aacb0bfa01 | 20260113 | Status |  |  | SingleBit | 489 | FALSE
GTD_TRF03_TRF03_P_81O1 |  | 81 - TRIP SOBRE FREQUENCIA E1 | df73a71f-8af1-464f-add7-2955c93f64c1 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_81O1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_81O1 |  | 86cec335-8587-4d74-bd03-feb6e4eb2a5c | 20260113 | Status |  |  | SingleBit | 476 | FALSE
GTD_TRF03_24-3_MOLA |  | MOLA | 4d7557a7-841c-4fef-8b5e-f11409f02484 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_24-3_MOLA |  | ae5ef8bb-2e7d-4d4d-bcbb-99e5eb4362bd | 20260113 | Status |  |  | SingleBit | 410 | FALSE
GTD_TRF03_TRF03_OI |  | OPERACAO INDEVIDA SEC | 98f101cc-b01a-4cf5-af33-f0ed33879f5b | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_OI |  | 26857ab0-3aad-4e1c-8884-3be8deff0877 | 20260113 | Status |  |  | SingleBit | 429 | FALSE
GTD_TRF03_TRF03_A_79OK |  | 79 COM SUCESSO | 792f81c5-de43-407b-95c3-dce136d0e66a | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_79OK |  | 80f03bc4-6833-4368-8cef-a386237aba40 | 20260113 | Status |  |  | SingleBit | 559 | FALSE
GTD_TRF03_TRF03_A_51N1 |  | 51 NEUTRO | 4051777c-1085-4387-90d3-5aa749b2d79f | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_51N1 |  | 8e3ce572-2126-4462-b041-ed9f7e04fd1a | 20260113 | Status |  |  | SingleBit | 539 | FALSE
GTD_TRF03_TRF03_A_59_T |  | 59 - TRIP SOBRETENSAO | 309f046a-eb27-4e9d-9cc7-61b601edf2a2 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | Unknown | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_59_T |  | 6bdb0050-0be9-4acc-bdf1-1762b1e5583d | 20260113 | Status |  |  | SingleBit | 553 | FALSE
GTD_TRF03_TRF03_P_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | 9b0373c1-244e-4884-b9da-e83961f92b34 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_67NT |  | d66d2f40-a8ea-4ea9-8ca5-4149f10ead42 | 20260113 | Status |  |  | SingleBit | 471 | FALSE
GTD_TRF03_TRF03_A_FCSF |  | FECHAMENTO SOB FALTA | 3281785c-c4c5-4dee-b5de-6811b8883d17 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_FCSF |  | 58130ec4-b064-49c3-b435-340aed89cf6a | 20260113 | Status |  |  | SingleBit | 569 | FALSE
GTD_TRF03_TRF03_A_50F1 |  | 50 FASE ESTAGIO 1 | ac44a3b2-617e-4415-9ccd-32d23ad842a2 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_50F1 |  | 4614a56a-03a0-4e05-ae4f-437f616c3b57 | 20260113 | Status |  |  | SingleBit | 534 | FALSE
GTD_TRF03_TRF03_P_FC |  | FASE C | c936b50d-fb61-4292-ab7f-31f1d4b08d54 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_FC |  | 7090ca72-289f-42d1-ae15-73a9fd684bc6 | 20260113 | Status |  |  | SingleBit | 452 | FALSE
GTD_TRF03_TRF03_A_67 |  | 67 - FUNCAO DIRECIONAL SOBRECORRENTE | 1968430d-dd43-4e17-b678-4b9a6e45ecb4 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_67 |  | 6b3adf07-6484-44cf-a0c3-c83ed9375a38 | 20260113 | Status |  |  | SingleBit | 545 | FALSE
GTD_TRF03_TRF03_A_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | 15bc603f-1978-4555-a821-a5acc17821c6 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_67FT |  | 2cbf53bc-0caa-44ef-86c7-c7020f5872b9 | 20260113 | Status |  |  | SingleBit | 548 | FALSE
GTD_TRF03_TRF03_P_67F1 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E1 | 2fe298be-97fc-4189-8da0-ad2a26a99fa5 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_67F1 |  | 06731427-2ca7-4545-98c6-6251e021cf55 | 20260113 | Status |  |  | SingleBit | 466 | FALSE
GTD_TRF03_24-3_43LR |  | 43LR | 8ca8cb52-0253-460b-ab92-4944d73327f2 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom___INV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TRF03_24-3_43LR |  | 281e85ca-d904-4c21-a83e-432b0372ca70 | 20260113 | Status |  |  | SingleBit | 411 | FALSE
GTD_TRF03_TRF03_A_62BF |  | 62BF | 4b79570c-28a2-4aaf-a1cb-04be9a0bb8b9 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_62BF |  | 51b752c8-87d7-42d9-919a-5a7532fab0b1 | 20260113 | Status |  |  | SingleBit | 529 | FALSE
GTD_TRF03_TRF03_P_21Z2 |  | 21 - TRIP ZONA 2 | 4b47d1c4-6b0e-4609-9fdb-31e184739872 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_21Z2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_21Z2 |  | bb394683-35d4-4155-a4ec-938ba82ee859 | 20260113 | Status |  |  | SingleBit | 462 | FALSE
GTD_TRF03_TRF03_P_DR |  | DEFEITO RELE | 04f4d26c-c83e-470c-8aa5-7476199d3cec | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_DR |  | 23f4a619-2692-4d62-919c-136c3052ebc1 | 20260113 | Status |  |  | SingleBit | 447 | FALSE
GTD_TRF03_TRF03_A_FSIN |  | FALHA SINCRONISMO IRIG B | aa51df37-bd34-440f-8fbc-e0ef711b8261 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_FSIN |  | 17a59564-5c6b-44f6-a109-19a9938525ea | 20260113 | Status |  |  | SingleBit | 526 | FALSE
GTD_TRF03_TRF03_A_21Z3 |  | 21 - TRIP ZONA 3 | 8d33f576-9f1b-4426-a7dd-a940b45c3632 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_21Z3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_21Z3 |  | 19458a95-a78b-4a58-8f3c-b627f9b589c0 | 20260113 | Status |  |  | SingleBit | 543 | FALSE
GTD_TRF03_TRF03_P_21Z1 |  | 21 - TRIP ZONA 1 | ed0c9ee0-7044-4307-8245-83c1d9c2b741 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_21Z1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_21Z1 |  | 9018a348-3b79-41b0-b5f7-e91468ba1db3 | 20260113 | Status |  |  | SingleBit | 461 | FALSE
GTD_TRF03_TRF03_MDBT |  | DJAUX TP BARRA T | c5c27be6-fa54-4069-8f37-f8239c53e09e | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_MDBT |  | ec06f369-2eaa-450d-b282-d1cdd089490c | 20260113 | Status |  |  | SingleBit | 430 | FALSE
GTD_TRF03_TRF03_A_79_1 |  | 79 PARTIDA | 85bf669c-cbbd-43f9-bbae-3b67a905bbe1 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_79_1 |  | 9de20762-ca72-4d87-be87-63aa740b4685 | 20260113 | Status |  |  | SingleBit | 558 | FALSE
GTD_TRF03_BARRA_P_FPBR |  | FALTA POTENCIAL BARRA | a94c75be-34fc-4ab4-8eb3-4e816c0ca824 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_BARRA_P_FPBR |  | 8fc5e278-b209-40fe-aaca-2eeb6b728400 | 20260326 | Status |  |  | SingleBit | 487 | FALSE
GTD_TRF03_TRF03_A_N |  | NEUTRO | 66b700be-cc17-4752-a48a-4db84c64bb5d | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_N |  | 4560c243-c5f8-42b2-a9fc-3d92b26bdf40 | 20260113 | Status |  |  | SingleBit | 533 | FALSE
GTD_TRF03_89-20_DSEC |  | SECCIONADORA | 7a8d6b36-be87-4514-9092-832b0d3ceee6 | Status | GTD Trans | [6 empty] | GTD_TRANS_89-20_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_89-20_DSEC |  | a6a0943f-ee29-4c36-8949-cba384b9d506 | 20260113 | Status |  |  | SingleBit | 421 | FALSE
GTD_TRF03_89-22_DSEC |  | SECCIONADORA | a6e6216c-08e6-49cb-9d9e-666ba2529b48 | Status | GTD Trans | [6 empty] | IVB_TRANS_89-40_SEC |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_89-22_DSEC |  | 0ae2a40c-395f-4b43-90ca-83640f849043 | 20260113 | Status |  |  | SingleBit | 426 | FALSE
GTD_TRF03_TRF03_A_21Z2 |  | 21 - TRIP ZONA 2 | 1da6e20c-d56a-4bb5-9882-d9335b21b5cc | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_21Z2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_21Z2 |  | 4d2ab53d-97a4-4c33-bb69-e75196a02f3c | 20260113 | Status |  |  | SingleBit | 542 | FALSE
GTD_TRF03_TRF03_P_81E1 |  | 81 - TRIP SUB FREQUENCIA E1 | 092f45a2-7bb6-4b6e-bb1b-7914255de080 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_81E1 |  | 4ca076e7-d601-4e4e-aa6a-5a2c2e46db5f | 20260113 | Status |  |  | SingleBit | 474 | FALSE
GTD_TRF03_TRF03_P_67N1 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E1 | 0f3bec08-0cbf-43d1-bd8c-fc00c0d03471 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_67N1 |  | 75ae024e-d427-4f8f-9934-b0dc0a6ddd85 | 20260113 | Status |  |  | SingleBit | 469 | FALSE
GTD_TRF03_TRF03_A_25VT |  | 25 - TRIP DIFERENCA TENSAO | ef62fe36-4b32-45ba-97be-a6466b5cabab | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_25VT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_25VT |  | 56679c78-bae8-4121-8d7a-85d681c8a3b1 | 20260113 | Status |  |  | SingleBit | 564 | FALSE
GTD_TRF03_TRF03_P_79RE |  | 79 RESET | 0202abd9-c129-40fb-a142-0bb54b698255 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_79RE |  | a9b4c21c-c224-4f71-9912-caf307a5489b | 20260113 | Status |  |  | SingleBit | 481 | FALSE
GTD_TRF03_TRF03_A_67F1 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E1 | 2034818b-123c-437c-8155-298ad78f2f6f | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_67F1 |  | 995328f9-2899-474a-8548-141277839bae | 20260113 | Status |  |  | SingleBit | 546 | FALSE
GTD_TRF03_TRF03_P_21 |  | 21 - FUNCAO DISTANCIA | d3560aa5-a62d-41fc-a29a-0360802db1d8 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_21 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_21 |  | 1cb208d0-941a-4774-83f9-701ecc9ae9e2 | 20260113 | Status |  |  | SingleBit | 460 | FALSE
GTD_TRF03_TRF03_MDBP |  | DJAUX TP BARRA P | 536c42ef-b25e-4fb5-8158-e33cf3478dac | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_MDBP |  | a6f452b7-0d89-4787-854c-921385692a0a | 20260113 | Status |  |  | SingleBit | 431 | FALSE
GTD_TRF03_TRF03_A_67N2 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E2 | 7fe64e47-5993-4277-bf5f-3d3f5a4521fa | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_67N2 |  | b3bf0ddd-456f-4da2-a60a-fa0cc2b0d4de | 20260113 | Status |  |  | SingleBit | 550 | FALSE
GTD_TRF03_TRF03_P_81E2 |  | 81 - TRIP SUB FREQUENCIA E2 | 28a78113-0608-49e7-a18a-b7af334b1981 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_81E2 |  | 84d0d2d3-dd4a-454c-a654-e718e2d418cc | 20260113 | Status |  |  | SingleBit | 475 | FALSE
GTD_TRF03_TRF03_P_N |  | NEUTRO | 972e9452-6667-4c6a-a5a7-67068267d3f5 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_N |  | 7b3eeb06-253a-4229-ae31-21dafe686cc9 | 20260113 | Status |  |  | SingleBit | 453 | FALSE
GTD_TRF03_TRF03_A_GOOS |  | FALHA GOOSE | dd120ec6-bdc1-4318-974f-15bd3ff8ba65 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_GOOS |  | 5754096c-1b50-4323-abae-51a46e4c5fd9 | 20260113 | Status |  |  | SingleBit | 524 | FALSE
GTD_TRF03_TRF03_P_50N1 |  | 50 NEUTRO ESTAGIO 1 | de553350-7180-4144-a959-b8d1084f4c70 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_50N1 |  | 5a8063c9-ff35-4656-a550-5baed11f626d | 20260113 | Status |  |  | SingleBit | 457 | FALSE
GTD_TRF03_TRF03_P_25AT |  | 25 - TRIP DIFERENCA DE ANGULO | 6909a563-4aa3-4927-8a2e-c3d7e0a1b0ed | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_25AT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_25AT |  | d051d2cd-5463-4c4a-a655-fd6ea70d60ad | 20260113 | Status |  |  | SingleBit | 486 | FALSE
GTD_TRF03_TRF03_P_FB |  | FASE B | 665d8bbc-9542-4ca6-8364-7fd2785e929e | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_FB |  | 558cdba7-d512-4fe5-9d89-a51114e20b61 | 20260113 | Status |  |  | SingleBit | 451 | FALSE
GTD_TRF03_TRF03_A_27_T |  | 27 - TRIP SUBTENSAO | b276df47-fb34-4122-8719-4a443567fa04 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | Unknown | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_27_T |  | cf5facad-efe1-474d-af32-27c68147a2a7 | 20260113 | Status |  |  | SingleBit | 552 | FALSE
GTD_TRF03_TRF03_A_67F2 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E2 | 98de4bf5-0751-4dd6-ae5e-25882f16d32b | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_A_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_A_67F2 |  | 5480af56-2efc-4d63-9be7-c65cb9400c38 | 20260113 | Status |  |  | SingleBit | 547 | FALSE
GTD_TRF03_TRF03_P_25FT |  | 25 - TRIP DIFERENCA FREQUENCIA | 9b9ed500-9b4e-4629-b392-dfd6ec724fd5 | Status | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_P_PROT_25FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_P_25FT |  | 5d8032ed-6b1a-439b-8c11-9733ea44d8e0 | 20260113 | Status |  |  | SingleBit | 485 | FALSE
GTD_TRF03_24-3_DJF1 |  | DISJUNTOR NF | fc6c5fb6-cf9a-42c1-9396-f388bd19e5e8 | SwitchStatus | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 1 |  | UTR_GTD_1 | GTD_TRF03_24-3_DJF1 |  | 89f7c9bd-00d9-476f-b564-45057acd859b | 20260113 | Status | 30 | AutoSelectWithValue | MultiCoord | 405;406 | FALSE | FALSE | 15 | SingleCoord | 400;400 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TRF03_TRF03_25 |  | 25 RELE SINCRONISMO | b0dabbe6-4ec7-4f0b-9ce8-f82a0410f26d | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_25 |  | c009d487-02ac-41a7-aafe-602be7270d00 | 20260113 | Status | 30 | AutoSelectWithValue | SingleBit | 482 | FALSE | FALSE | 15 | SingleCoord | 404;404 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TRF03_TRF03_79 |  | 79 - RELIGAMENTO | 4a48bb0e-3e7b-4d2f-918d-1a58a6039619 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_TRF03_TRF03_79 |  | b7ecda3d-fdf6-41b7-976e-dfd2fa91b489 | 20260113 | Status | 30 | AutoSelectWithValue | SingleBit | 477 | FALSE | FALSE | 15 | SingleCoord | 403;403 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TRF03_89-20_SECF |  | SECCIONADORA FONTE | bce41d3d-08d5-4a0e-b702-3d27944c120d | SwitchStatus | GTD Trans | [6 empty] | GTD_TRANS_89-20_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 2 |  | UTR_GTD_1 | GTD_TRF03_89-20_SECF |  | c2e9edbe-2499-49a4-8b40-20d243cfc295 | 20260113 | Status | 30 | AutoSelectWithValue | MultiCoord | 418;419 | FALSE | FALSE | 15 | SingleCoord | 401;401 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_TRF03_89-22_SECF |  | SECCIONADORA FONTE | 1111f783-fd6a-4ed9-b10e-ef2c3e1e7264 | SwitchStatus | GTD Trans | [6 empty] | IVB_TRANS_89-40_SEC |  | SwitchStatus | ABC | None | ReadWrite |  | ABRIR@FECHAR___ABERTO@FECHADO___SwitchStatus_D_TC_SO | 2 |  | UTR_GTD_1 | GTD_TRF03_89-22_SECF |  | 25da5e9d-a23c-4274-8401-28a5681bef1e | 20260113 | Status | 30 | AutoSelectWithValue | MultiCoord | 423;424 | FALSE | FALSE | 15 | SingleCoord | 402;402 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_AL11_52-11_TRIP |  | TRIP EXTERNO | GTD_AL11_52-11_TRIP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_TRIP |  | GTD_AL11_52-11_TRIP_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1557 | FALSE
GTD_AL11_52-11_MOLA |  | MOLA | GTD_AL11_52-11_MOLA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_MOLA |  | GTD_AL11_52-11_MOLA_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1503 | FALSE
GTD_AL11_52-11_TOED |  | TEMPERATURA OLEO ENROLAMENTO TRIP | GTD_AL11_52-11_TOED_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_TOED |  | GTD_AL11_52-11_TOED_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1556 | FALSE
GTD_AL11_52-11_FSIN |  | FALHA SINCRONISMO IRIG-B | GTD_AL11_52-11_FSIN_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_FSIN |  | GTD_AL11_52-11_FSIN_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1518 | FALSE
GTD_AL11_52-11_81E3 |  | 81 ESTAGIO 3 | GTD_AL11_52-11_81E3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_81E3 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_81E3 |  | GTD_AL11_52-11_81E3_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1546 | FALSE
GTD_AL11_52-11_81E5 |  | 81 ESTAGIO 5 | GTD_AL11_52-11_81E5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_81E5 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_81E5 |  | GTD_AL11_52-11_81E5_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1548 | FALSE
GTD_AL11_52-11_CCMO |  | VCC MOT | GTD_AL11_52-11_CCMO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_CCMO |  | GTD_AL11_52-11_CCMO_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1506 | FALSE
GTD_TRF1_24-1_50EF |  | 50EF - END FAULT | 56cc3df3-2936-431a-8cdb-329e5ad229f7 | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_50EF |  | 79c18ce7-76cc-4f5f-804a-53d4fbc06af1 | 20260327 | Status |  |  | SingleBit | 3239 | FALSE
GTD_AL11_52-11_81E1 |  | 81 ESTAGIO 1 | GTD_AL11_52-11_81E1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_81E1 |  | GTD_AL11_52-11_81E1_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1544 | FALSE
GTD_AL11_52-11_79RE |  | 79 RESET | GTD_AL11_52-11_79RE_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_79RE |  | GTD_AL11_52-11_79RE_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1553 | FALSE
GTD_AL11_52-11_79LO |  | 79 BLOQUEADO | GTD_AL11_52-11_79LO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_79LO |  | GTD_AL11_52-11_79LO_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1552 | FALSE
GTD_AL11_52-11_FB |  | FASE B | GTD_AL11_52-11_FB_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_FB |  | GTD_AL11_52-11_FB_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1524 | FALSE
GTD_AL11_52-11_DR |  | RELE | GTD_AL11_52-11_DR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_DR |  | GTD_AL11_52-11_DR_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1520 | FALSE
GTD_AL11_52-11_BBA1 |  | BOB AB 1 | GTD_AL11_52-11_BBA1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_BBA1 |  | GTD_AL11_52-11_BBA1_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1509 | FALSE
GTD_AL11_52-11_51N1 |  | 51N 1 | GTD_AL11_52-11_51N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_51N1 |  | GTD_AL11_52-11_51N1_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1533 | FALSE
GTD_AL11_52-11_51F |  | 51F | GTD_AL11_52-11_51F_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_51F |  | GTD_AL11_52-11_51F_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1529 | FALSE
GTD_AL11_52-11_81E2 |  | 81 ESTAGIO 2 | GTD_AL11_52-11_81E2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_81E2 |  | GTD_AL11_52-11_81E2_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1545 | FALSE
GTD_AL11_52-11_50F2 |  | 50F 2 | GTD_AL11_52-11_50F2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_50F2 |  | GTD_AL11_52-11_50F2_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1528 | FALSE
GTD_AL11_52-11_50F1 |  | 50F 1 | GTD_AL11_52-11_50F1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_50F1 |  | GTD_AL11_52-11_50F1_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1527 | FALSE
GTD_AL11_52-11_43LR |  | 43LR | GTD_AL11_52-11_43LR_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_43LR |  | GTD_AL11_52-11_43LR_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1504 | FALSE
GTD_AL11_52-11_46 |  | 46 | GTD_AL11_52-11_46_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_46 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_46 |  | GTD_AL11_52-11_46_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1536 | FALSE
GTD_AL11_52-11_43TC |  | 43TC | GTD_AL11_52-11_43TC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_43TC |  | GTD_AL11_52-11_43TC_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1515 | FALSE
GTD_AL11_52-11_62BF |  | 62BF | GTD_AL11_52-11_62BF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_62BF |  | GTD_AL11_52-11_62BF_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1522 | FALSE
GTD_AL11_52-11_BBFC |  | BOB FEC | GTD_AL11_52-11_BBFC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_BBFC |  | GTD_AL11_52-11_BBFC_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1508 | FALSE
GTD_AL11_52-11_50N1 |  | 50N 1 | GTD_AL11_52-11_50N1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_50N1 |  | GTD_AL11_52-11_50N1_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1531 | FALSE
GTD_AL11_52-11_GOOS |  | FALHA GOOSE | GTD_AL11_52-11_GOOS_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_GOOS |  | GTD_AL11_52-11_GOOS_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1516 | FALSE
GTD_AL11_52-11_FC |  | FASE C | GTD_AL11_52-11_FC_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_FC |  | GTD_AL11_52-11_FC_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1525 | FALSE
GTD_AL11_52-11_FA |  | FASE A | GTD_AL11_52-11_FA_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_FA |  | GTD_AL11_52-11_FA_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1523 | FALSE
GTD_AL11_52-11_CCCO |  | VCC CMD | GTD_AL11_52-11_CCCO_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_CCCO |  | GTD_AL11_52-11_CCCO_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1507 | FALSE
GTD_AL11_52-11_BBA2 |  | BOB AB 2 | GTD_AL11_52-11_BBA2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_BBA2 |  | GTD_AL11_52-11_BBA2_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1510 | FALSE
GTD_AL11_52-11_79OK |  | 79 OK | GTD_AL11_52-11_79OK_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_79OK |  | GTD_AL11_52-11_79OK_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1551 | FALSE
GTD_AL11_52-11_SGFT |  | SGF_TRIP | GTD_AL11_52-11_SGFT_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_SGFT |  | GTD_AL11_52-11_SGFT_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1535 | FALSE
GTD_AL11_52-11_50N2 |  | 50N 2 | GTD_AL11_52-11_50N2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_50N2 |  | GTD_AL11_52-11_50N2_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1532 | FALSE
GTD_AL11_52-11_79_1 |  | 79 LIGA | GTD_AL11_52-11_79_1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_79_1 |  | GTD_AL11_52-11_79_1_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1550 | FALSE
GTD_BP2_BP2_GOOS |  | FALHA GOOSE | de279d68-8f64-4bf2-bdc8-ab239bfcb4d8 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BP2_BP2_GOOS |  | fc3a269d-e5dd-4694-880f-aea6c9c20a8e | 20260327 | Status |  |  | SingleBit | 3301 | FALSE
GTD_AL11_52-11_FCOM |  | COMUNIC | GTD_AL11_52-11_FCOM_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_FCOM |  | GTD_AL11_52-11_FCOM_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1521 | FALSE
GTD_AL11_52-11_FUTP |  | FALHA CIRCUITO TP | GTD_AL11_52-11_FUTP_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_FUTP |  | GTD_AL11_52-11_FUTP_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1554 | FALSE
GTD_IB_52-18_BP2_50EF |  | 50EF - END FAULT | 5e8a81af-eb22-4b65-9658-621cd9168244 | Status | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_BP2_50EF |  | 9d4d5962-0eed-41d6-8093-4395b9aea7c9 | 20260327 | Status |  |  | SingleBit | 3342 | FALSE
GTD_AL11_52-11_81E4 |  | 81 ESTAGIO 4 | GTD_AL11_52-11_81E4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_81E4 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_81E4 |  | GTD_AL11_52-11_81E4_UTR_GTD_1 | 20260310 | Status |  |  | SingleBit | 1547 | FALSE
GTD_AL11_52-11_SGF |  | SGF | GTD_AL11_52-11_SGF_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_SGF |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL11_52-11_SGF |  | GTD_AL11_52-11_SGF_UTR_GTD_1 | 20260310 | Status | 30 | DirectOperate | SingleBit | 1534 | FALSE | FALSE | 15 | SingleCoord | 1502;1502 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL11_52-11_DJF1 |  | DJ | GTD_AL11_52-11_DJF1_UTR_GTD_1_SwitchStatus | SwitchStatus | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_GTD_1 | GTD_AL11_52-11_DJF1 |  | GTD_AL11_52-11_DJF1_UTR_GTD_1 | 20260310 | Status | 30 | DirectOperate | MultiCoord | 1500;1501 | FALSE | FALSE | 15 | SingleCoord | 1500;1500 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_AL11_52-11_79 |  | 79 | GTD_AL11_52-11_79_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL11_52-11_79 |  | GTD_AL11_52-11_79_UTR_GTD_1 | 20260310 | Status | 30 | DirectOperate | SingleBit | 1549 | FALSE | FALSE | 15 | SingleCoord | 1509;1509 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL11_52-11_81 |  | 81 | GTD_AL11_52-11_81_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL11_52-11_81 |  | GTD_AL11_52-11_81_UTR_GTD_1 | 20260310 | Status | 30 | DirectOperate | SingleBit | 1537 | FALSE | FALSE | 15 | SingleCoord | 1503;1503 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL11_52-11_2649 |  | 26 49 - FUNCAO TEMPERATURA | GTD_AL11_52-11_2649_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_2649 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL11_52-11_2649 |  | GTD_AL11_52-11_2649_UTR_GTD_1 | 20260310 | Status | 30 | DirectOperate | SingleBit | 1555 | FALSE | FALSE | 5 | SingleCoord | 1510;1510 | TripPulseOn;ClosePulseOn | 0.25;0.25
GTD_AL11_52-11_81U1 |  | AJUSTE PARA 81 ESTAGIO 1 | GTD_AL11_52-11_81U1_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_81U1 |  | GTD_AL11_52-11_81U1_UTR_GTD_1 | 20260310 | Status | 30 | DirectOperate | SingleBit | 1539 | FALSE | FALSE | 5 | SingleCoord | 1504 | ClosePulseOn | 0.25
GTD_AL11_52-11_81U2 |  | AJUSTE PARA 81 ESTAGIO 2 | GTD_AL11_52-11_81U2_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_81U2 |  | GTD_AL11_52-11_81U2_UTR_GTD_1 | 20260310 | Status | 30 | DirectOperate | SingleBit | 1540 | FALSE | FALSE | 5 | SingleCoord | 1505 | ClosePulseOn | 0.25
GTD_AL11_52-11_51N |  | 51N | GTD_AL11_52-11_51N_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_AL11_52-11_51N |  | GTD_AL11_52-11_51N_UTR_GTD_1 | 20260310 | Status | 30 | DirectOperate | SingleBit | 1530 | FALSE | FALSE | 15 | SingleCoord | 1501;1501 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_AL11_52-11_81U3 |  | AJUSTE PARA 81 ESTAGIO 3 | GTD_AL11_52-11_81U3_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_81U3 |  | GTD_AL11_52-11_81U3_UTR_GTD_1 | 20260310 | Status | 30 | DirectOperate | SingleBit | 1541 | FALSE | FALSE | 5 | SingleCoord | 1506 | ClosePulseOn | 0.25
GTD_AL11_52-11_81U5 |  | AJUSTE PARA 81 ESTAGIO 5 | GTD_AL11_52-11_81U5_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_81U5 |  | GTD_AL11_52-11_81U5_UTR_GTD_1 | 20260310 | Status | 30 | DirectOperate | SingleBit | 1543 | FALSE | FALSE | 5 | SingleCoord | 1508 | ClosePulseOn | 0.25
GTD_AL11_52-11_81U4 |  | AJUSTE PARA 81 ESTAGIO 4 | GTD_AL11_52-11_81U4_UTR_GTD_1_Status | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_81U4 |  | GTD_AL11_52-11_81U4_UTR_GTD_1 | 20260310 | Status | 30 | DirectOperate | SingleBit | 1542 | FALSE | FALSE | 5 | SingleCoord | 1507 | ClosePulseOn | 0.25
GTD_TRF2_24-2_50EF |  | 50EF - END FAULT | b2ecc5fa-617f-4ea2-8a4d-53f7a3ff5918 | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_50EF |  | e045c7f8-4ea8-4361-90fe-68a5dd988c98 | 20260327 | Status |  |  | SingleBit | 3339 | FALSE
GTD_TRF1_24-1_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | 13ddbb66-c215-4256-b21e-6e9a9089cb4d | Status | GTD Distr | [6 empty] | GTD-TRF1_24-1_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_67FT |  | 60038664-58a7-4813-8079-be2ef8f827cd | 20262602 | Status |  |  | SingleBit | 2066 | FALSE
GTD_TRF2_24-2_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | 386edd40-02e1-4fb1-88cc-b08e9e6e2e9c | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_67NT |  | 658d332f-b068-4a2c-bb88-ae969d3d31ee |  | Status |  |  | SingleBit | 2969 | FALSE
GTD_TRF2_24-2_67N1 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E1 | 3859a768-cb14-4f82-a235-f54b908daf19 | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_67N1 |  | 46a2eed7-b5a9-42b5-a3bf-bb546b6dbab4 |  | Status |  |  | SingleBit | 2967 | FALSE
GTD_AL21_52-21_67 |  | 67 | b300b0d9-7712-4929-b45a-11a936435a19 | Status | GTD Distr | [6 empty] | GTD_AL21_AL21_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_AL21_52-21_67 |  | 1449aa55-4a83-493f-8b7b-afc9b183b5c1 | 20220606 | Status |  |  | SingleBit | 2460 | FALSE
GTD_TRF1_24-1_PROT_27E1 |  | 27 - SUBTENSAO E1 | aa5778ea-fa9a-426a-acb4-2604965397a5 | Status | GTD Distr | [6 empty] | GTD-TRF1_24-1_PROT_27E1 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_PROT_27E1 |  | 7069bef7-6dfb-49ed-9e3f-8324622c57ac |  | Status |  |  | SingleBit | 2071 | FALSE
GTD_IB_52-18_67 |  | 67 | 4be51909-0b26-4e02-bac3-06762b79b46a | Status | GTD Trans | [6 empty] | GTD_IBF1_52-160_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_IB_52-18_67 |  | bc6f3df8-fa47-497d-9d01-3aa938af0005 | 20220606 | Status |  |  | SingleBit | 2347 | FALSE
GTD_TRF2_24-2_67F1 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E1 | 16504cdf-dea9-4bf0-b324-f10f73f2fade | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_67F1 |  | f2a2c7cb-eba3-421b-9748-4902d3891a53 |  | Status |  |  | SingleBit | 2964 | FALSE
GTD_TRF2_24-2_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | e328523d-758d-4bdd-b400-0fd7a4743b89 | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_67FT |  | 58178499-103b-4992-a29a-245f6032dc6e |  | Status |  |  | SingleBit | 2966 | FALSE
GTD_TRF1_24-1_67F1 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E1 | 1ad71f5b-7a1c-4ee6-8a49-975cbeaf5e0b | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_67F1 |  | f2576e75-2ed3-46fa-94f5-b8369984933a |  | Status |  |  | SingleBit | 2064 | FALSE
GTD_TRF2_24-2_59E2 |  | 59 E2 | 519f0de7-7bc5-44c6-8ebc-b4c8a6117e18 | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_59_2 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_59E2 |  | b837249b-f68a-4d96-a99b-48e915a94bde |  | Status |  |  | SingleBit | 2975 | FALSE
GTD_TRF2_24-2_59E1 |  | 59 E1 | c9a77c81-9b50-4601-846d-1ce2a9500049 | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_59_1 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_59E1 |  | 403e4788-473d-42e1-bd46-40f5f2992480 |  | Status |  |  | SingleBit | 2974 | FALSE
GTD_AL21_52-21_67N2 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E2 | c942e1dc-b0fd-45ce-a9d9-5729d4d1cef7 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_67N2 |  | 61a739c6-9ed3-4c36-ac00-e0a2257485f9 |  | Status |  |  | SingleBit | 2465 | FALSE
GTD_AL21_52-21_67F1 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E1 | 7cc9fb93-de60-474a-a1af-a60a738840fa | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_67F1 |  | d8fe6e2f-24c1-44fa-ad16-6187316c712f |  | Status |  |  | SingleBit | 2461 | FALSE
GTD_AL21_52-21_67N1 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E1 | 35cd5a8a-774d-4362-b64e-eeb12268ead1 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_67N1 |  | ae85d907-6d21-4362-b62c-56a8126e19cc |  | Status |  |  | SingleBit | 2464 | FALSE
GTD_AL21_52-21_67F2 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E2 | 8165883b-2e59-4be1-ba6a-bb88f4355f7d | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_67F2 |  | cc2c8c4a-addc-4795-923e-2ecbd467483b |  | Status |  |  | SingleBit | 2462 | FALSE
GTD_TRF2_24-2_PROT_27E2 |  | 27 - SUBTENSAO E2 | 520f9a51-ac4c-42ac-9c06-621671768a97 | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_27E2 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_PROT_27E2 |  | 02694a14-543b-45e3-b2be-e194e7e46fb7 |  | Status |  |  | SingleBit | 2972 | FALSE
GTD_AL22_52-22_67F1 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E1 | 54f7afd9-c15b-409d-a8f6-e26238160d4f | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_67F1 |  | 7c567d74-58ce-4f08-b8c2-ed40ef46c658 |  | Status |  |  | SingleBit | 2562 | FALSE
GTD_AL22_52-22_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | ce27bba6-fa15-4e26-9947-2e0cb8079928 | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_67FT |  | 4653e110-bb7e-4b5d-a0aa-51633837e4a4 | 20262602 | Status |  |  | SingleBit | 2564 | FALSE
GTD_AL22_52-22_67N1 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E1 | d4f0f7f1-8f3e-4e88-abef-6d47cce96193 | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_67N1 |  | cd158fbd-8e5d-4b67-adfd-1609d3612e94 |  | Status |  |  | SingleBit | 2565 | FALSE
GTD_AL22_52-22_67F2 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E2 | 72fd70c9-9faa-4b7f-b845-ecea17d473df | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_67F2 |  | e7e761b1-72a0-4616-aa6c-95250cab55fd |  | Status |  |  | SingleBit | 2563 | FALSE
GTD_AL22_52-22_67N2 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E2 | 6c71f793-3bd0-4440-ab84-46943d81588d | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_67N2 |  | 31150b57-e66b-4331-a42a-c21ec1e3a4d3 |  | Status |  |  | SingleBit | 2566 | FALSE
GTD_AL23_52-23_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | cf276255-e5a1-4c4e-8e67-5dfe5b17c31f | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_67NT |  | 2d03978f-163c-4cdd-ae64-fe1db04eac46 | 20262602 | Status |  |  | SingleBit | 2666 | FALSE
GTD_AL23_52-23_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | e079657e-df13-4905-a6bc-066089aed8b1 | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_67FT |  | 705371aa-a826-42f2-8be7-4c4b4f4f24e5 | 20262602 | Status |  |  | SingleBit | 2663 | FALSE
GTD_AL23_52-23_67N1 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E1 | 27911f05-2891-4559-98e2-37a5db082700 | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_67N1 |  | 8d9d6bd1-dd85-4f18-a99b-b6817d3228b1 |  | Status |  |  | SingleBit | 2664 | FALSE
GTD_AL23_52-23_67F1 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E1 | ddf03c33-0544-427c-9eef-4ad57f82f4eb | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_67F1 |  | 767febb9-f7b1-4f24-8dff-2ef55545dcf1 |  | Status |  |  | SingleBit | 2661 | FALSE
GTD_TRF1_24-1_59E1 |  | 59 E1 | c1ef7b83-b05f-4122-861d-55b8778a424a | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_59_1 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_59E1 |  | 93b084cc-777f-47a0-9573-252677bae599 | 20241002 | Status |  |  | SingleBit | 2074 | FALSE
GTD_AL23_52-23_67 |  | 67 | 29ae52df-66d1-4d00-ae2c-f17d5621dba8 | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_AL23_52-23_67 |  | a3ab7a3a-37c9-4a17-9e6c-f9094c0072ff | 20220606 | Status |  |  | SingleBit | 2660 | FALSE
GTD_AL23_52-23_67F2 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E2 | 8520fc06-f480-4fe3-87f9-1a4124183eac | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_67F2 |  | 0f0692e4-88dd-46c8-b65a-1a0c26cc89e1 |  | Status |  |  | SingleBit | 2662 | FALSE
GTD_TRF1_24-1_67F2 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E2 | 0bbd039b-7a0b-4b33-bd88-d53f77ba8b13 | Status | GTD Distr | [6 empty] | GTD-TRF1_24-1_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_67F2 |  | 984e8409-7934-468e-a75e-a6fef32c270f |  | Status |  |  | SingleBit | 2065 | FALSE
GTD_AL24_52-24_67F1 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E1 | 52496254-2c3f-418d-9d8a-698ff0327724 | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_67F1 |  | 6c048311-b75c-47ae-bdc2-428c8997fccc |  | Status |  |  | SingleBit | 2761 | FALSE
GTD_AL24_52-24_67F2 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E2 | be84a714-01b8-4cb3-beb6-679a441e614f | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_67F2 |  | 16d6ddc4-aefa-4ef9-b005-b4e7a59d2ede |  | Status |  |  | SingleBit | 2762 | FALSE
GTD_AL24_52-24_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | 0d1f855f-b064-40ff-a475-25a1d73cd978 | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_67FT |  | d6b845fd-6ece-4708-aa53-ccc596345dd4 | 20262602 | Status |  |  | SingleBit | 2763 | FALSE
GTD_AL24_52-24_67N2 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E2 | 2b773571-c4e3-445d-b02c-03088709ddc2 | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_67N2 |  | e5d553f1-8dac-4162-a454-5f0f15a08c9c |  | Status |  |  | SingleBit | 2765 | FALSE
GTD_AL24_52-24_67 |  | 67 | 66cc7a7b-9af2-4531-b5e9-efaf8cebb00b | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_AL24_52-24_67 |  | fe2cbea0-b44f-4759-a604-ba44bfdc23f4 | 20220606 | Status |  |  | SingleBit | 2760 | FALSE
GTD_AL24_52-24_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | 9c44dd80-1fe9-4b54-aa62-5747b040e32e | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_67NT |  | 78149a2c-2859-4f73-9f2e-df493b5c4c52 | 20262602 | Status |  |  | SingleBit | 2766 | FALSE
GTD_AL24_52-24_67N1 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E1 | 1872a7af-df31-4e7a-9f33-73b221f307f1 | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL24_52-24_67N1 |  | 71e27a8a-d208-4bcd-bf67-75fcbb9ab825 |  | Status |  |  | SingleBit | 2764 | FALSE
GTD_AL25_52-25_67N2 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E2 | 5bd63fb7-364f-49a1-a992-771bb4c2bf86 | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_67N2 |  | fac1a324-a4ba-42a9-a46e-1f6f4339dede |  | Status |  |  | SingleBit | 2865 | FALSE
GTD_IB_52-18_BP1_50EF |  | 50EF - END FAULT | 86d86142-1718-4ee0-9191-ccbb789783f9 | Status | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_BP1_50EF |  | d2f1f8e5-1e16-4312-8ae4-7f6f992f4950 | 20260327 | Status |  |  | SingleBit | 3242 | FALSE
GTD_AL25_52-25_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | 64545c37-847e-402c-a52d-02553691ca57 | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_67FT |  | 07c6f68e-4256-473c-89fc-33158007ae69 | 20262602 | Status |  |  | SingleBit | 2863 | FALSE
GTD_AL23_52-23_67N2 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E2 | d43206ef-cd03-4994-a8b8-43fa41c75697 | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL23_52-23_67N2 |  | 8cf06d17-bc88-4312-9056-7cdbce3e93ea |  | Status |  |  | SingleBit | 2665 | FALSE
GTD_AL25_52-25_67 |  | 67 | 92c6ad68-3438-4c10-b006-ef9769e24b9a | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_AL25_52-25_67 |  | daa5088a-0b47-4732-a6e6-4c7a3cdb5c25 | 20220606 | Status |  |  | SingleBit | 2860 | FALSE
GTD_AL25_52-25_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | f4695c73-400a-442c-ab9d-8d68131cd95f | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_67NT |  | d6af058f-361c-4cb9-bbda-1ad9d8badec9 | 20262602 | Status |  |  | SingleBit | 2866 | FALSE
GTD_AL25_52-25_67N1 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E1 | 52fc8dd9-1405-4630-9efc-568aa636c3aa | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_67N1 |  | ba265581-c012-4e39-a79c-e4f414b918b0 |  | Status |  |  | SingleBit | 2864 | FALSE
GTD_AL25_52-25_67F2 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E2 | 35530620-8787-4551-9f8a-70896978ad8d | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_67F2 |  | 082ae78b-3d1f-44ed-bf1f-43119f939ad7 |  | Status |  |  | SingleBit | 2862 | FALSE
GTD_SE_RET1_BADC |  | BATERIA EM DESCARGA | 9929b9aa-b0df-4775-a870-6fe6fd542d48 | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_SE_RET1_BADC |  | 6cabefd5-f3ae-4b78-9fb4-8006d93a75b3 | 20260408 | Status |  |  | SingleBit | 3423 | FALSE
GTD_TRF1_24-1_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | 523a37a7-b3b7-4303-b70f-f97a7555e534 | Status | GTD Distr | [6 empty] | GTD-TRF1_24-1_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_67NT |  | f2e5364a-5482-4264-9ae8-41f8b0c2313b | 20262602 | Status |  |  | SingleBit | 2069 | FALSE
GTD_AL11_52-11_67 |  | 67 | ac0f5940-8dbb-4501-860c-e7d827ab79b5 | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_AL11_52-11_67 |  | d5d8569a-b0fb-4ae0-830f-9ab162898924 | 20220606 | Status |  |  | SingleBit | 1560 | FALSE
GTD_TRF1_24-1_59E2 |  | 59 E2 | d899cf8a-8dd7-4d42-a0b4-e121e79f8c96 | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_59_2 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_59E2 |  | 17ad04c1-57f1-4c4f-ac99-d65299265f5b | 20241002 | Status |  |  | SingleBit | 2075 | FALSE
GTD_AL11_52-11_67F1 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E1 | 2cd46e21-ec9b-4330-9eeb-57486d5b2c06 | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_67F1 |  | a0220fd8-adf5-4ae6-9486-18e6bbff2cc0 |  | Status |  |  | SingleBit | 1561 | FALSE
GTD_AL11_52-11_67N1 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E1 | acee4f60-d79c-44a4-8fc4-a2998dea5a1a | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_67N1 |  | acceafbb-d5e4-4a5c-b343-cfdd15c2478a |  | Status |  |  | SingleBit | 1564 | FALSE
GTD_AL11_52-11_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | 8c7ce85e-8dfc-416a-8530-3775228ee8de | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_67NT |  | 331d89c5-1359-4450-adfc-589a16d7c73a | 20262602 | Status |  |  | SingleBit | 1566 | FALSE
GTD_TRF1_24-1_67 |  | 67 | 41534d1b-35aa-406f-8dbd-a25bbb81334d | Status | GTD Distr | [6 empty] | GTD-TRF1_24-1_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_TRF1_24-1_67 |  | 2cf211c7-fb2a-4c85-91d2-0c35307604f1 | 20220606 | Status |  |  | SingleBit | 2063 | FALSE
GTD_AL11_52-11_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | d4dbc73b-4cd8-417f-94ac-2ff99ba93db9 | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_67FT |  | ccec5ce5-b3ea-4ec2-8506-1e32270c77c7 | 20262602 | Status |  |  | SingleBit | 1563 | FALSE
GTD_AL12_52-12_67F1 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E1 | 265f333a-e2b3-47d8-9073-2ef59a3dbb35 | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_67F1 |  | eebf01bf-1166-4a72-8219-083db72d616d |  | Status |  |  | SingleBit | 1661 | FALSE
GTD_AL12_52-12_67 |  | 67 | 349fb863-9009-4783-bd17-fb3d255e9a0b | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_AL12_52-12_67 |  | fd8ffe93-cb7f-40c8-8144-ab6e25f2947c | 20220606 | Status |  |  | SingleBit | 1660 | FALSE
GTD_AL12_52-12_67F2 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E2 | cbab8bc3-1ec3-4955-9189-ea8b7a621846 | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_67F2 |  | 892ac150-add5-4f30-b3b2-73b4d8f564e1 |  | Status |  |  | SingleBit | 1662 | FALSE
GTD_AL12_52-12_67N1 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E1 | ccc36622-91ef-4700-91bb-eb992c2bdbba | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_67N1 |  | 982d7986-8561-4491-966f-a903666fc229 |  | Status |  |  | SingleBit | 1664 | FALSE
GTD_AL12_52-12_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | c82a7409-8e1a-40e9-af11-01a8d482d82e | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_67FT |  | 5a470ee6-277c-4982-8ff9-dba9d1e09809 | 20262602 | Status |  |  | SingleBit | 1663 | FALSE
GTD_AL11_52-11_67F2 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E2 | 4452cf43-8630-4ae7-a753-41a56d699f10 | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_67F2 |  | 7507357a-51be-4dc7-ac0b-24994ed33d35 |  | Status |  |  | SingleBit | 1562 | FALSE
GTD_AL13_52-13_67N1 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E1 | 8599c85d-b68b-407f-9c15-ef81dc862aa9 | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_67N1 |  | 331e7bc5-859d-4547-9261-3d6ca2da7069 |  | Status |  |  | SingleBit | 1764 | FALSE
GTD_AL13_52-13_67N2 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E2 | b004286b-ef7a-41d7-9d5c-da662fb28f37 | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_67N2 |  | 2f94b5cb-7bcc-42ef-b185-76f9dda97096 |  | Status |  |  | SingleBit | 1765 | FALSE
GTD_AL13_52-13_67 |  | 67 | 228607b7-faec-4fb8-a0cb-90cd3b0a9700 | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_AL13_52-13_67 |  | 89d6f3e6-f660-4f49-a544-7902f73bf3aa | 20220606 | Status |  |  | SingleBit | 1760 | FALSE
GTD_AL13_52-13_67F2 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E2 | 24d34367-e70d-4b3b-9ff2-718958824a4b | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_67F2 |  | f0cd27de-b17a-4586-9487-e7642c7e92f7 |  | Status |  |  | SingleBit | 1762 | FALSE
GTD_AL25_52-25_67F1 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E1 | 3d1162d7-53f5-4648-98a3-45ae18118b7e | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL25_52-25_67F1 |  | f8b0f8d1-4353-4cda-8440-e593f854b621 |  | Status |  |  | SingleBit | 2861 | FALSE
GTD_AL13_52-13_67F1 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E1 | 4991b7b6-4803-4516-984c-4e769f741df9 | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_67F1 |  | 428fcbd0-e689-4c89-9e79-7d0dbb55ac67 |  | Status |  |  | SingleBit | 1761 | FALSE
GTD_AL13_52-13_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | 9215fb23-aa3c-4324-8850-4dcbb0e1fb0a | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_67FT |  | 54a0ebf9-77d4-41bc-9366-1dd1cd62d51d | 20262602 | Status |  |  | SingleBit | 1763 | FALSE
GTD_AL14_52-14_67N1 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E1 | 5e1932d1-1782-4390-9bca-9f14600b32be | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_67N1 |  | 7440de87-b62a-4a18-9c72-f58a63e80bfa |  | Status |  |  | SingleBit | 1864 | FALSE
GTD_AL14_52-14_67N2 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E2 | c3d00261-3231-4781-9545-eb12b2bb983d | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_67N2 |  | b8c44b27-51ad-4c3f-a193-2db29bfa1f93 |  | Status |  |  | SingleBit | 1865 | FALSE
GTD_BP2_BP2_FSIN |  | FALHA SINCRONISMO IRIG B | fde2e97d-ae42-4c68-8442-a64ce272e194 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BP2_BP2_FSIN |  | 76447fa8-4ada-451e-9585-5d01ad49a271 | 20260327 | Status |  |  | SingleBit | 3303 | FALSE
GTD_AL14_52-14_67 |  | 67 | 970e5344-6131-4347-87e7-049a00339265 | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_AL14_52-14_67 |  | 2ae65429-b438-4842-a6ae-1fc35b0fdc34 | 20220606 | Status |  |  | SingleBit | 1860 | FALSE
GTD_AL14_52-14_67F2 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E2 | 75b6c662-95e2-4a5f-931f-3a0d1b333e7a | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_67F2 |  | 223ef893-41bc-4456-90c0-513108e5fd14 |  | Status |  |  | SingleBit | 1862 | FALSE
GTD_AL14_52-14_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | 47b8a4b1-c1c3-46ee-aa37-89ca1300f33d | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_67NT |  | 09c139c6-f985-4dd9-924a-2c006b01db75 | 20262602 | Status |  |  | SingleBit | 1866 | FALSE
GTD_AL14_52-14_67F1 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E1 | 6d16bc70-f904-4e6d-b6ce-bdb770d430fe | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_67F1 |  | 9d0d5e84-6da7-42c2-a475-d5913e90364c |  | Status |  |  | SingleBit | 1861 | FALSE
GTD_AL14_52-14_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | 83f74f33-78c2-4f20-9321-87bdb2657cb8 | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL14_52-14_67FT |  | 46b8e2d9-d693-477b-aee4-819d3906d666 | 20262602 | Status |  |  | SingleBit | 1863 | FALSE
GTD_SE_RET1_CAAL |  | VCA ALARME | ce4cf908-9210-40cc-a3d0-0342c0d5ddb4 | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_SE_RET1_CAAL |  | a06c1fde-4a5f-4ceb-a276-8752fd0e34f3 | 20260407 | Status |  |  | SingleBit | 3419 | FALSE
GTD_AL13_52-13_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | 205c4068-3c47-4f01-a3f0-9176ffe0f739 | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL13_52-13_67NT |  | 65685c83-e8e9-4e1c-ba6d-5df595cd56fe | 20262602 | Status |  |  | SingleBit | 1766 | FALSE
GTD_AL15_52-15_67N1 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E1 | 52bb883c-f242-40d4-824b-780dc1a2ab8f | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_67N1 |  | f55cd660-8189-466c-a00d-315da12cc6a1 |  | Status |  |  | SingleBit | 1964 | FALSE
GTD_AL15_52-15_67N2 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E2 | 3ce0ac20-f531-4c41-93cf-1dd2bb0c447d | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_67N2 |  | 7f745213-4903-4951-8c98-4d01718915cd |  | Status |  |  | SingleBit | 1965 | FALSE
GTD_AL15_52-15_67F2 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E2 | 032dbf79-7f1d-4a05-8cb1-ab8797a4e389 | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_67F2 |  | 56f6bfd3-abfe-441f-bc3c-046875ebe89a |  | Status |  |  | SingleBit | 1962 | FALSE
GTD_AL15_52-15_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | 6375624d-51ee-44f2-ac63-d3f9f45ec408 | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_67FT |  | 3251d1e0-e263-4ff3-aee7-0bfea10934bf | 20262602 | Status |  |  | SingleBit | 1963 | FALSE
GTD_AL15_52-15_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | 065e3693-275f-423b-a3cf-3db4de4d7e25 | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_67NT |  | 31d3b65a-0a8b-472b-81f4-de4a23810fde | 20262602 | Status |  |  | SingleBit | 1966 | FALSE
GTD_SE_RET2_CAAL |  | VCA ALARME | 03415843-c2f2-40d8-8d96-bec4c88179d6 | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_SE_RET2_CAAL |  | a9cb2805-c209-4e2a-b29f-c2da53226aad | 20260407 | Status |  |  | SingleBit | 3424 | FALSE
GTD_TRF1_24-1_67N2 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E2 | ccbc6978-a6ad-4e6f-834a-f1f56800de8d | Status | GTD Distr | [6 empty] | GTD-TRF1_24-1_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_67N2 |  | 88d184d4-e7b1-4cf3-baf3-a874d62f6d5d |  | Status |  |  | SingleBit | 2068 | FALSE
GTD_AL15_52-15_67F1 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E1 | f64ab5e1-2f19-45c2-94f0-b94ae3e0f49d | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_67F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL15_52-15_67F1 |  | 7cf71ef9-09c4-44cf-8b6f-d0f1c15e05e0 |  | Status |  |  | SingleBit | 1961 | FALSE
GTD_TRF1_24-1_67N1 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E1 | 6e4eace7-23e1-4520-bbfe-30c856951303 | Status | GTD Distr | [6 empty] | GTD-TRF1_24-1_PROT_67N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_67N1 |  | ac4145d4-31c5-4e02-9bd8-c8dfb5a56a39 |  | Status |  |  | SingleBit | 2067 | FALSE
GTD_TRF2_24-2_67 |  | 67 | 4de1d134-b9f4-4987-8b0d-a60b9643fd93 | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_TRF2_24-2_67 |  | 94fdb677-be1c-4231-9228-aaee2caf7df2 |  | Status |  |  | SingleBit | 2963 | FALSE
GTD_AL15_52-15_67 |  | 67 | 7322959e-0a6f-4b9b-a2e0-3e873cedc21a | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_AL15_52-15_67 |  | 6c2c5fdc-57e2-4d25-bc3c-1a53f1736a06 | 20220606 | Status |  |  | SingleBit | 1960 | FALSE
GTD_AL12_52-12_67N2 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E2 | 7e7d5689-b06c-4f1f-b521-0070a34e10f2 | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_67N2 |  | 545556fd-f3ff-4315-94e6-8b4272ad285f |  | Status |  |  | SingleBit | 1665 | FALSE
GTD_BP1_BP1_87_FC |  | FASE C | 80268677-0c79-492d-9b7d-b4030ae01430 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_P_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BP1_BP1_87_FC |  | 5c03616e-c01e-4e36-b5c4-cee0a674a23e | 20260402 | Status |  |  | SingleBit | 3221 | FALSE
GTD_TRF1_24-1_PROT_27E2 |  | 27 - SUBTENSAO E2 | 90c661d6-a560-4772-a487-7a8cdb96a13b | Status | GTD Distr | [6 empty] | GTD-TRF1_24-1_PROT_27E2 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_PROT_27E2 |  | d1b61912-dc2d-4e65-a70c-8b5adeaf2062 |  | Status |  |  | SingleBit | 2072 | FALSE
GTD_AL22_52-22_67 |  | 67 | a3685178-d6c8-4ad8-954a-e643c88ed859 | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_67 |  | Enabled | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_AL22_52-22_67 |  | d1c77d2c-dda9-4bab-81b0-8eec5d5562f3 | 20220606 | Status |  |  | SingleBit | 2561 | FALSE
GTD_AL12_52-12_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | 3b43d046-7a2b-4309-ad86-c0e6a8110f42 | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL12_52-12_67NT |  | a3554c33-4aa4-4fd1-8b8b-e2e5c8c0f5da | 20262602 | Status |  |  | SingleBit | 1666 | FALSE
GTD_AL22_52-22_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | 7c8a455f-7d70-4964-a07c-7b17dbff6dbd | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL22_52-22_67NT |  | 3de44204-a8c5-4c74-ab2b-ebffc8f10f31 | 20262602 | Status |  |  | SingleBit | 2567 | FALSE
GTD_AL11_52-11_67N2 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E2 | be31d105-b9df-4396-9501-ebda7c42e41b | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL11_52-11_67N2 |  | b09545cc-496c-450c-ba9a-bf9cdf9a1928 |  | Status |  |  | SingleBit | 1565 | FALSE
GTD_AL21_52-21_81BLOQ |  | 81 BLOQUEIO DINAMICO | f700af1b-cc18-45db-ac93-58ba83d8ee63 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | Read |  | null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_AL21_52-21_81BLOQ |  | 86c01df5-a12e-4baf-9ab2-81c50fa24cc3 | 20260204 | Status |  |  | SingleBit | 2438 | FALSE
GTD_AL21_52-21_67FT |  | 67 - DIRECIONAL SOBRECORRENTE FASE TEMPORIZADO | 83c1f141-f6a7-4f3a-9e2f-d4fb2a087b5d | Status | GTD Distr | [6 empty] | CZA_LTETB_LTETB_A_PROT_67FT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_67FT |  | 4f6b541b-7d9e-4a98-8141-49918752c578 | 20262602 | Status |  |  | SingleBit | 2463 | FALSE
GTD_AL21_52-21_67NT |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO TEMPORIZADO | 62c3c49f-712f-4bac-bdaf-13d3b91a5db0 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_PROT_67NT |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_AL21_52-21_67NT |  | 145883f6-437d-4549-8cbb-a62b7e72cb89 | 20262602 | Status |  |  | SingleBit | 2466 | FALSE
GTD_TRF2_24-2_67F2 |  | 67 - DIRECIONAL SOBRECORRENTE FASE E2 | 24ca0f19-0514-4017-8d59-e37280eb68e8 | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_67F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-1_67F2 |  | df0aee8e-2326-4771-886a-ba2efe6bad63 |  | Status |  |  | SingleBit | 2965 | FALSE
GTD_TRF2_24-2_67N2 |  | 67 - DIRECIONAL SOBRECORRENTE NEUTRO E2 | a5990ddc-cf43-42b5-93a6-0fced7ff2556 | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_67N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_67N2 |  | fe7e8dc4-0320-4087-be58-d88314f062b9 |  | Status |  |  | SingleBit | 2968 | FALSE
GTD_TRF2_24-2_PROT_27E1 |  | 27 - SUBTENSAO E1 | e46a3bd2-6e4c-41ec-8875-dc047ac32554 | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_27E1 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_PROT_27E1 |  | f37cc265-7cca-485e-9eb0-751fabdd8e18 |  | Status |  |  | SingleBit | 2971 | FALSE
GTD_SE_RET2_BADC |  | BATERIA EM DESCARGA | 766c869c-6187-4d51-a6e7-104a163bf876 | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_SE_RET2_BADC |  | f67aa22e-34e1-4f4c-aacd-33d0ba11f6bf | 20260408 | Status |  |  | SingleBit | 3428 | FALSE
GTD_TRF2_24-2_27 |  | 27 FUNCAO | 356f5b12-f086-4614-acf8-7e779709c917 | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_27 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_TRF2_24-2_27 |  | 90902b48-3323-451b-b5f2-0df1403335d4 | 20262602 | Status | 30 | DirectOperate | SingleBit | 2970 | FALSE | FALSE | 15 | SingleCoord | 2915;2915 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TSA_TSA_DR |  | DEFEITO RELE | 5acbb565-b2fe-4ed9-80d0-751f1e60613b | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_TSA_TSA_DR |  | b97e5912-078b-4715-b8dc-a922289a477d | 20260408 | Status |  |  | SingleBit | 3415 | FALSE
GTD_TSA2_TSA2_CAFL |  | FALTA VCA | 5f837430-1ed7-4a66-b66a-08c83d04285f | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TSA2_TSA2_CAFL |  | 21bc1561-9045-4596-8937-915874cd9aa6 | 20260408 | Status |  |  | SingleBit | 3401 | FALSE
GTD_TRF1_24-1_59 |  | 59 - FUNCAO SOBRETENSAO | 950d8f02-16b1-49c6-8381-19f20abc1547 | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_59 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_59 |  | e87bf78f-884c-4f02-ad0d-352f9a6122f6 |  | Status | 30 | DirectOperate | SingleBit | 2073 | FALSE | FALSE | 5 | SingleCoord | 2016;2016 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TRF03_TRF03_AJG1 |  | AJUSTE PARA GRUPO 1 | 992d835a-745e-4524-b7f2-c26aa7f92a91 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_AJG1 |  | 62533ce9-1d6c-4040-b180-2ca2e5159b41 |  | Status | 30 | DirectOperate | SingleBit | 440 | FALSE | FALSE | 5 | SingleCoord | 405 | ClosePulseOn | 0
GTD_AL21_52-21_AJG2 |  | AJUSTE PARA GRUPO 2 | 63cfe41c-85eb-4259-9d32-d0644d0b4da7 | Status | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 2 |  | UTR_GTD_1 | GTD_AL21_52-21_AJG2 |  | 400c1f2e-9925-497e-a0c0-c1b186ec8a46 |  | Status | 30 | DirectOperate | SingleBit | 2459 | FALSE | FALSE | 5 | SingleCoord | 2411;2411 | TripPulseOn;ClosePulseOn | 0;0
GTD_TRF03_TRF03_AJG2 |  | AJUSTE PARA GRUPO 2 | 0a78ca94-4357-4a0a-83a7-ccd6a6ab044e | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_AJG2 |  | f5630d9c-430e-470a-9811-6d0be6c9f528 |  | Status | 30 | DirectOperate | SingleBit | 441 | FALSE | FALSE | 5 | SingleCoord | 406 | ClosePulseOn | 0
GTD_TRF03_TRF03_AJG4 |  | AJUSTE PARA GRUPO 4 | a05a1af6-fec3-421a-b1ba-ad38fade660c | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_AJG4 |  | a3f86a73-7a21-4e45-aea4-bd2fbea7152b |  | Status | 30 | DirectOperate | SingleBit | 443 | FALSE | FALSE | 5 | SingleCoord | 408 | ClosePulseOn | 0
GTD_AL15_52-15_AJG2 |  | AJUSTE PARA GRUPO 2 | 666c6518-1a54-43df-bf5d-c05278b20228 | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 2 |  | UTR_GTD_1 | GTD_AL15_52-15_AJG2 |  | 2bf2d142-9a1a-4edd-8484-595372c39cd5 |  | Status | 30 | DirectOperate | SingleBit | 1959 | FALSE | FALSE | 5 | SingleCoord | 1911;1911 | TripPulseOn;ClosePulseOn | 0;0
GTD_TRF2_24-2_AJG4 |  | AJUSTE PARA GRUPO 4 | 2b387216-9d97-487c-93e3-137073419c6e | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_AJG4 |  | db669fc2-c4f6-4f6b-8cfb-ef9ff92e761a | 20260401 | Status | 30 | DirectOperate | SingleBit | 2962 | FALSE | FALSE | 5 | SingleCoord | 2914 | ClosePulseOn | 0
GTD_TRF03_TRF03_AJG3 |  | AJUSTE PARA GRUPO 3 | 33f8798b-b60f-4d0b-a6f8-c313496b2c39 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF03_TRF03_AJG3 |  | d44b4521-bd3d-4763-b68b-f1395b3784ef |  | Status | 30 | DirectOperate | SingleBit | 442 | FALSE | FALSE | 5 | SingleCoord | 407 | ClosePulseOn | 0
GTD_AL25_52-25_AJG2 |  | AJUSTE PARA GRUPO 2 | f4938733-11c6-4726-ad0c-5257d3d1710e | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 2 |  | UTR_GTD_1 | GTD_AL25_52-25_AJG2 |  | c7abf7ba-00ef-4443-8d93-fc17bea61afe |  | Status | 30 | DirectOperate | SingleBit | 2859 | FALSE | FALSE | 5 | SingleCoord | 2811;2811 | TripPulseOn;ClosePulseOn | 0;0
GTD_AL14_52-14_AJG2 |  | AJUSTE PARA GRUPO 2 | 806648e2-0fcb-494f-a31b-103007c89ecc | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 2 |  | UTR_GTD_1 | GTD_AL14_52-14_AJG2 |  | 32ef5f98-4e7a-48bd-acaf-b7dfb7c98532 |  | Status | 30 | DirectOperate | SingleBit | 1859 | FALSE | FALSE | 5 | SingleCoord | 1811;1811 | TripPulseOn;ClosePulseOn | 0;0
GTD_AL24_52-24_AJG2 |  | AJUSTE PARA GRUPO 2 | 8d46636a-b601-434c-87ed-495a5a722717 | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 2 |  | UTR_GTD_1 | GTD_AL24_52-24_AJG2 |  | d3cd3e62-6c1b-48c9-b6ea-b8a725800c30 |  | Status | 30 | DirectOperate | SingleBit | 2759 | FALSE | FALSE | 5 | SingleCoord | 2711;2711 | TripPulseOn;ClosePulseOn | 0;0
GTD_AL23_52-23_AJG2 |  | AJUSTE PARA GRUPO 2 | 848ecc05-ea85-4a99-832a-a9183352229a | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 2 |  | UTR_GTD_1 | GTD_AL23_52-23_AJG2 |  | b05042cf-4e79-4f92-af3c-b9ee33ce4c22 |  | Status | 30 | DirectOperate | SingleBit | 2659 | FALSE | FALSE | 5 | SingleCoord | 2611;2611 | TripPulseOn;ClosePulseOn | 0;0
GTD_TRF1_24-1_27 |  | 27 FUNCAO | 3151c49e-5685-449e-9f60-563888710906 | Status | GTD Distr | [6 empty] | GTD_TRF1_24-1_PROT_27 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_27 |  | 8b9df032-fdcb-45bf-a38a-a434604489a7 | 20262602 | Status | 30 | DirectOperate | SingleBit | 2070 | FALSE | FALSE | 15 | SingleCoord | 2015;2015 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TRF2_24-2_59 |  | 59 - SOBRETENSAO | 8d6b3d45-93df-4648-8221-bd0d097db9b5 | Status | GTD Distr | [6 empty] | GTD_TRF2_24-2_PROT_59 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_59 |  | 51a5cd60-d86c-43f6-af1b-3b78b72b32e9 |  | Status | 30 | DirectOperate | SingleBit | 2973 | FALSE | FALSE | 5 | SingleCoord | 2916;2916 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TSA1_52Q1_EST |  | ESTADO | 6c9aa4e9-36a3-4b38-a350-c0ba0493116d | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___DESLIGADO@LIGADO___Custom___INV_S_TS_SB | 2 |  | UTR_GTD_1 | GTD_TSA1_52Q1_EST |  | a2b545ca-95a8-4552-9980-b632ccffa846 | 20260408 | Status |  |  | MultiCoord | 3405;3406 | FALSE
GTD_BC1_52-16_59 |  | 59 - SOBRETENSAO | 8bda5011-f907-4d60-8802-cf0460895903 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_59 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_59 |  | a932040d-cddf-4f93-9063-c4d4e39c7f4d |  | Status | 30 | DirectOperate | SingleBit | 2148 | FALSE | FALSE | 5 | SingleCoord | 2104;2104 | ClosePulseOn;TripPulseOn | 0;0
GTD_TSA_BARRA_CAFL |  | FALTA VCA | 2d2f95bc-ff10-4263-b4a8-03fdd7756845 | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TSA_BARRA_CAFL |  | e21124cd-786f-4208-8cbf-8b5a501f63a3 | 20260408 | Status |  |  | SingleBit | 3402 | FALSE
GTD_AL11_52-11_AJG2 |  | AJUSTE PARA GRUPO 2 | 9921ded4-8cd3-477a-a922-a738889a25cb | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 2 |  | UTR_GTD_1 | GTD_AL11_52-11_AJG2 |  | 4197721c-b167-441b-9c55-69031cc3e5da |  | Status | 30 | DirectOperate | SingleBit | 1559 | FALSE | FALSE | 5 | SingleCoord | 1511;1511 | TripPulseOn;ClosePulseOn | 0;0
GTD_AL22_52-22_AJG2 |  | AJUSTE PARA GRUPO 2 | e74ad6bc-934b-4fee-8c18-397b406def11 | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 2 |  | UTR_GTD_1 | GTD_AL22_52-22_AJG2 |  | 945dd8ee-2748-4b33-8f5f-697c804adecc |  | Status | 30 | DirectOperate | SingleBit | 2560 | FALSE | FALSE | 5 | SingleCoord | 2511;2511 | TripPulseOn;ClosePulseOn | 0;0
GTD_AL12_52-12_AJG2 |  | AJUSTE PARA GRUPO 2 | 6cca2168-4e6c-4dfe-9ef7-8d3c5b37d564 | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 2 |  | UTR_GTD_1 | GTD_AL12_52-12_AJG2 |  | 8c090c53-b2e0-47e2-91e8-654c7bfc93fd |  | Status | 30 | DirectOperate | SingleBit | 1659 | FALSE | FALSE | 5 | SingleCoord | 1611;1611 | TripPulseOn;ClosePulseOn | 0;0
GTD_TSA2_52Q2_EST |  | ESTADO | 21f977a3-99a8-4104-b82b-23911584c080 | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___DESLIGADO@LIGADO___Custom___INV_S_TS_SB | 2 |  | UTR_GTD_1 | GTD_TSA2_52Q2_EST |  | bd111857-1019-4ae8-a5bd-7e6c586a4115 | 20260408 | Status |  |  | MultiCoord | 3408;3409 | FALSE
GTD_TRF2_24-2_AJG3 |  | AJUSTE PARA GRUPO 3 | 040eeb6d-ab05-4d37-a66d-09ce0fef121f | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_AJG3 |  | fae3f437-38cd-461c-90da-abea8caf6e6e | 20260401 | Status | 30 | DirectOperate | SingleBit | 2961 | FALSE | FALSE | 5 | SingleCoord | 2913 | ClosePulseOn | 0
GTD_AL13_52-13_AJG2 |  | AJUSTE PARA GRUPO 2 | 0c6b8fa4-f43e-4c07-a8b0-5860b71e04e9 | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 2 |  | UTR_GTD_1 | GTD_AL13_52-13_AJG2 |  | e264b9f6-7026-4ffc-89f3-e32a398f24bd |  | Status | 30 | DirectOperate | SingleBit | 1759 | FALSE | FALSE | 5 | SingleCoord | 1711;1711 | TripPulseOn;ClosePulseOn | 0;0
GTD_BC1_52-16_62BF |  | 62BF | 69492c91-63ba-4f6c-9e1d-a09ce6281dfa | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_62BF |  | 90bab35c-3f31-4482-9018-c74d1bc7fcb5 |  | Status |  |  | SingleBit | 2125 | FALSE
GTD_BC1_52-16_50F1 |  | 50 FASE ESTAGIO 1 | d1cbba47-5ee1-4585-87df-1b22a4395772 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_50F1 |  | 0cdeb070-5a76-4733-9962-654c2167a6d6 |  | Status |  |  | SingleBit | 2130 | FALSE
GTD_BC1_52-16_50N2 |  | 50N 2 | f741b4d9-d556-4fe1-a1c8-5cc755b091db | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_50N2 |  | 0b435347-06c4-42c4-8399-5a06036c4868 |  | Status |  |  | SingleBit | 2134 | FALSE
GTD_BC1_52-16_43TC |  | 43TC | 0298eb9a-0327-4ab0-b335-3044207f1125 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_BC1_52-16_43TC |  | 630ef73f-b021-4bb7-a05b-e2d909111907 |  | Status |  |  | SingleBit | 2116 | FALSE
GTD_BC1_52-16_BBA2 |  | BOBINA ABERTURA 2 | d57b6e31-f46e-49b8-83ee-3a603d2fdf8d | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_BBA2 |  | d8690d4a-0497-405c-9e4a-bffe4baeba09 |  | Status |  |  | SingleBit | 2110 | FALSE
GTD_BC1_52-16_AUTC |  | AUTOMATISMO | 79beaef3-d8d6-48c4-8575-a8db43e7a22e | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_AUTC |  | 5af5707b-fe19-4932-baca-cece589ca77b |  | Status |  |  | SingleBit | 2121 | FALSE
GTD_BC1_52-16_FA |  | FASE A | 7d71df73-4794-4bd0-9ccb-1398ef0ab867 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_FA |  | bfc779e2-afc1-421a-8b8c-fbf4fac96b03 |  | Status |  |  | SingleBit | 2126 | FALSE
GTD_BC1_52-16_27E1 |  | 27 1 | bc882519-16eb-42d4-856d-fafd1f0d185b | Status | GTD Trans | [6 empty] | SSC_BC1_52-3_PROT_27E1 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_27E1 |  | d46e77b6-b272-47c5-aebf-376eccb4b839 |  | Status |  |  | SingleBit | 2139 | FALSE
GTD_BC1_52-16_27E2 |  | 27 - SUBTENSAO E2 | d348b9f9-ce96-48da-a166-f3eacd51e901 | Status | GTD Trans | [6 empty] | PFC_BC1_BC1_PROT_27E2 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_27E2 |  | afbff870-b0f5-4d09-bfdb-50d2ebce72d5 |  | Status |  |  | SingleBit | 2140 | FALSE
GTD_BC1_52-16_N |  | NEUTRO | 461fd826-1476-44e9-858d-7c3f6692a506 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_N |  | a8737729-7db8-4376-ba69-f757153dc420 |  | Status |  |  | SingleBit | 2129 | FALSE
GTD_BC1_52-16_81SO |  | 81 - TRIP SOBRE FREQUENCIA | 6e67053a-5f91-42db-a8b2-8aaeda91f757 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_81SO |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_81SO |  | fbf1a418-2934-4406-b563-e6cecaf03c7c |  | Status |  |  | SingleBit | 2145 | FALSE
GTD_BC1_52-16_GOOS |  | FALHA GOOSE | 392364ac-4494-478a-bd18-6a18d0dafc2a | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_GOOS |  | a5297e4b-e593-4e85-86a0-e810c5f2de6a |  | Status |  |  | SingleBit | 2117 | FALSE
GTD_BC1_52-16_MOLA |  | MOLA | 433330fd-195d-4eaf-ab40-9d93898b79c9 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_MOLA |  | 8804b757-8efb-4b8e-9fcd-b515d8404021 |  | Status |  |  | SingleBit | 2103 | FALSE
GTD_BC1_52-16_B5M |  | BLOQUEIO 5 MINUTOS | 430a8cec-beac-4827-a487-3188f61936b0 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_B5M |  | ce0492b6-2b4e-4ea0-bc32-cab0e483d5ca |  | Status |  |  | SingleBit | 2115 | FALSE
GTD_BC1_52-16_TEXT |  | TRIP EXTERNO | af4de31c-1bae-426d-b9c2-46fbbbc7ae86 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_TEXT |  | 953c7ce2-3aae-44f4-8400-6f343707c2e8 |  | Status |  |  | SingleBit | 2147 | FALSE
GTD_BC1_52-16_FCOM |  | FALHA COMUNICACAO | 1ec5ede4-ae9b-43e3-9763-051b18a7b3c5 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_FCOM |  | d1ee3a60-30db-4b08-b8be-287ce7fe7e65 |  | Status |  |  | SingleBit | 2124 | FALSE
GTD_BC1_52-16_BBFC |  | BOB FEC | 5c4f4c93-e29b-4eec-95f3-ff514bc40099 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_BBFC |  | 6342b0b4-11c8-4671-8708-a2936d31a0e2 |  | Status |  |  | SingleBit | 2108 | FALSE
GTD_BC1_52-16_FSIN |  | FALHA SINCRONISMO IRIG-B | 2dff47da-e49a-4db7-9b48-96eb6db3910b | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_FSIN |  | 0f181947-ac3d-42d1-843b-ad801eb2bd81 |  | Status |  |  | SingleBit | 2119 | FALSE
GTD_TRF03_BARRA_T_FPBR |  | FALTA POTENCIAL BARRA | 837762ed-16b2-4749-8f12-1e76590752a5 | Status | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF03_BARRA_T_FPBR |  | fcab570f-d245-4589-81c7-7b50139b001b | 20260326 | Status |  |  | SingleBit | 488 | FALSE
GTD_TR1AT_TR1AT_MTRF |  | MODULO TRANSFERIDO | e2fbfcdb-cec1-4b3a-87f7-633b23ad26c3 | Status | GTD Trans | [6 empty] | GTD_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@TRANSFERIDA___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_MTRF |  | a6031d40-40fb-4163-b1f0-8dc596ca0258 | 20260126 | Status |  |  | SingleBit | 651 | FALSE
GTD_BC1_52-16_51F |  | 51 FASE | 66ada0b9-b851-495a-ac7d-64a50afcfa72 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_51F |  | fb9b1f0f-88bc-4a0a-aaea-9e083fd89d17 |  | Status |  |  | SingleBit | 2132 | FALSE
GTD_BC1_52-16_CCMO |  | FALTA VCC MOTOR | 3a2e70c3-d74f-4590-8d41-58ae328d958d | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_CCMO |  | 579fdc45-5d08-4fb7-b96c-aac01ec90e85 |  | Status |  |  | SingleBit | 2106 | FALSE
GTD_BC1_52-16_59E2 |  | 59 E2 | 57413bfd-0933-47a7-a47e-53a86caa492c | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_59_2 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_59E2 |  | 07527ca2-d666-4d6c-b3ff-eba12a63e7a6 |  | Status |  |  | SingleBit | 2142 | FALSE
GTD_BC1_52-16_59E1 |  | 59 E1 | 893a5582-8c32-4efb-9987-c625dcb2b658 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_59_1 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_59E1 |  | b814ba82-debf-414e-9b83-a4f791d6b758 |  | Status |  |  | SingleBit | 2141 | FALSE
GTD_BC1_52-16_50N1 |  | 50N 1 | 4f310a39-0291-441d-9bb0-5c5fa6f0a018 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_50N1 |  | 7c14776c-8b6d-4216-b2c5-1b4c10297d16 |  | Status |  |  | SingleBit | 2133 | FALSE
GTD_BC1_52-16_BBA1 |  | BOBINA ABERTURA 1 | 46eec39f-1ceb-43b7-8dd8-de626c6b854a | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_BBA1 |  | 05fd8942-bbd0-4758-acf6-1900f829eb5c |  | Status |  |  | SingleBit | 2109 | FALSE
GTD_BC1_52-16_43LR |  | 43LR | c4260966-2628-49ba-9387-9c8bd655d222 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_43LR |  | 79b14a27-7b05-40ae-a8e5-3d5ad9732c64 |  | Status |  |  | SingleBit | 2104 | FALSE
GTD_BC1_52-16_FC |  | FASE C | 6a37b628-1900-43ef-a4f4-dc85f6a36d06 | Status | GTD Trans | [6 empty] | GTD_AL11_52-11_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_FC |  | f0fea51d-7128-4ec6-8b87-8b646bba37c0 |  | Status |  |  | SingleBit | 2128 | FALSE
GTD_BC1_52-16_CCCO |  | FALTA VCC COMANDO | 3848c226-009a-46ef-95cf-65bdd406c375 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_CCCO |  | 8c4f68bf-cac5-4b2a-8d46-ee6c303a1d89 |  | Status |  |  | SingleBit | 2107 | FALSE
GTD_BC1_52-16_FB |  | FASE B | 3ed59ac5-2846-4d08-be4a-033d70175353 | Status | GTD Trans | [6 empty] | GTD_AL11_52-11_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_FB |  | 9a2b0df1-5716-44ad-937b-df70012a4f93 |  | Status |  |  | SingleBit | 2127 | FALSE
GTD_BC1_52-16_51N1 |  | 51N 1 | 8030d63e-171e-4ee7-9d47-606a4cf65706 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_51N1 |  | 260fd396-2c75-424f-95b9-870c931fae55 |  | Status |  |  | SingleBit | 2135 | FALSE
GTD_BC1_52-16_50F2 |  | 50 FASE ESTAGIO 2 | 77862e8f-28b0-4f0c-b32c-a3bbe2592faa | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_50F2 |  | 7cfa5a75-bdb0-4107-9d9e-685b5a642092 |  | Status |  |  | SingleBit | 2131 | FALSE
GTD_BC1_52-16_DR |  | RELE | e197a5be-2f0c-4c47-99f1-12edf1ba8e10 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_DR |  | 524c5dd7-83a7-42bf-84b0-bed9982abee1 |  | Status |  |  | SingleBit | 2123 | FALSE
GTD_BC1_52-16_27 |  | 27 - FUNCAO | cdba3075-d456-465e-b12c-c85a8173c360 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_27 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_BC1_52-16_27 |  | 3d1f80de-a784-43d7-a5e0-efeca3ce763c |  | Status | 30 | DirectOperate | SingleBit | 2138 | FALSE | FALSE | 5 | SingleCoord | 2101;2101 | ClosePulseOn;TripPulseOn | 0;0
GTD_TR1BT_TR1BT_MTRF |  | MODULO TRANSFERIDO | d376042e-5206-4ba8-a568-158d10f51872 | Status | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@TRANSFERIDA___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_MTRF |  | db39ebed-132e-4470-9d16-17064e91c30f | 20260126 | Status |  |  | SingleBit | 656 | FALSE
GTD_TR2BT_TR2BT_MTRF |  | MODULO TRANSFERIDO | dcf67cd8-4f14-40e5-8813-793d8ba8e92a | Status | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@TRANSFERIDA___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_MTRF |  | ca6d7d8f-b140-47c2-952b-d59ee55bbcee | 20260126 | Status |  |  | SingleBit | 956 | FALSE
GTD_BC1_52-16_DJF1 |  | DISJUNTOR NF | 79dd73ef-37ef-4ebb-93ac-de154951180c | SwitchStatus | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SC_USO_BC | 2 |  | UTR_GTD_1 | GTD_BC1_52-16_DJF1 |  | 96ee594a-4a56-4345-b593-61b4844711b4 |  | Status | 30 | DirectOperate | MultiCoord | 2100;2101 | FALSE | FALSE | 5 | SingleCoord | 2100;2100 | TripPulseOn;ClosePulseOn | 0;0
GTD_TR2AT_TR2AT_TPIN |  | TRANSFERENCIA DE PROTECAO | 2eec0eb5-a0ce-4ed8-9b18-6a6e1822b4ee | Status | GTD Trans | [6 empty] | GTD_TR2AT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___COMPLETA@INCOMPLETA___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_TPIN |  | c1d0db73-9533-4fcb-b39c-129bdd0d7730 | 20260126 | Status |  |  | SingleBit | 952 | FALSE
GTD_BC1_52-16_AUTO |  | AUTOMATISMO | 02722b4e-8368-494c-8b31-f85b68951b94 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS_AUTO | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_AUTO |  | 6d2286f6-b788-4e17-b20f-f12583fdb459 |  | Status | 30 | DirectOperate | SingleBit | 2120 | FALSE | FALSE | 5 | SingleCoord | 2102;2102 | TripPulseOn;ClosePulseOn | 0;0
GTD_BC1_52-16_81BLOQ |  | 81 BLOQUEIO DINAMICO | 96622442-6bc1-403a-abcd-cd9ad6a3e504 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_BC1_52-16_81BLOQ |  | e554bcde-1147-4e06-822a-21978c67af03 |  | Status |  |  | SingleBit | 2143 | FALSE
GTD_BC2_52-17_50F1 |  | 50 FASE ESTAGIO 1 | c047d98b-7f7d-4161-ba86-d9f9348855d4 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_50F1 |  | 6ab2d53c-f070-4742-8caf-923b32f97170 |  | Status |  |  | SingleBit | 2230 | FALSE
GTD_BC2_52-17_N |  | NEUTRO | f444f127-f813-4449-8211-88aa402f9d61 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_N |  | bbdd57ec-8d25-49eb-8e2e-bdfd9c785df2 |  | Status |  |  | SingleBit | 2229 | FALSE
GTD_BC2_52-17_62BF |  | 62BF | 6ed47f1c-e38e-496d-9033-00147066d4ea | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_62BF |  | b7c86fd6-e278-4fb4-952c-cde6d67f5ffe |  | Status |  |  | SingleBit | 2225 | FALSE
GTD_BC2_52-17_27E1 |  | 27 1 | 26f3955b-73dd-4577-aa17-cd53e0e68a66 | Status | GTD Trans | [6 empty] | SSC_BC1_52-3_PROT_27E1 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_27E1 |  | e5f23616-9163-4740-9608-d808c26119c8 |  | Status |  |  | SingleBit | 2239 | FALSE
GTD_BC2_52-17_BBFC |  | BOB FEC | 65866505-d28f-4dbf-a9b7-8afdbca7604e | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_BBFC |  | 1a8ced52-e403-468d-abcd-df27ef79e0d6 |  | Status |  |  | SingleBit | 2208 | FALSE
GTD_BC2_52-17_AUTC |  | AUTOMATISMO | 40429e70-465f-49ca-af18-290cc0d9e353 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_AUTC |  | 99906def-d80a-4ef5-8d61-ce251b3be369 |  | Status |  |  | SingleBit | 2221 | FALSE
GTD_BC2_52-17_51N1 |  | 51N 1 | 20cbe117-8f42-4c0b-b85d-7c4afa193eff | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_51N1 |  | 3135229b-e0c9-4605-afdf-eae8cd22e1f0 |  | Status |  |  | SingleBit | 2235 | FALSE
GTD_BC2_52-17_BBA1 |  | BOBINA ABERTURA 1 | fb4c3796-e630-4b73-9d18-89ff07562c72 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_BBA1 |  | 70bb0273-9748-4b50-b297-2e61338208a0 |  | Status |  |  | SingleBit | 2209 | FALSE
GTD_BC2_52-17_FC |  | FASE C | 1d820675-9ec1-4cc2-bfbe-6031399687b1 | Status | GTD Trans | [6 empty] | GTD_AL11_52-11_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_FC |  | 908dfe55-6cb3-4423-8e0d-a742db7779f7 |  | Status |  |  | SingleBit | 2228 | FALSE
GTD_BC2_52-17_MOLA |  | MOLA | 05cafbea-4f7f-4bed-93e6-6556671b4790 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_MOLA |  | 9b6810df-a61e-41f2-aace-0a3c4c5f74ee |  | Status |  |  | SingleBit | 2203 | FALSE
GTD_BC2_52-17_CCMO |  | FALTA VCC MOTOR | 9b390eda-bce3-49de-b9c6-3cd770e43c02 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_CCMO |  | 190af265-94a8-4e02-a5e0-2259f8130a55 |  | Status |  |  | SingleBit | 2206 | FALSE
GTD_BC2_52-17_TEXT |  | TRIP EXTERNO | b83fdbcb-3e41-4b8d-810c-bcd9bbb678fa | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_TEXT |  | 35c8a9c3-a3a4-4e48-bb5c-b548196a978c |  | Status |  |  | SingleBit | 2247 | FALSE
GTD_BC2_52-17_GOOS |  | FALHA GOOSE | 4d56fb5b-afad-43c2-b4c8-99ccb832e0e8 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_GOOS |  | efc8733d-1462-465e-9e9d-dad84b4d5299 |  | Status |  |  | SingleBit | 2217 | FALSE
GTD_BC2_52-17_59E2 |  | 59 E2 | 5dce285d-eb9c-40e4-8ccb-86ee863d23b4 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_59_2 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_59E2 |  | 863453c3-a349-48f4-bbda-4047b410fcd0 |  | Status |  |  | SingleBit | 2242 | FALSE
GTD_BC2_52-17_FSIN |  | FALHA SINCRONISMO IRIG-B | 8589e5e8-f798-434e-9ffd-3a2ddc9ba95f | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_FSIN |  | a7ff0b92-48e6-4ef6-8ab1-1200709ec578 |  | Status |  |  | SingleBit | 2219 | FALSE
GTD_BC1_52-11_FUTP |  | FALHA CIRCUITO TP | d030937a-d503-464a-874f-ddc0e66ce76f | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC1_52-11_FUTP |  | 8bbf9af3-9140-479b-b994-860ef7d112cd |  | Status |  |  | SingleBit | 2146 | FALSE
GTD_BC2_52-17_81SU |  | 81 - TRIP SUB FREQUENCIA | 71cd489c-befa-4582-928b-809ad3cf34bb | Status | GTD Trans | [6 empty] | PFA_LTKSM_LTKSM_PROT_81SU |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_81SU |  | bd619430-516f-4551-9e74-8495efc4b8df |  | Status |  |  | SingleBit | 2244 | FALSE
GTD_TSA1_TSA1_CAFL |  | FALTA VCA | 84543f6e-5745-4f61-9e46-9fce195d4d3a | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TSA1_TSA1_CAFL |  | 96407e3b-d0fb-4263-851d-e9c7529a7bb1 | 20260408 | Status |  |  | SingleBit | 3400 | FALSE
GTD_TRSA_TRSA_AUTO |  | AUTOMATISMO | a3ddc584-be9f-4349-a041-2138d979acdc | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS_AUTO | 1 |  | UTR_GTD_1 | GTD_TRSA_TRSA_AUTO |  | 859d0967-a15f-46e4-9376-c94ef97c9ec2 |  | Status | 30 | DirectOperate | SingleBit | 3403 | FALSE | FALSE | 5 | SingleCoord | 3402;3402 | TripPulseOn;ClosePulseOn | 0;0
GTD_BC3_52-26_81SU |  | 81 - TRIP SUB FREQUENCIA | 0c4d5eb8-8317-4e1c-95c9-dba1027258aa | Status | GTD Trans | [6 empty] | PFA_LTKSM_LTKSM_PROT_81SU |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_81SU |  | e3655ee9-c72b-4ab0-8497-78133e96aaee |  | Status |  |  | SingleBit | 3044 | FALSE
GTD_BC3_52-26_50F2 |  | 50 FASE ESTAGIO 2 | e8ae8521-ce6f-4213-8848-0b837f414ca8 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_50F2 |  | 5ae0ee1e-6f5e-4b49-a6c7-62406ad184a8 |  | Status |  |  | SingleBit | 3031 | FALSE
GTD_BC3_52-26_50N1 |  | 50N 1 | 51c781e6-9713-436e-9195-c395fb119ba1 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_50N1 |  | 6a9822d7-8a58-4a65-979e-4820cdb50804 |  | Status |  |  | SingleBit | 3033 | FALSE
GTD_BC2_52-17_FUTP |  | FALHA CIRCUITO TP | 04e5f9a3-dcf3-4a55-980c-8c28b5b82631 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_FUTP |  | cada6eba-67d6-4718-884e-c10a145bcf22 |  | Status |  |  | SingleBit | 2246 | FALSE
GTD_BC3_52-26_50N2 |  | 50N 2 | 901c27f1-4abc-4d7d-a8da-a55085105e12 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_50N2 |  | 59d43525-a05d-4b49-89ab-fe463bf08cdf |  | Status |  |  | SingleBit | 3034 | FALSE
GTD_BC3_52-26_51F |  | 51 FASE | 139d3b29-24d1-40b9-a054-e707c81c12b8 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_51F |  | 22ebdb68-07e8-404d-aace-18b3a83feeab |  | Status |  |  | SingleBit | 3032 | FALSE
GTD_BC2_52-17_50F2 |  | 50 FASE ESTAGIO 2 | 21309ac0-1028-4813-8dc0-070dc0de356c | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_50F2 |  | ae6c0a05-aa1e-40b6-826e-2858f8fd3852 |  | Status |  |  | SingleBit | 2231 | FALSE
GTD_BC3_52-26_FA |  | FASE A | 9690339a-5beb-4102-9dbf-183d70d6f19c | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_FA |  | 142b494a-c2c9-4382-8b53-fcf0a6830d38 |  | Status |  |  | SingleBit | 3026 | FALSE
GTD_BC3_52-26_FB |  | FASE B | b2b02fa4-1c8a-4856-adaa-56e8ab9d0127 | Status | GTD Trans | [6 empty] | GTD_AL11_52-11_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_FB |  | 1b517488-a53b-44b3-889e-612424ce3a00 |  | Status |  |  | SingleBit | 3027 | FALSE
GTD_BC2_52-17_59E1 |  | 59 E1 | 23d96d00-b220-4fbe-af80-4eed92f3273b | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_59_1 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_59E1 |  | 2a88bd11-01de-4261-8691-1ac5a8776df4 |  | Status |  |  | SingleBit | 2241 | FALSE
GTD_BC3_52-26_FC |  | FASE C | 611f20d9-cb7e-49c4-97f7-384de1d821bd | Status | GTD Trans | [6 empty] | GTD_AL11_52-11_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_FC |  | 497c720b-f236-4e1c-816d-816c41f0de7d |  | Status |  |  | SingleBit | 3028 | FALSE
GTD_BC3_52-26_50F1 |  | 50 FASE ESTAGIO 1 | 125ae8e8-e808-4b96-b3e1-04d1383cf04d | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_50F1 |  | bf696042-3768-429b-8b78-8ab485e4a35f |  | Status |  |  | SingleBit | 3030 | FALSE
GTD_BC3_52-26_N |  | NEUTRO | 7f8b9864-ad48-4218-9ea9-e735464821ed | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_N |  | ca072d2c-2604-4d4a-ae86-12fbb6536b32 |  | Status |  |  | SingleBit | 3029 | FALSE
GTD_BC2_52-17_BBA2 |  | BOBINA ABERTURA 2 | d1d9948c-ef04-41b8-9426-1e123ec4c37c | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_BBA2 |  | 67f006f6-aacc-4005-8aea-b844d01c8ced |  | Status |  |  | SingleBit | 2210 | FALSE
GTD_BC3_52-26_27E2 |  | 27 - SUBTENSAO E2 | eb31a379-be32-4cc7-badc-1e198bcb8d18 | Status | GTD Trans | [6 empty] | PFC_BC1_BC1_PROT_27E2 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_27E2 |  | c964e304-7030-4dbf-ad04-a13b89fb9e75 |  | Status |  |  | SingleBit | 3040 | FALSE
GTD_BC3_52-26_59E2 |  | 59 E2 | 752cf5e7-6c27-4561-abb1-de5c4a267e6e | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_59_2 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_59E2 |  | ad744f6e-15b8-4a23-9581-89bd2d8af6a8 |  | Status |  |  | SingleBit | 3042 | FALSE
GTD_BC3_52-26_59E1 |  | 59 E1 | b189afbc-aee7-4d19-930a-6302a492d649 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_59_1 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_59E1 |  | 3ba4b0a3-d317-46d3-8760-e6388a66446c |  | Status |  |  | SingleBit | 3041 | FALSE
GTD_BC3_52-26_43LR |  | 43LR | ffadaa0b-92e0-4ba4-96ba-ba443f631c15 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_43LR |  | b02fa0df-fe34-4760-a2a0-0d3f1320e597 |  | Status |  |  | SingleBit | 3004 | FALSE
GTD_BC3_52-26_62BF |  | 62BF | cee29803-a7e2-4452-89fb-199f6f00d011 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_62BF |  | 9266b578-f2ef-43f5-b46f-a96c47997baf |  | Status |  |  | SingleBit | 3025 | FALSE
GTD_BC3_52-26_81BLOQ |  | 81 BLOQUEIO DINAMICO | 8cb229e9-1203-43ce-99a1-3615ffbc1a0c | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_81BLOQ |  | 09b75df3-63d9-4455-a9dc-95426006f01a |  | Status |  |  | SingleBit | 3043 | FALSE
GTD_BC3_52-26_AUTC |  | AUTOMATISMO | 9ac52079-9163-4024-80be-5df2a5d66079 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_AUTC |  | 7c1e6703-9721-4012-a5b6-e3d11b8c9369 |  | Status |  |  | SingleBit | 3021 | FALSE
GTD_BC3_52-26_B5M |  | BLOQUEIO 5 MINUTOS | 2eac88ae-3b1a-4a1a-bba5-d3c0d2ea68b1 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_B5M |  | fb75a4a3-95c9-4010-a000-ce67139efce6 |  | Status |  |  | SingleBit | 3015 | FALSE
GTD_BC3_52-26_43TC |  | 43TC | 9d11efe6-d3ae-41a0-8e08-6641c479abad | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_BC3_52-26_43TC |  | 8ef4ee07-9e1d-4230-8020-fe4c9b412fa1 |  | Status |  |  | SingleBit | 3016 | FALSE
GTD_BC3_52-26_BBA1 |  | BOBINA ABERTURA 1 | d45d451a-4259-4608-ab4c-c4e5c562244d | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_BBA1 |  | 844c32c0-5609-490a-b13b-ae3cc1b81cbf |  | Status |  |  | SingleBit | 3009 | FALSE
GTD_BC3_52-26_BBA2 |  | BOBINA ABERTURA 2 | 0ca5ad3e-73ca-4e1b-8ee2-44c2d9785da3 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_BBA2 |  | 9a6c3e1a-d55b-4c4c-a6d9-b2bbae2226be |  | Status |  |  | SingleBit | 3010 | FALSE
GTD_BC3_52-26_BBFC |  | BOB FEC | bacd4cd3-9a09-4879-8f4f-af6a8053e278 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_BBFC |  | 4051c999-e8c8-4adc-bece-a26253d10e02 |  | Status |  |  | SingleBit | 3008 | FALSE
GTD_BC2_52-17_CCCO |  | FALTA VCC COMANDO | f7443caa-6f9d-4e12-bc40-426338639d0b | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_CCCO |  | 9a00f49b-d86a-4d09-bcd0-e7aa8c9fb652 |  | Status |  |  | SingleBit | 2207 | FALSE
GTD_BC3_52-26_DR |  | RELE | 34fbfcca-6bcf-4719-b6b6-50f20b0c31c9 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_DR |  | 422fc939-95c6-4f00-8c03-1a4b76918de2 |  | Status |  |  | SingleBit | 3023 | FALSE
GTD_BC3_52-26_81SO |  | 81 - TRIP SOBRE FREQUENCIA | e664ed17-672f-43ac-9613-829d6b967840 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_81SO |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_81SO |  | e4a20aed-c776-4e26-8ac9-2dc66b8a9224 |  | Status |  |  | SingleBit | 3045 | FALSE
GTD_BC1_52-16_81SU |  | 81 - TRIP SUB FREQUENCIA | c63f86d8-3c94-416c-bb91-1241e5e98e10 | Status | GTD Trans | [6 empty] | PFA_LTKSM_LTKSM_PROT_81SU |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_81SU |  | 5b0ef72f-c2d2-419e-9f80-99425ef21161 |  | Status |  |  | SingleBit | 2144 | FALSE
GTD_BC3_52-26_FSIN |  | FALHA SINCRONISMO IRIG-B | 6ab708a4-9b54-4b74-97ad-531432365d0c | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_FSIN |  | 7bbd9949-83a1-4989-bab4-647ee0947164 |  | Status |  |  | SingleBit | 3019 | FALSE
GTD_BC3_52-26_CCMO |  | FALTA VCC MOTOR | 64c61002-4b55-4997-b202-42014a1c00ad | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_CCMO |  | c735774c-c424-4e40-9d48-97e2e202827c |  | Status |  |  | SingleBit | 3006 | FALSE
GTD_BC3_52-26_GOOS |  | FALHA GOOSE | 9867cad0-5d09-477c-8443-e24fb55558f3 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_GOOS |  | d55044ba-703f-49f3-8fd5-c4b6e1f493af |  | Status |  |  | SingleBit | 3017 | FALSE
GTD_BC2_52-17_81SO |  | 81 - TRIP SOBRE FREQUENCIA | 82f40ecc-2984-4aed-9145-a41b7015da0d | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_81SO |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_81SO |  | 91d57f25-ff51-4d7f-8893-184727c5cea1 |  | Status |  |  | SingleBit | 2245 | FALSE
GTD_BC3_52-26_FUTP |  | FALHA CIRCUITO TP | 3e97425e-cf7e-41b2-bb78-40410d604bde | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_FUTP |  | 090344ba-ba63-481e-9332-a74aee7a41a7 |  | Status |  |  | SingleBit | 3046 | FALSE
GTD_BC4_52-27_50F2 |  | 50 FASE ESTAGIO 2 | c8c423a1-be61-411f-a389-f9ddc1b81a7f | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_50F2 |  | caa91920-f760-4a25-8525-ae7a324d194c |  | Status |  |  | SingleBit | 3131 | FALSE
GTD_BC4_52-27_50F1 |  | 50 FASE ESTAGIO 1 | 166f93f6-bbb2-4aa6-9636-1831eb69eb59 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_50F1 |  | 3a9f651f-5d2a-4ce6-9663-576f1f4ac9b7 |  | Status |  |  | SingleBit | 3130 | FALSE
GTD_BC3_52-26_TEXT |  | TRIP EXTERNO | 509df218-b4b2-4882-9493-d2db81deac3a | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_TEXT |  | e91b626a-45b8-4f29-a71d-faf069aab956 |  | Status |  |  | SingleBit | 3047 | FALSE
GTD_BC4_52-27_50N1 |  | 50N 1 | 192895d6-85b7-47e7-80d8-dcd6c07547bc | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_50N1 |  | 90bf3fc8-5fec-46c2-9c72-e8aa07b0a3e4 |  | Status |  |  | SingleBit | 3133 | FALSE
GTD_BC3_52-26_FCOM |  | FALHA COMUNICACAO | 6695cbd4-2c57-4243-8c80-7c5087e5fffc | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_FCOM |  | deb33c8c-33a9-411c-b655-96eb30b1b36f |  | Status |  |  | SingleBit | 3024 | FALSE
GTD_BC4_52-27_51N1 |  | 51N 1 | 2ae9ed59-e1aa-4fdf-903b-01b4961595ec | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_51N1 |  | 5e9ff77c-d714-438c-a97b-2a50e6a6009f |  | Status |  |  | SingleBit | 3135 | FALSE
GTD_BC3_52-26_27E1 |  | 27 1 | c2890ad4-028f-40c2-8fcc-9b803d14c232 | Status | GTD Trans | [6 empty] | SSC_BC1_52-3_PROT_27E1 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_27E1 |  | e47daa18-9ffa-4c91-8f42-a5a411a5e963 |  | Status |  |  | SingleBit | 3039 | FALSE
GTD_BC3_52-26_MOLA |  | MOLA | 6d93f6e7-dd90-4bd8-9f1d-4e37ce032f5c | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_MOLA |  | 570e9b32-e6ed-42bd-881b-5b386a28a548 |  | Status |  |  | SingleBit | 3003 | FALSE
GTD_BC3_52-26_61_1 |  | 61 - DESEQUILIBRIO E1 | e432993f-85c4-4ed9-b832-4d0ac2ff20fc | Status | GTD Trans | [6 empty] | SIA_BC1_52-5_PROT_61_1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_61_1 |  | fa77babe-533c-4377-bdfb-7c34d0000b3e |  | Status |  |  | SingleBit | 3036 | FALSE
GTD_BC4_52-27_FB |  | FASE B | 6118345d-3504-48c8-bbb8-4ae5c2448810 | Status | GTD Trans | [6 empty] | GTD_AL11_52-11_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_FB |  | b54ede9c-7912-49b3-b7ff-268690e72156 |  | Status |  |  | SingleBit | 3127 | FALSE
GTD_BC4_52-27_FA |  | FASE A | 12dbdae2-f373-4c4a-b27e-8eb496c04f3b | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_FA |  | 964a6f1c-5469-4902-87a6-8a4cf5f0d275 |  | Status |  |  | SingleBit | 3126 | FALSE
GTD_BC4_52-27_27E2 |  | 27 - SUBTENSAO E2 | f37cdcfe-3c2c-45ac-a414-0de10fbabb4f | Status | GTD Trans | [6 empty] | PFC_BC1_BC1_PROT_27E2 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_27E2 |  | 0f460128-9c4e-491c-aff6-93ac4276a0e3 |  | Status |  |  | SingleBit | 3140 | FALSE
GTD_BC4_52-27_59E1 |  | 59 E1 | 07a7b270-76c8-433f-820c-19f00ce42c0e | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_59_1 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_59E1 |  | 7725dbdd-89a0-48ad-867a-7554f67243d3 |  | Status |  |  | SingleBit | 3141 | FALSE
GTD_BC3_52-26_51N1 |  | 51N 1 | 16cfccc8-7246-44a6-bfbd-d97eff6a0b83 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_51N1 |  | 2de96c0f-b135-4eec-b2f6-7863ef0538e0 |  | Status |  |  | SingleBit | 3035 | FALSE
GTD_BC4_52-27_N |  | NEUTRO | 0db6915b-9e4e-4f8b-81fd-e477fd460ab6 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_N |  | 2d651df4-83ad-438a-bdc1-d953cd35a77a |  | Status |  |  | SingleBit | 3129 | FALSE
GTD_BC4_52-27_59E2 |  | 59 E2 | 43cbe4b9-4722-42d4-9b4a-d66540cc825d | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_59_2 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_59E2 |  | c5115a26-0e46-47ac-9cb0-22e9f205ba2b |  | Status |  |  | SingleBit | 3142 | FALSE
GTD_BC4_52-27_81SO |  | 81 - TRIP SOBRE FREQUENCIA | 058b7395-6184-41cb-9a0f-6bf592136e35 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_81SO |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_81SO |  | e8a82a44-33dc-4404-ba8a-98e6ad9b0d7c |  | Status |  |  | SingleBit | 3145 | FALSE
GTD_BC4_52-27_FC |  | FASE C | 9e868a4f-854d-4b59-bad8-53f481fd2123 | Status | GTD Trans | [6 empty] | GTD_AL11_52-11_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_FC |  | 00e25987-0dcb-49fb-9500-10734f3e6063 |  | Status |  |  | SingleBit | 3128 | FALSE
GTD_BC4_52-27_81SU |  | 81 - TRIP SUB FREQUENCIA | c24c05fa-1f93-49cf-ba4a-9025118095c4 | Status | GTD Trans | [6 empty] | PFA_LTKSM_LTKSM_PROT_81SU |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_81SU |  | 21b08e83-260b-47e5-840b-d3f7f15b4b38 |  | Status |  |  | SingleBit | 3144 | FALSE
GTD_BC4_52-16_FUTP |  | FALHA CIRCUITO TP | 1982c53e-1b05-4e6d-bec1-9eba61f07a82 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC4_52-16_FUTP |  | efe88998-bff1-4726-96b8-6124811622f7 |  | Status |  |  | SingleBit | 3146 | FALSE
GTD_BC4_52-27_43TC |  | 43TC | a9a10c0d-6ff0-4300-85ca-a14076b36451 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_BC4_52-27_43TC |  | 5c6debf8-c26e-4767-a99a-a555ce16d517 |  | Status |  |  | SingleBit | 3116 | FALSE
GTD_BC4_52-27_AUTC |  | AUTOMATISMO | 4818730c-7e41-4f25-a5e9-780293e9f449 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_AUTC |  | dcb51322-5251-4f53-a026-f8a16fd965d7 |  | Status |  |  | SingleBit | 3121 | FALSE
GTD_BC4_52-27_B5M |  | BLOQUEIO 5 MINUTOS | dbd85b37-cbbf-4815-ab5a-59ef2ac561e7 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_B5M |  | f3703c04-e406-4422-ad6e-060250d18183 |  | Status |  |  | SingleBit | 3115 | FALSE
GTD_BC4_52-27_BBA1 |  | BOBINA ABERTURA 1 | f2b16ffc-0007-4556-9c20-ecae7289333e | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_BBA1 |  | 936bf49a-cb00-47e5-96f7-67367dd53f71 |  | Status |  |  | SingleBit | 3109 | FALSE
GTD_BC4_52-27_BBA2 |  | BOBINA ABERTURA 2 | 6445897b-16bd-42af-9002-bae0d45211cf | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_BBA2 |  | 835a942a-caa8-4d15-bbbd-22a4e83244b0 |  | Status |  |  | SingleBit | 3110 | FALSE
GTD_BC4_52-27_BBFC |  | BOB FEC | e7056b2b-d8b0-4d69-9805-af1ebd9511ea | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_BBFC |  | 1ec3c698-e616-4cfc-986d-0ca894e6dceb |  | Status |  |  | SingleBit | 3108 | FALSE
GTD_BC4_52-27_CCCO |  | FALTA VCC COMANDO | d21137a0-0025-4af7-acf1-4daa3792d2f8 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_CCCO |  | 7e437e38-f823-4ee9-a134-b595788a9ca9 |  | Status |  |  | SingleBit | 3107 | FALSE
GTD_BC4_52-27_CCMO |  | FALTA VCC MOTOR | 7148165a-adb3-4258-aad4-b9f526ff65bd | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_CCMO |  | b5fd01f3-b077-4c48-a532-31bf6fce908d |  | Status |  |  | SingleBit | 3106 | FALSE
GTD_BC4_52-27_DR |  | RELE | e38af47b-ed3a-4bb1-8a15-ddca99f1d9af | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_DR |  | 51c1e14e-b5bb-48fd-8520-2c9a6c7bb766 |  | Status |  |  | SingleBit | 3123 | FALSE
GTD_BC4_52-27_FCOM |  | FALHA COMUNICACAO | 2b617c7f-daf8-4307-88a3-bff44215b372 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_FCOM |  | a2a96f65-20fd-4d3e-a966-441f0dbef8b8 |  | Status |  |  | SingleBit | 3124 | FALSE
GTD_BC4_52-27_FSIN |  | FALHA SINCRONISMO IRIG-B | 75b6d14e-eea3-47ed-bc0b-1360bafefa9a | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_FSIN |  | 8ef7f407-76fd-4f4e-bfe1-05d2fb42291b |  | Status |  |  | SingleBit | 3119 | FALSE
GTD_BC4_52-27_GOOS |  | FALHA GOOSE | f1cd47e9-16c7-4fbc-ba8f-b77c1758a41b | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_GOOS |  | 68a35844-7687-4d97-9a6f-b53d2e0cbbb0 |  | Status |  |  | SingleBit | 3117 | FALSE
GTD_BC4_52-27_MOLA |  | MOLA | b4ad47d6-d5e1-4c34-83e7-518055f0c737 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_MOLA |  | 5ec0a0f6-906f-4a7e-a6d4-b63eb46eff68 |  | Status |  |  | SingleBit | 3103 | FALSE
GTD_BC2_52-17_50N1 |  | 50N 1 | eaafda84-17e2-4693-8c6f-943b148fd00a | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_50N1 |  | 31c0ac10-90f6-49bd-842b-654b13422862 |  | Status |  |  | SingleBit | 2233 | FALSE
GTD_BC4_52-27_TEXT |  | TRIP EXTERNO | ea451a4c-bf60-43e3-9456-08c1fd80b3a2 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_TEXT |  | a3546466-9eec-4505-b63f-417c425a6d08 |  | Status |  |  | SingleBit | 3147 | FALSE
GTD_BC4_52-27_51F |  | 51 FASE | d758c642-0b29-4a56-8428-7a8861a45291 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_51F |  | 8598d88a-2ac3-4597-9eff-267d6d8dc83a |  | Status |  |  | SingleBit | 3132 | FALSE
GTD_BC2_52-17_FA |  | FASE A | c0b9a445-da01-4774-af6d-53967efd1932 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_FA |  | RelayTrip | A | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_FA |  | b4a7e308-d30d-47fc-ae41-1e715ea0fbaa |  | Status |  |  | SingleBit | 2226 | FALSE
GTD_BC2_52-17_43LR |  | 43LR | 3e0f2eb6-126f-449e-8ff2-5e3ad97676d1 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_43LR |  | 8a64ee8d-29a3-4e8e-9db7-7842238d86a1 |  | Status |  |  | SingleBit | 2204 | FALSE
GTD_BC2_52-17_B5M |  | BLOQUEIO 5 MINUTOS | 5772bee5-223c-4c41-9d28-5007c28bd267 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_B5M |  | 0c2a06b6-28f1-4e72-8205-3e680691e545 |  | Status |  |  | SingleBit | 2215 | FALSE
GTD_BC2_52-17_81BLOQ |  | 81 BLOQUEIO DINAMICO | 8798a22f-872d-4e6f-aa05-5a348d268570 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_81BLOQ |  | 72455df4-34ca-42b8-a039-40e8dacb97b0 |  | Status |  |  | SingleBit | 2243 | FALSE
GTD_BC4_52-27_27E1 |  | 27 1 | 605683f1-ca77-40e0-b7dc-73487ce4e7cd | Status | GTD Trans | [6 empty] | SSC_BC1_52-3_PROT_27E1 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_27E1 |  | 8c63d2ec-1d9b-4c3e-9828-a0b3821b555a |  | Status |  |  | SingleBit | 3139 | FALSE
GTD_BC4_52-27_62BF |  | 62BF | a6aa262b-7e2a-4de9-9734-9872beade319 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_62BF |  | 85293f52-aaab-4f06-b45f-59ddc78c40d1 |  | Status |  |  | SingleBit | 3125 | FALSE
GTD_BC4_52-27_43LR |  | 43LR | 7d13a97d-b0d7-4434-a467-f82cc51bf5f2 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_43LR |  | b953cfa1-f165-409d-8bfc-a5bec45fd907 |  | Status |  |  | SingleBit | 3104 | FALSE
GTD_BC2_52-17_43TC |  | 43TC | b6e14761-b76f-41f9-a5c9-491dfb1b849c | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_BC2_52-17_43TC |  | 05429afb-2a6e-43a8-8092-84dd2c79d149 |  | Status |  |  | SingleBit | 2216 | FALSE
GTD_BC4_52-27_81BLOQ |  | 81 BLOQUEIO DINAMICO | fe226853-2add-4d6d-bb99-4fd0d7dba33a | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_81BLOQ |  | 81d979ee-b0e8-4da9-84ab-f06647e64a46 |  | Status |  |  | SingleBit | 3143 | FALSE
GTD_BC2_52-17_DR |  | RELE | 35dec5d5-8189-4a18-bcef-c1e9819beae3 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_DR |  | 49c70580-5fcb-449b-874f-784fc417ee2c |  | Status |  |  | SingleBit | 2223 | FALSE
GTD_BC2_52-17_50N2 |  | 50N 2 | e4366eb1-b75a-46f5-a1c2-d25978a5291a | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_50N2 |  | 26d3d37a-ebc5-442d-b552-58a111a9256e |  | Status |  |  | SingleBit | 2234 | FALSE
GTD_BC3_52-26_CCCO |  | FALTA VCC COMANDO | b26a1fe8-228c-40e2-abb8-df5544169018 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_CCCO |  | af310215-53f2-411f-a316-80bff86c5e46 |  | Status |  |  | SingleBit | 3007 | FALSE
GTD_BC4_52-27_50N2 |  | 50N 2 | 9cd30b90-3f42-4ea4-a70a-d3478e4a6b35 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_50N2 |  | a2032600-b367-4462-96a5-5400cbc17258 |  | Status |  |  | SingleBit | 3134 | FALSE
GTD_BC2_52-17_FB |  | FASE B | b7e2d59c-6576-4de0-8644-e11e255499a5 | Status | GTD Trans | [6 empty] | GTD_AL11_52-11_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_FB |  | ad4aed05-58de-44a1-9fa2-1561ee819aa2 |  | Status |  |  | SingleBit | 2227 | FALSE
GTD_BC2_52-17_27E2 |  | 27 - SUBTENSAO E2 | 4efc58a3-aac2-4cc7-98b7-eb06f4e87dc8 | Status | GTD Trans | [6 empty] | PFC_BC1_BC1_PROT_27E2 |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_27E2 |  | 6bc34492-d276-4a8d-8e72-1006200e7618 |  | Status |  |  | SingleBit | 2240 | FALSE
GTD_BC2_52-17_51F |  | 51 FASE | 67962df2-8550-42ab-9fed-c1a90bc00b5b | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_51F |  | 096deb3b-08e4-482c-b609-82068066c7f1 |  | Status |  |  | SingleBit | 2232 | FALSE
GTD_BC2_52-17_FCOM |  | FALHA COMUNICACAO | aab16905-16c4-4a00-9633-1cd026f1a241 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_FCOM |  | d4186715-cb7f-410d-9bf0-1db767a2a28b |  | Status |  |  | SingleBit | 2224 | FALSE
GTD_BC1_52-16_86 |  | 86 | 519c911f-a9ca-4867-bcbe-b70d7a47231d | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | ReadWrite |  | REARMAR@null___NORMAL@ATUADO___Custom_S_TC_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_86 |  | dae111f1-d4e5-44c1-b9af-e7794fde4931 |  | Status | 30 | DirectOperate | SingleBit | 2122 | FALSE | FALSE | 5 | SingleCoord | 2103 | ClosePulseOn | 0
GTD_BC2_52-17_DJF1 |  | DISJUNTOR NF | f683d6c6-1746-43be-93b1-178a91c4bdc0 | SwitchStatus | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SC_USO_BC | 2 |  | UTR_GTD_1 | GTD_BC2_52-17_DJF1 |  | 671fd2a7-2f9c-42db-a1e5-f71efe283f80 |  | Status | 30 | DirectOperate | MultiCoord | 2200;2201 | FALSE | FALSE | 5 | SingleCoord | 2200;2200 | TripPulseOn;ClosePulseOn | 0;0
GTD_BC2_52-17_86 |  | 86 | 64933a84-3aa7-4f2b-8d63-a0e9d26b2b20 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | ReadWrite |  | REARMAR@null___NORMAL@ATUADO___Custom_S_TC_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_86 |  | b524e67b-33ba-49ac-9d94-c5bf0ec75184 |  | Status | 30 | DirectOperate | SingleBit | 2222 | FALSE | FALSE | 5 | SingleCoord | 2203 | ClosePulseOn | 0
GTD_BC2_52-17_AUTO |  | AUTOMATISMO | 8cb1f75d-83ac-49a2-a45a-b4e76bec7d46 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS_AUTO | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_AUTO |  | 79890a53-0e50-42ba-aaa2-2b4c1c691152 |  | Status | 30 | DirectOperate | SingleBit | 2220 | FALSE | FALSE | 5 | SingleCoord | 2202;2202 | TripPulseOn;ClosePulseOn | 0;0
GTD_BC4_52-27_AUTO |  | AUTOMATISMO | 08330d34-7207-4cdd-92a5-e45eec5ac922 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS_AUTO | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_AUTO |  | af0ee927-9779-4776-8b1d-fd6cf215a2df |  | Status | 30 | DirectOperate | SingleBit | 3120 | FALSE | FALSE | 5 | SingleCoord | 3102;3102 | TripPulseOn;ClosePulseOn | 0;0
GTD_BC3_52-26_AUTO |  | AUTOMATISMO | 82c81bec-d767-4165-a8f9-6d84542da57e | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Custom___INV_S_TC_SS_AUTO | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_AUTO |  | 02d93aa6-daab-4a86-a2a6-2b4dddd66aa3 |  | Status | 30 | DirectOperate | SingleBit | 3020 | FALSE | FALSE | 5 | SingleCoord | 3002;3002 | TripPulseOn;ClosePulseOn | 0;0
GTD_BC4_52-27_DJF1 |  | DISJUNTOR NF | 379d729b-b07d-4ad7-a70d-884cdc4b1d0a | SwitchStatus | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SC_USO_BC | 2 |  | UTR_GTD_1 | GTD_BC4_52-27_DJF1 |  | a370be0d-2115-4681-8ccb-2711b3616788 |  | Status | 30 | DirectOperate | MultiCoord | 3100;3101 | FALSE | FALSE | 5 | SingleCoord | 3100;3100 | TripPulseOn;ClosePulseOn | 0;0
GTD_BC2_52-17_59 |  | 59 - SOBRETENSAO | b9c89d54-a776-4659-8659-076f4ccb2345 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_59 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_59 |  | 20a56169-c63f-4ca1-82e8-c75850e1f203 |  | Status | 30 | DirectOperate | SingleBit | 2248 | FALSE | FALSE | 5 | SingleCoord | 2204;2204 | ClosePulseOn;TripPulseOn | 0;0
GTD_BC3_52-26_86 |  | 86 | 20b84441-0fd6-495e-a617-5a9cc02d9986 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | ReadWrite |  | REARMAR@null___NORMAL@ATUADO___Custom_S_TC_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_86 |  | 25cfa19b-c723-4167-9f40-d082fac2d382 |  | Status | 30 | DirectOperate | SingleBit | 3022 | FALSE | FALSE | 5 | SingleCoord | 3003 | ClosePulseOn | 0
GTD_BC4_52-27_27 |  | 27 - FUNCAO | 17bddae2-11ff-40dc-b04e-b4bd0f9ec21d | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_27 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_BC4_52-27_27 |  | 1629a497-4dff-431a-9233-0941fbe113cc |  | Status | 30 | DirectOperate | SingleBit | 3138 | FALSE | FALSE | 5 | SingleCoord | 3101;3101 | ClosePulseOn;TripPulseOn | 0;0
GTD_BC3_52-26_59 |  | 59 - SOBRETENSAO | 1a629499-1a66-41a8-b2ac-db69a9dc9ae2 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_59 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_59 |  | 5a4f0eb9-2531-438b-be44-7160aa03e3d5 |  | Status | 30 | DirectOperate | SingleBit | 3048 | FALSE | FALSE | 5 | SingleCoord | 3004;3004 | ClosePulseOn;TripPulseOn | 0;0
GTD_BC3_52-26_27 |  | 27 - FUNCAO | 337511fc-340b-462e-97b2-36f83aa34a59 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_27 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_BC3_52-26_27 |  | 9506c98a-2998-436f-8587-eea7d43763be |  | Status | 30 | DirectOperate | SingleBit | 3038 | FALSE | FALSE | 5 | SingleCoord | 3001;3001 | ClosePulseOn;TripPulseOn | 0;0
GTD_BC2_52-17_27 |  | 27 - FUNCAO | ee1fa165-03ba-4dd7-85c9-78678fab77c9 | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_27 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_BC2_52-17_27 |  | 36ebe843-b5c0-4b60-a742-fb2504f9ca44 |  | Status | 30 | DirectOperate | SingleBit | 2238 | FALSE | FALSE | 5 | SingleCoord | 2201;2201 | ClosePulseOn;TripPulseOn | 0;0
GTD_BC4_52-27_59 |  | 59 - SOBRETENSAO | e636803b-6ebb-4d1b-a67d-b98dec0d8bba | Status | GTD Trans | [6 empty] | GTD_BC1_52-16_PROT_59 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_59 |  | 35938e7a-ec42-43ee-b147-bb832c38bf65 |  | Status | 30 | DirectOperate | SingleBit | 3148 | FALSE | FALSE | 5 | SingleCoord | 3104;3104 | ClosePulseOn;TripPulseOn | 0;0
GTD_BC4_52-27_86 |  | 86 | 6027aa2f-5ece-488c-b7d1-636b04a495a8 | Status | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | Custom | ABC | None | ReadWrite |  | REARMAR@null___NORMAL@ATUADO___Custom_S_TC_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_86 |  | ee64df73-b1a6-47a6-a58c-31312db2652e |  | Status | 30 | DirectOperate | SingleBit | 3122 | FALSE | FALSE | 5 | SingleCoord | 3103 | ClosePulseOn | 0
GTD_BC3_52-26_DJF1 |  | DISJUNTOR NF | d413e04a-ed35-4685-a641-253f22c6203b | SwitchStatus | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SC_USO_BC | 2 |  | UTR_GTD_1 | GTD_BC3_52-26_DJF1 |  | cf0aac9d-f203-4dd5-87fa-0ea02dac5eb0 |  | Status | 30 | DirectOperate | MultiCoord | 3000;3001 | FALSE | FALSE | 5 | SingleCoord | 3000;3000 | TripPulseOn;ClosePulseOn | 0;0
GTD_TR2BT_TR2BT_TPIN |  | TRANSFERENCIA DE PROTECAO | e3783459-cd46-4a13-ac66-bdfa51404171 | Status | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | Custom | ABC | None | Read |  | null@null___COMPLETA@INCOMPLETA___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_TPIN |  | 5b2ab7c8-f041-427a-a0f8-18619e4404b8 | 20260126 | Status |  |  | SingleBit | 957 | FALSE
GTD_TR1AT_TR1AT_TPIN |  | TRANSFERENCIA DE PROTECAO | fca2c170-8f12-4fdd-9a45-25a02d95c923 | Status | GTD Trans | [6 empty] | GTD_TR1AT_52-2_DJ |  | Custom | ABC | None | Read |  | null@null___COMPLETA@INCOMPLETA___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1AT_TR1AT_TPIN |  | ee7ca610-409a-44ef-8477-85fc26cd1fb5 | 20260126 | Status |  |  | SingleBit | 652 | FALSE
GTD_TR1BT_TR1BT_TPIN |  | TRANSFERENCIA DE PROTECAO | 6f44e759-85c4-4df8-b6e3-a1ce7482a21d | Status | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | Custom | ABC | None | Read |  | null@null___COMPLETA@INCOMPLETA___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_TPIN |  | 63f54bdd-4498-42c0-8bd4-2927dea80bf5 | 20260126 | Status |  |  | SingleBit | 657 | FALSE
GTD_TR2AT_TR2AT_MTRF |  | MODULO TRANSFERIDO | 9edac312-4086-4351-b42d-1e3a662642c3 | Status | GTD Trans | [6 empty] | GTD_TR2AT_52-6_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@TRANSFERIDA___Custom_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_TR2AT_TR2AT_MTRF |  | b083cf8f-216e-45c7-8e3c-7ce6460c7883 | 20260126 | Status |  |  | SingleBit | 951 | FALSE
GTD_TR1BT_TR1BT_A_81U1 |  | AJUSTE PARA 81 ESTAGIO 1 | b86e459f-6b49-4134-b7fa-2d06b7ce902e | Status | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_81U1 |  | 5af49fb8-b9a7-43aa-b609-37e1fab9c65d | 20260326 | Status | 30 | DirectOperate | SingleBit | 819 | FALSE | FALSE | 5 | SingleCoord | 609 | ClosePulseOn | 0.25
GTD_TR1BT_TR1BT_A_81U3 |  | AJUSTE PARA 81 ESTAGIO 3 | 2647ca98-e6e2-400d-99b2-09000900a58c | Status | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_81U3 |  | f5bc2839-9624-4cc3-b5e1-53afcfc63f1b | 20260326 | Status | 30 | DirectOperate | SingleBit | 821 | FALSE | FALSE | 5 | SingleCoord | 611 | ClosePulseOn | 0.25
GTD_TR2_TR2_P_87 |  | 87 - FUNCAO DIFERENCIAL | 0ad1bb87-5b73-4674-af39-62f2fa8a26e0 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_PROT_87 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_P_87 |  | 85c17f0c-2fea-4663-9131-e46f9d62552b | 20260326 | Status | 30 | DirectOperate | SingleBit | 997 | FALSE | FALSE | 5 | SingleCoord | 907;907 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TR2BT_TR2BT_A_81U3 |  | AJUSTE PARA 81 ESTAGIO 3 | 63eed126-14f0-44e3-8a2f-969954bb2238 | Status | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_81U3 |  | 1bd88385-01d1-4380-b833-3e697417d527 | 20260326 | Status | 30 | DirectOperate | SingleBit | 1091 | FALSE | FALSE | 5 | SingleCoord | 911 | ClosePulseOn | 0.25
GTD_TR2BT_TR2BT_A_81 |  | 81 - FUNCAO SUB/SOB FREQUENCIA | d6d13b64-a512-4f6f-b7ce-2fb348da40df | Status | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_A_PROT_81 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_81 |  | 284b26dd-4561-4db6-8d9d-061fd405fb81 | 20260326 | Status | 30 | DirectOperate | SingleBit | 1087 | FALSE | FALSE | 5 | SingleCoord | 908;908 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TR2BT_TR2BT_A_81U4 |  | AJUSTE PARA 81 ESTAGIO 4 | 50b78b0c-9d22-4583-9213-90f47a3e54ce | Status | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_81U4 |  | 6f82e63a-b4bb-4cbc-be5e-f75f5c7072ba | 20260326 | Status | 30 | DirectOperate | SingleBit | 1092 | FALSE | FALSE | 5 | SingleCoord | 912 | ClosePulseOn | 0.25
GTD_TR2BT_TR2BT_A_81U1 |  | AJUSTE PARA 81 ESTAGIO 1 | f8d2f0ca-033e-4b2c-9f90-e57d0d5542ce | Status | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_81U1 |  | b240c5d3-ab2a-4ec5-90af-0f24399db9f5 | 20260326 | Status | 30 | DirectOperate | SingleBit | 1089 | FALSE | FALSE | 5 | SingleCoord | 909 | ClosePulseOn | 0.25
GTD_TR1_TR1_P_87 |  | 87 - FUNCAO DIFERENCIAL | c51fdbd8-e7a2-4b13-8951-667fd112543f | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_PROT_87 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_TR1_TR1_P_87 |  | 5bee0d06-028e-400e-b8d0-7845c2407576 | 20260326 | Status | 30 | DirectOperate | SingleBit | 697 | FALSE | FALSE | 5 | SingleCoord | 607;607 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TR1BT_TR1BT_A_81U2 |  | AJUSTE PARA 81 ESTAGIO 2 | ee0b204e-0685-40a2-861b-eb38926a823a | Status | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_81U2 |  | 4524727f-8541-4d14-ac5c-d549c5ab3367 | 20260326 | Status | 30 | DirectOperate | SingleBit | 820 | FALSE | FALSE | 5 | SingleCoord | 610 | ClosePulseOn | 0.25
GTD_TR1BT_TR1BT_A_81 |  | 81 - FUNCAO SUB/SOB FREQUENCIA | db66d26f-8340-4c48-a244-d29070487b68 | Status | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_A_PROT_81 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_81 |  | 8028cb89-93d3-4c70-a00c-1a6974dd67d1 | 20260326 | Status | 30 | DirectOperate | SingleBit | 817 | FALSE | FALSE | 5 | SingleCoord | 608;608 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TR1BT_TR1BT_A_81U4 |  | AJUSTE PARA 81 ESTAGIO 4 | abcd3c1e-128d-4382-bc42-ffb48e9a024a | Status | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_81U4 |  | 16fa4e55-c6cf-4eec-a4a8-e9fbcdbec70f | 20260326 | Status | 30 | DirectOperate | SingleBit | 822 | FALSE | FALSE | 5 | SingleCoord | 612 | ClosePulseOn | 0.25
GTD_TR1_TR1_A_87 |  | 87 - FUNCAO DIFERENCIAL | 6aca1db5-df1f-4fcf-921b-b237a04a88db | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_PROT_87 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_GTD_1 | GTD_TR1_TR1_A_87 |  | 27fb2325-688a-4865-b738-116e08835864 | 20260326 | Status | 30 | DirectOperate | SingleBit | 787 | FALSE | FALSE | 5 | SingleCoord | 614;614 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TR2_TR2_A_87 |  | 87 - FUNCAO DIFERENCIAL | daa34e0f-2a29-4bfb-a9d3-5edd6fd5f9d3 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_PROT_87 |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_A_87 |  | d0d212fe-89cd-453b-9448-9decb841634a | 20260326 | Status | 30 | DirectOperate | SingleBit | 1057 | FALSE | FALSE | 5 | SingleCoord | 914;914 | ClosePulseOn;TripPulseOn | 0.25;0.25
GTD_TR2BT_TR2BT_A_81U2 |  | AJUSTE PARA 81 ESTAGIO 2 | 75ca0276-035c-459e-8102-a4a34949c9d8 | Status | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_81U2 |  | 2e463fae-42d8-453c-b873-18af81b483a6 | 20260326 | Status | 30 | DirectOperate | SingleBit | 1090 | FALSE | FALSE | 5 | SingleCoord | 910 | ClosePulseOn | 0.25
GTD_TR2BT_TR2BT_A_81U5 |  | AJUSTE PARA 81 ESTAGIO 5 | a16ab19c-dee9-45fa-901d-658b0de22b5d | Status | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TR2BT_TR2BT_A_81U5 |  | 903045fa-2a13-441f-ad38-e04c65842d30 | 20260326 | Status | 30 | DirectOperate | SingleBit | 1093 | FALSE | FALSE | 5 | SingleCoord | 913 | ClosePulseOn | 0.25
GTD_TR1BT_TR1BT_A_81U5 |  | AJUSTE PARA 81 ESTAGIO 5 | 696bb9f6-36e3-46fc-9091-4a557c9a582f | Status | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TR1BT_TR1BT_A_81U5 |  | 4cb0924d-7e7d-4702-9de5-89cc3ca61d4e | 20260326 | Status | 30 | DirectOperate | SingleBit | 823 | FALSE | FALSE | 5 | SingleCoord | 613 | ClosePulseOn | 0.25
GTD_BP2_BP2_86BF |  | 86BF | b745b1f1-4b3f-4276-aec8-d1a69521375a | Status | GTD Trans | [6 empty] | ARV_BP2_BP2_BP |  | Custom | ABC | None | ReadWrite |  | REARMAR@null___NORMAL@ATUADO___Custom_S_TC_SA | 1 |  | UTR_GTD_1 | GTD_BP2_BP2_86BF |  | 312612f7-c660-4843-9a07-78d35084251d | 20260327 | Status | 30 | DirectOperate | SingleBit | 1202 | FALSE | FALSE | 5 | SingleCoord | 1272 | ClosePulseOn | 0
GTD_BP1_BP1_86BF |  | 86BF | 57916990-f2cb-4614-9e68-9f7b94d562e0 | Status | GTD Trans | [6 empty] | ARV_BP1_BP1_BP |  | Custom | ABC | None | ReadWrite |  | REARMAR@null___NORMAL@ATUADO___Custom_S_TC_SA | 1 |  | UTR_GTD_1 | GTD_BP1_BP1_86BF |  | fffd2072-1ce1-4396-bc67-233359e94685 | 20260327 | Status | 30 | DirectOperate | SingleBit | 1201 | FALSE | FALSE | 5 | SingleCoord | 1271 | ClosePulseOn | 0
GTD_B69_B69_86BF |  | 86BF | 03c5b711-0161-447a-b1bf-6a3ed3599114 | Status | GTD Trans | [6 empty] | ARV_B69_B69_BP |  | Custom | ABC | None | ReadWrite |  | REARMAR@null___NORMAL@ATUADO___Custom_S_TC_SA | 1 |  | UTR_GTD_1 | GTD_B69_B69_86BF |  | 13c3765b-3f17-4969-9e59-71e8c897e19c | 20260327 | Status | 30 | DirectOperate | SingleBit | 1200 | FALSE | FALSE | 5 | SingleCoord | 1270 | ClosePulseOn | 0
GTD_IB_52-18_FB |  | FASE B | c97e3a3c-04fc-4c50-8438-9975297e4637 | Status | GTD Trans | [6 empty] | GTD_IB_52-160_PROT_FB |  | RelayTrip | B | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_FB |  | 55f29920-328c-4316-acad-687c5d5b0de1 |  | Status |  |  | SingleBit | 2324 | FALSE
GTD_IB_52-18_PERP |  | PERMISSAO PARALELISMO | 7e76cde9-eafb-427a-bf26-89400e9672d5 | Status | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | Custom | ABC | None | Read |  | null@null___NÃO PERMITIDO@PERMITIDO___Custom_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_IB_52-18_PERP |  | 21d1cb2d-c670-4e40-a201-3843b815e9b5 |  | Status |  |  | SingleBit | 2319 | FALSE
GTD_IB_52-18_62BF |  | 62BF | a90bc6b5-0e9f-4460-beff-655fdc556ccd | Status | GTD Trans | [6 empty] | GTD_IB_52-160_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_62BF |  | 4b7ff006-252d-4206-85e8-1c58d0e4ccc0 |  | Status |  |  | SingleBit | 2322 | FALSE
GTD_IB_52-18_43TC |  | 43TC | a908f3a6-04e2-446b-a3fa-43165c1357a0 | Status | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_IB_52-18_43TC |  | 586f361d-2e84-4a46-8d41-5b84b4dd1d43 |  | Status |  |  | SingleBit | 2315 | FALSE
GTD_IB_52-18_MOLA |  | MOLA | d56c7a51-f54d-4f78-91c6-9814ea351129 | Status | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_IB_52-18_MOLA |  | b9dd88a7-25f8-49a0-aacd-2e6b01979436 |  | Status |  |  | SingleBit | 2303 | FALSE
GTD_IB_52-18_81E1 |  | 81 ESTAGIO 1 | 5f405a6f-14cc-438f-b5f4-dbc4ef020f2c | Status | GTD Trans | [6 empty] | IVB_AL21_52-21_PROT_81E1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_81E1 |  | 6d56add6-2697-4568-8c19-4de03d0fc4f8 |  | Status |  |  | SingleBit | 2343 | FALSE
GTD_IB_52-18_81E2 |  | 81 ESTAGIO 2 | e7289aa2-446b-4d7d-bc8c-01a9014becc4 | Status | GTD Trans | [6 empty] | IVB_AL21_52-21_PROT_81E2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_81E2 |  | 5fa5b552-139a-4ee6-9a6d-8ba889412acb |  | Status |  |  | SingleBit | 2344 | FALSE
GTD_IB_52-18_46 |  | 46 | d9ce0ddd-9af7-451d-b895-775ef6476b58 | Status | GTD Trans | [6 empty] | IVB_AL21_52-21_PROT_46 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_46 |  | e2c91ea3-fc70-43b5-a8d7-475e3b8706dd |  | Status |  |  | SingleBit | 2342 | FALSE
GTD_IB_52-18_FUTP |  | FALHA CIRCUITO TP | e7fb5549-6fff-4cf7-8744-ed1fe0d94b7f | Status | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_IB_52-18_FUTP |  | 6f6f63e8-7336-408b-9b1d-caa72defe836 |  | Status |  |  | SingleBit | 2345 | FALSE
GTD_IB_52-18_BBA1 |  | BOB AB 1 | 4b8c07b5-2ef6-487c-9a08-cf121a468276 | Status | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_IB_52-18_BBA1 |  | bd1c0559-cd8b-4e11-b757-50f53346bc8e |  | Status |  |  | SingleBit | 2309 | FALSE
GTD_IB_52-18_CCCO |  | FALTA VCC COMANDO | da376d14-50ee-48aa-935e-042745858cbd | Status | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_IB_52-18_CCCO |  | b09eefc6-49f3-433b-bef6-79d9791c577b |  | Status |  |  | SingleBit | 2307 | FALSE
GTD_IB_52-18_50N2 |  | 50N 2 | 4d199175-e96d-47f8-ace3-432f33c218f9 | Status | GTD Trans | [6 empty] | IVB_AL21_52-21_PROT_50N2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_50N2 |  | c0afe428-6e46-4b0c-84d0-c261cf8c1a68 |  | Status |  |  | SingleBit | 2331 | FALSE
GTD_IB_52-18_GOOS |  | FALHA GOOSE | 3fdc50e2-ea86-4a4f-afac-fc3662eefccf | Status | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_IB_52-18_GOOS |  | f56ab584-a491-4019-bc44-2853156ed902 |  | Status |  |  | SingleBit | 2316 | FALSE
GTD_IB_52-18_FSIN |  | FALHA SINCRONISMO IRIG-B | ae98e466-ae03-49c1-bbda-59eb72071a5f | Status | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_IB_52-18_FSIN |  | 772e189c-f316-4782-840a-5cd7a03cbc72 |  | Status |  |  | SingleBit | 2318 | FALSE
GTD_IB_52-18_67NTD |  | 67 - DIRECIONAL SOBRECORRENTE DIRETO NEUTRO TEMPORIZADA | 0a8e1abd-bc21-4dae-a113-9231c729e311 | Status | GTD Trans | [6 empty] | GTD_IB_52-160_PROT_67NTD |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_67NTD |  | a55d2ea3-dbcf-4410-bfd3-4f19a174417c | 20260401 | Status |  |  | SingleBit | 2336 | FALSE
GTD_IB_52-18_67NTR |  | 67 - DIRECIONAL SOBRECORRENTE REVERSO NEUTRO TEMPORIZADA | e0f50e34-29c4-4269-8594-51f9d6d87a42 | Status | GTD Trans | [6 empty] | GTD_IB_52-160_PROT_67NTR |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_67NTR |  | 0bfa28cb-ed83-4c74-a2e2-f7dced624303 | 20260401 | Status |  |  | SingleBit | 2340 | FALSE
GTD_IB_52-18_67FTD |  | 67 - DIRECIONAL SOBRECORRENTE DIRETO FASE TEMPORIZADA | 66326b0f-3e1e-4131-a0af-1e0146719c6d | Status | GTD Trans | [6 empty] | SBB_IB_24-2_PROT_67T1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_67FTD |  | ccbfeb11-3853-4be9-86bc-047b17a95142 | 20260401 | Status |  |  | SingleBit | 2334 | FALSE
GTD_IB_52-18_67FTR |  | 67 - DIRECIONAL SOBRECORRENTE REVERSO FASE TEMPORIZADA | 4a311612-7020-4d4f-a6cb-d1bcc186ecb2 | Status | GTD Trans | [6 empty] | GTD_IB_52-160_PROT_67FTR |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_67FTR |  | d5d7af66-345f-4807-b3b9-8078c1d3dc81 |  | Status |  |  | SingleBit | 2338 | FALSE
GTD_IB_52-18_67FR |  | 67 - DIRECIONAL SOBRECORRENTE REVERSO FASE | 00371556-c1be-47db-8cc9-2e210dc95279 | Status | GTD Trans | [6 empty] | GTD_IB_52-160_PROT_67FR |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_67FR |  | c8f92694-8b16-42c7-8f5c-fabafa8c267a | 20260401 | Status |  |  | SingleBit | 2337 | FALSE
GTD_IB_52-18_CCMO |  | FALTA VCC MOTOR | 30192a14-0aaa-4803-a7b6-5229eb600f60 | Status | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_IB_52-18_CCMO |  | 49ded81d-55a0-4010-963b-8a4f0655dca7 |  | Status |  |  | SingleBit | 2306 | FALSE
GTD_IB_52-18_67ND |  | 67 - DIRECIONAL SOBRECORRENTE DIRETO NEUTRO | fc549511-7e8f-4937-b1c0-50b37192d302 | Status | GTD Trans | [6 empty] | GTD_IB_52-160_PROT_67ND |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_67ND |  | edbe263e-8df9-40af-9e7d-6d123baa6b1f | 20260401 | Status |  |  | SingleBit | 2335 | FALSE
GTD_IB_52-18_FCOM |  | COMUNIC | 6f9e99f7-5d4d-4f36-8abf-c3a064703e6b | Status | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_IB_52-18_FCOM |  | 29d04343-cf12-45dd-bff0-bcd2316b8c7b |  | Status |  |  | SingleBit | 2321 | FALSE
GTD_IB_52-18_SGFT |  | SGF_TRIP | be20ec36-a872-4854-97cf-43a05b3c49b2 | Status | GTD Trans | [6 empty] | IVB_AL21_52-21_PROT_SGFT |  | Enabled | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_SGFT |  | f8659512-4964-49d6-803d-5c1030233ec9 |  | Status |  |  | SingleBit | 2341 | FALSE
GTD_IB_52-18_TEXT |  | TRIP EXTERNO | 4d47bb90-1e81-42b9-a366-f10aca6bb76a | Status | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_IB_52-18_TEXT |  | 200488c9-ff0a-40a3-8f32-162ea0335189 |  | Status |  |  | SingleBit | 2346 | FALSE
GTD_IB_52-18_BBFC |  | BOB FEC | 6479bd58-101d-453a-8200-9d27c770c611 | Status | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_IB_52-18_BBFC |  | 113ed9ee-ed43-418f-903f-20014e56b6e2 |  | Status |  |  | SingleBit | 2308 | FALSE
GTD_IB_52-18_50N1 |  | 50N 1 | 25fd811b-8502-421a-bf1e-5f541c76e07d | Status | GTD Trans | [6 empty] | IVB_AL21_52-21_PROT_50N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_50N1 |  | 6372333d-07b8-47dd-a1d4-a8c50689fb5f |  | Status |  |  | SingleBit | 2330 | FALSE
GTD_IB_52-18_67NR |  | 67 - DIRECIONAL SOBRECORRENTE REVERSO NEUTRO | 05919634-ece9-4810-a893-62f17f1569c0 | Status | GTD Trans | [6 empty] | GTD_IB_52-160_PROT_67NR |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_67NR |  | 0d5620b5-a9e8-4410-95e6-703df918cf3e | 20260401 | Status |  |  | SingleBit | 2339 | FALSE
GTD_IB_52-18_67FD |  | 67 - DIRECIONAL SOBRECORRENTE DIRETO FASE | 146cf471-1ef0-4d63-a5b9-c7c3ab27f644 | Status | GTD Trans | [6 empty] | GTD_IB_52-160_PROT_67FD |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_67FD |  | 21f0bd4a-a086-4b6a-89ae-decaa52139a4 | 20260401 | Status |  |  | SingleBit | 2333 | FALSE
GTD_IB_52-18_FC |  | FASE C | 7abad8b1-3d03-4a84-8d7a-248e0d53b32d | Status | GTD Trans | [6 empty] | GTD_IB_52-160_PROT_FC |  | RelayTrip | C | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_FC |  | 610b2b98-fbbd-453f-9e8a-2066ecc73767 |  | Status |  |  | SingleBit | 2325 | FALSE
GTD_IB_52-18_BBA2 |  | BOB AB 2 | 6994335a-d2bc-4624-aa6f-e02c907d4f49 | Status | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_IB_52-18_BBA2 |  | 5a8ed262-39b0-4cb1-8a48-4ee1d9d8f116 |  | Status |  |  | SingleBit | 2310 | FALSE
GTD_IB_52-18_43LR |  | 43LR | 9de106f9-e2f3-4530-beac-9b9649f4ef1b | Status | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_IB_52-18_43LR |  | 219c08c2-b6a8-4689-93a8-87df6b9137df |  | Status |  |  | SingleBit | 2304 | FALSE
GTD_IB_52-18_DR |  | RELE | 53dfb87d-c6a4-4f3e-baca-3b6a2c42d2dc | Status | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_IB_52-18_DR |  | 9f6cfc91-658b-4b0e-bed9-4b1dc8b418ba |  | Status |  |  | SingleBit | 2320 | FALSE
GTD_IB_52-18_50F2 |  | 50F 2 | f11d0a41-b864-4de0-bee6-df62de0a242b | Status | GTD Trans | [6 empty] | IVB_AL21_52-21_PROT_50F2 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_50F2 |  | a2dddaa3-e8f8-4349-a6e8-6750b1b34b4e |  | Status |  |  | SingleBit | 2328 | FALSE
GTD_IB_52-18_50F1 |  | 50F 1 | 389ecc7b-44ec-4011-8ea5-237095b42743 | Status | GTD Trans | [6 empty] | IVB_AL21_52-21_PROT_50F1 |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_IB_52-18_50F1 |  | c01a5bdc-9302-4184-83d8-d0dbbd3d925f |  | Status |  |  | SingleBit | 2327 | FALSE
GTD_IB_52-18_DJF1 |  | DISJUNTOR NF | 1593c518-2253-459f-adde-b0c86a7cf419 | SwitchStatus | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 1 |  | UTR_GTD_1 | GTD_IB_52-18_DJF1 |  | 674d2aad-70fb-46a5-a703-934afe6a751e |  | Status | 30 | DirectOperate | MultiCoord | 2300;2301 | FALSE | FALSE | 5 | SingleCoord | 2300;2300 | TripPulseOn;ClosePulseOn | 0;0
GTD_AL11_52-11_81BLOQ |  | 81 BLOQUEIO DINAMICO | f273e2f3-9e5a-40a5-a397-d7106ef1df9b | Status | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | Custom | ABC | None | Read |  | null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_AL11_52-11_81BLOQ |  | 86f908d5-be50-4996-8086-444cb4b49f30 | 20260330 | Status |  |  | SingleBit | 1538 | FALSE
GTD_AL14_52-14_81BLOQ |  | 81 BLOQUEIO DINAMICO | c9d7ac66-9a10-4b5a-9231-326cd7fa3b2f | Status | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | Custom | ABC | None | Read |  | null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_AL14_52-14_81BLOQ |  | 0839c7ec-ee5e-4217-a77e-da341ff41fe0 | 20260330 | Status |  |  | SingleBit | 1838 | FALSE
GTD_TRF1_24-1_81BLOQ |  | 81 BLOQUEIO DINAMICO | b9ea6b0d-f95a-4e41-9b8f-7e2539cf125b | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | Read |  | null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_TRF1_24-1_81BLOQ |  | 7b5115ed-3498-44b6-bd70-4f722bb3c333 | 20260330 | Status |  |  | SingleBit | 2041 | FALSE
GTD_AL24_52-24_81BLOQ |  | 81 BLOQUEIO DINAMICO | a8d52679-2aa4-4a9c-a254-bdbf29b638b4 | Status | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | Custom | ABC | None | Read |  | null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_AL24_52-24_81BLOQ |  | e7659d33-25d2-4fc4-9854-f8a4ee006131 | 20260204 | Status |  |  | SingleBit | 2738 | FALSE
GTD_AL23_52-23_81BLOQ |  | 81 BLOQUEIO DINAMICO | 3aff1c82-b0f0-449e-bec7-e6ac78cf563c | Status | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | Custom | ABC | None | Read |  | null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_AL23_52-23_81BLOQ |  | bcb383c8-5a34-40dd-b6a7-427eed4eefaa | 20260204 | Status |  |  | SingleBit | 2638 | FALSE
GTD_AL25_52-25_81BLOQ |  | 81 BLOQUEIO DINAMICO | eac49e7e-1531-45fb-af44-91cb47ff510a | Status | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | Custom | ABC | None | Read |  | null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_AL25_52-25_81BLOQ |  | 12d3700b-af30-45b0-897b-9dc71823dab9 | 20260204 | Status |  |  | SingleBit | 2838 | FALSE
GTD_TRF2_24-2_81BLOQ |  | 81 BLOQUEIO DINAMICO | 6ca14de5-e693-4a0e-82ba-fbce01b7247a | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | Read |  | null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_TRF2_24-2_81BLOQ |  | 3176c6f2-1606-4991-a625-013ebabd1779 | 20260204 | Status |  |  | SingleBit | 2941 | FALSE
GTD_AL12_52-12_81BLOQ |  | 81 BLOQUEIO DINAMICO | d9f67099-16ec-4e74-86ce-92fc4bed9f8e | Status | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | Custom | ABC | None | Read |  | null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_AL12_52-12_81BLOQ |  | 281bd3fc-1a8e-4f4c-a2b4-89a47f1eb9db | 20260330 | Status |  |  | SingleBit | 1638 | FALSE
GTD_AL15_52-15_81BLOQ |  | 81 BLOQUEIO DINAMICO | 9bc5c061-6d56-40a2-99e3-72db9d81ea1e | Status | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | Custom | ABC | None | Read |  | null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_AL15_52-15_81BLOQ |  | 4dc5c377-9de6-4cb6-9494-1676c066e11a | 20260330 | Status |  |  | SingleBit | 1938 | FALSE
GTD_AL22_52-22_81BLOQ |  | 81 BLOQUEIO DINAMICO | c4ef9b01-e42e-4094-a436-d7438f548377 | Status | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | Custom | ABC | None | Read |  | null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_AL22_52-22_81BLOQ |  | d25fa7d8-89cd-433e-8432-68d20d208a03 | 20260204 | Status |  |  | SingleBit | 2539 | FALSE
GTD_AL13_52-13_81BLOQ |  | 81 BLOQUEIO DINAMICO | 0e86fa66-8305-4835-84f2-1590ff5091f6 | Status | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___BLOQUEADA@LIBERADA___Custom___INV_S_TS_SS | 2 |  | UTR_GTD_1 | GTD_AL13_52-13_81BLOQ |  | 4b8df439-6c90-4042-85e5-278d11b8240d | 20260330 | Status |  |  | SingleBit | 1738 | FALSE
GTD_TR2_TR2_CDLM |  | CDC LOCAL MANUAL | e6697c78-feb9-4ce7-a524-8d78fa566d74 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___MANUAL DESATIVOU@MANUAL ATIVOU___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_CDLM |  | e049c9a8-00e4-489f-9f03-40b8b1af9b10 | 20260331 | Status |  |  | SingleBit | 994 | FALSE
GTD_TR2_TR2_CDLA |  | CDC LOCAL AUTOMATICO | 807d2314-b256-4096-84b4-6411902aa796 | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___AUTOM DESATIVADO@AUTOM ATIVOU___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_CDLA |  | 5c006e7b-e63e-4089-b436-9dadedf265e6 | 20260331 | Status |  |  | SingleBit | 995 | FALSE
GTD_TR1_TR1_CDLM |  | CDC LOCAL MANUAL | 4cffa2ba-03c3-4ef2-a0b0-d95b489ff952 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___MANUAL DESATIVOU@MANUAL ATIVOU___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_CDLM |  | f59a95de-59c0-4315-968f-cabf5f8743f6 | 20260331 | Status |  |  | SingleBit | 694 | FALSE
GTD_TR1_TR1_CDLA |  | CDC LOCAL AUTOMATICO | 793913aa-0c6b-4b29-8c86-4b9654d79572 | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___AUTOM DESATIVADO@AUTOM ATIVOU___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_CDLA |  | e4b27999-9e0d-42f4-abcd-a379d945767e | 20260331 | Status |  |  | SingleBit | 695 | FALSE
GTD_TR1_TR1_CDRA |  | CDC REMOTO AUTOMATICO | 2a27ddb4-1ead-4543-bd13-d968569411bb | Status | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | None | Read |  | null@null___AUTOM DESATIVADO@AUTOM ATIVOU___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TR1_TR1_CDRA |  | 0ae8d175-c39e-4ede-be74-dfba6cd0f526 | 20260331 | Status |  |  | SingleBit | 696 | FALSE
GTD_TR2_TR2_CDRA |  | CDC REMOTO AUTOMATICO | f3783ee3-8f72-4f58-b2e2-907f6424f31a | Status | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | None | Read |  | null@null___AUTOM DESATIVADO@AUTOM ATIVOU___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TR2_TR2_CDRA |  | 40da75f5-7974-46ea-8546-ec132341f577 | 20260331 | Status |  |  | SingleBit | 996 | FALSE
GTD_TRF1_24-1_MDBP |  | DJAUX BARRA P | df275611-fa62-4dff-83ae-93515f57d9af | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | Read |  | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_MDBP |  | 836c66ee-8626-466d-8633-166899e6e5bf | 20230401 | Status |  |  | SingleBit | 2022 | FALSE
GTD_BC2_52-17_61_2 |  | 61 - DESEQUILIBRIO E2 | f20a6c9a-a77a-4122-9d48-bf2ceef78f72 | Status | GTD Trans | [6 empty] | GTD_BC2_52-17_PROT_61_2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_61_2 |  | 67eb4cf8-ca90-4e65-80b2-0f47ca4e048f | 20260401 | Status |  |  | SingleBit | 2237 | FALSE
GTD_BC2_52-17_61_1 |  | 61 - DESEQUILIBRIO E1 | 2416fc17-05f3-4aad-b7fe-71efff353d66 | Status | GTD Trans | [6 empty] | GTD_BC2_52-17_PROT_61_1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC2_52-17_61_1 |  | bee9a159-9334-4d83-a2ea-0ae197a3ce3a | 20260401 | Status |  |  | SingleBit | 2236 | FALSE
GTD_BC4_52-27_61_2 |  | 61 - DESEQUILIBRIO E2 | 035113f9-6d89-47a2-adc8-4e18dd2d6be4 | Status | GTD Trans | [6 empty] | GTD_BC4_52-27_PROT_61_2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_61_2 |  | facc7cbb-28c0-4ec8-aff4-8a8da87ad791 | 20260401 | Status |  |  | SingleBit | 3137 | FALSE
GTD_BC4_52-27_61_1 |  | 61 - DESEQUILIBRIO E1 | 17d17a0f-cc4b-4378-95f0-c97511946bc3 | Status | GTD Trans | [6 empty] | GTD_BC4_52-27_PROT_61_1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC4_52-27_61_1 |  | 05fd2a39-dd1f-4118-9af4-2c94f88b6bce | 20260401 | Status |  |  | SingleBit | 3136 | FALSE
GTD_BC1_52-16_61_2 |  | 61 - DESEQUILIBRIO E2 | f128f1bb-d37d-4f24-8ab4-c06428fa1621 | Status | GTD Trans | [6 empty] | GTD_BC3_52-26_PROT_61_2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_61_2 |  | 0d4eb382-b59e-4d9d-9404-faea71dfc512 | 20260401 | Status |  |  | SingleBit | 2137 | FALSE
GTD_BC3_52-26_61_2 |  | 61 - DESEQUILIBRIO E2 | b308ae8c-015d-4b9e-b55a-60336a915f23 | Status | GTD Trans | [6 empty] | GTD_BC3_52-26_PROT_61_2 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC3_52-26_61_2 |  | f6a41028-b544-44b5-af6c-52f79e224c9f | 20260401 | Status |  |  | SingleBit | 3037 | FALSE
GTD_TRF2_24-2_MDBP |  | DJAUX BARRA P | 9aa65b39-0063-4042-ba42-37e240f85d10 | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | Read |  | null@null___LIGADO@DESLIGADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_MDBP |  | aa003fe8-07e5-40cf-a238-580501d5e60c | 20230401 | Status |  |  | SingleBit | 2922 | FALSE
GTD_BC1_52-16_61_1 |  | 61 - DESEQUILIBRIO E1 | f18e0bbd-734b-4b34-b342-88d3644f646f | Status | GTD Trans | [6 empty] | SIA_BC1_52-5_PROT_61_1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_GTD_1 | GTD_BC1_52-16_61_1 |  | 8ff0ee59-0499-48ce-8127-b53ecaaf4019 |  | Status |  |  | SingleBit | 2136 | FALSE
GTD_TRF1_24-1_AJG2 |  | AJUSTE PARA GRUPO 2 | db64b283-cb32-4d0c-baae-c579d4d78a4f | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_AJG2 |  | 35da635f-8d42-44b3-9221-d7aaa5c824c1 | 20260401 | Status | 30 | DirectOperate | SingleBit | 2021 | FALSE | FALSE | 5 | SingleCoord | 2012 | ClosePulseOn | 0
GTD_TRF2_24-2_AJG2 |  | AJUSTE PARA GRUPO 2 | fad60033-275d-4458-bac7-096fb97b3ee2 | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_AJG2 |  | 0a9664c5-4dec-44af-b904-9477e027de3e | 20260401 | Status | 30 | DirectOperate | SingleBit | 2921 | FALSE | FALSE | 5 | SingleCoord | 2912 | ClosePulseOn | 0
GTD_TRF1_24-1_AJG3 |  | AJUSTE PARA GRUPO 3 | bba87001-a18e-4095-ab25-c84b073aacf8 | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_AJG3 |  | 27d484ff-bf34-41cd-b4f5-8fb9133856c5 | 20260401 | Status | 30 | DirectOperate | SingleBit | 2061 | FALSE | FALSE | 5 | SingleCoord | 2013 | ClosePulseOn | 0
GTD_TRF1_24-1_AJG4 |  | AJUSTE PARA GRUPO 4 | 8332ee63-44ec-4a77-8d97-d668654066ba | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_AJG4 |  | 98b91d98-f05e-48c6-b0dc-f2e05a7bcbc3 | 20260401 | Status | 30 | DirectOperate | SingleBit | 2062 | FALSE | FALSE | 5 | SingleCoord | 2014 | ClosePulseOn | 0
GTD_TRF1_24-1_AJG1 |  | AJUSTE PARA GRUPO 1 | 479f7bbd-e9a3-4ce9-b72f-ed3ea61bf012 | Status | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF1_24-1_AJG1 |  | 3f335c93-fe37-415d-a35f-365d98e723e1 | 20260401 | Status | 30 | DirectOperate | SingleBit | 2020 | FALSE | FALSE | 5 | SingleCoord | 2011 | ClosePulseOn | 0
GTD_TRF2_24-2_AJG1 |  | AJUSTE PARA GRUPO 1 | 31941deb-133e-4189-a1af-342b8f5b49fa | Status | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_GTD_1 | GTD_TRF2_24-2_AJG1 |  | 654f648c-c100-4d02-828a-a57a815ac4f7 | 20260401 | Status | 30 | DirectOperate | SingleBit | 2920 | FALSE | FALSE | 5 | SingleCoord | 2911 | ClosePulseOn | 0
GTD_SE_PTEL_DCMD |  | DEFEITO EQUIPAMENTOS | 81aae43d-d3f7-4276-8825-7a52250c8eaf | Status | GTD Trans | [8 empty] | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_SE_PTEL_DCMD |  | bf674492-a9d0-4bd9-a4fb-77faadfd87da | 20260408 | Status |  |  | SingleBit | 3448 | FALSE
GTD_SE_PATIO_CAAQ |  | FALTA VCA AQUECIMENTO E ILUMINACAO | d1b3f296-ef9a-40a0-93e0-93ff559c1a11 | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_SE_PATIO_CAAQ |  | 6171cd74-d9e7-4c79-b196-754455279002 | 20260408 | Status |  |  | SingleBit | 3434 | FALSE
GTD_SE_PCFTV_DCMD |  | DEFEITO EQUIPAMENTOS | ba609e29-74fe-4db6-a9cf-07b524bb69a3 | Status | GTD Trans | [8 empty] | Custom | ABC | None | Read |  | null@null___NORMAL@DEFEITO___Custom_S_TS_SI | 1 |  | UTR_GTD_1 | GTD_SE_PCFTV_DCMD |  | 240b6cb1-c4d0-44c9-bb20-67d1c1270f53 | 20260408 | Status |  |  | SingleBit | 3445 | FALSE
GTD_SE_PTEL_CCFL |  | FALTA VCC | 2adb9f46-1b19-4bd1-9ae5-4d8ec791a941 | Status | GTD Trans | [8 empty] | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_SE_PTEL_CCFL |  | 5f6d7c8c-b714-4bc5-97cf-84029833fac3 | 20260408 | Status |  |  | SingleBit | 3447 | FALSE
GTD_TSA_TSA_43TC |  | 43TC | fa5aa168-3c21-446c-829f-bd2f32b50740 | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Custom_S_TS_SS | 1 |  | UTR_GTD_1 | GTD_TSA_TSA_43TC |  | f803ea62-ed25-437a-af68-dbc26b9f845e | 20260408 | Status |  |  | SingleBit | 3404 | FALSE
GTD_TSA_TSA_FCOM |  | COMUNIC | 78e0dcad-2126-451f-8996-a1f5768a2334 | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TSA_TSA_FCOM |  | 2c96d1ce-f9a8-496f-952e-2144ce038d6e | 20260408 | Status |  |  | SingleBit | 3416 | FALSE
GTD_SE_RET1_CCLO |  | VCC BAIXA | 58c0d19f-3d47-4d70-9083-d480df6722d8 | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_SE_RET1_CCLO |  | 5047a468-cb89-4f10-b37f-7bb72810bea9 | 20260408 | Status |  |  | SingleBit | 3420 | FALSE
GTD_TSA_CC_E1_FGTE |  | FUGA TERRA | e76df6ba-19d8-48ec-b218-cf4020a3202f | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TSA_CC_E1_FGTE |  | 7f6447f1-ed5d-456a-be01-66fe9b4281a0 | 20260407 | Status |  |  | SingleBit | 3417 | FALSE
GTD_SE_PCFTV_ALM |  | ALARME GERAL | a460f9dd-56fc-4c12-8d70-c10ba99b79ff | Status | GTD Trans | [8 empty] | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SP | 1 |  | UTR_GTD_1 | GTD_SE_PCFTV_ALM |  | 6e62db4a-04d2-40f0-8564-06f6770f654b | 20260408 | Status |  |  | SingleBit | 3446 | FALSE
GTD_SE_SALA_CAAQ |  | FALTA VCA AQUECIMENTO E ILUMINACAO | 75b939c5-26e5-4159-8c32-9ad506ee0a37 | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_SE_SALA_CAAQ |  | 83167565-64b0-4a6d-8bff-02b7c3962673 | 20260408 | Status |  |  | SingleBit | 3435 | FALSE
GTD_SE_SE_PRIN |  | ALARME PREDIAL PRESENCA INTERNA | d4c54489-657f-44f7-87a3-467724c32d76 | Status | GTA Trans | [8 empty] | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SP | 1 |  | UTR_GTD_1 | GTD_SE_SE_PRIN |  | 7bdc1c6e-f74d-4188-aa61-153dab06153d | 20260408 | Status |  |  | SingleBit | 3438 | FALSE
GTD_TSA_CC_E2_FGTE |  | FUGA TERRA | beb0d201-6670-4055-8f17-7304830bd79a | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_TSA_CC_E2_FGTE |  | b0f7264b-a47a-482a-8284-8afbc1900317 | 20260407 | Status |  |  | SingleBit | 3418 | FALSE
GTD_SE_RET1_EST |  | ESTADO | 7a522ce2-c29b-48c5-9912-815ffc3d815c | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___DESLIGADO@LIGADO___SwitchStatus_S_TS | 2 |  | UTR_GTD_1 | GTD_SE_RET1_EST |  | c50569b5-bce7-4d47-8219-60fe6848d689 | 20260408 | Status |  |  | SingleBit | 3421 | FALSE
GTD_SE_RET2_EST |  | ESTADO | a24fe3c1-2e44-4247-9de6-9f5122de0911 | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___DESLIGADO@LIGADO___SwitchStatus_S_TS | 2 |  | UTR_GTD_1 | GTD_SE_RET2_EST |  | 81e52b05-0c51-4dcf-9e14-81b15d28eb4e | 20260408 | Status |  |  | SingleBit | 3426 | FALSE
GTD_SE_SE_PREX |  | ALARME PREDIAL PRESENCA EXTERNA | a368737e-e0f1-4b25-9b88-b0055478773b | Status | GTA Trans | [8 empty] | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SP | 1 |  | UTR_GTD_1 | GTD_SE_SE_PREX |  | b17a23fb-c8f7-4ffe-949e-b8c53b84dabc | 20260408 | Status |  |  | SingleBit | 3437 | FALSE
GTD_SE_PTEL_ALM |  | ALARME GERAL | 6e995617-77f2-45ff-989f-d53c913bd3e6 | Status | GTD Trans | [8 empty] | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SP | 1 |  | UTR_GTD_1 | GTD_SE_PTEL_ALM |  | ffc57744-0134-4483-aaad-9382baf340b4 | 20260408 | Status |  |  | SingleBit | 3449 | FALSE
GTD_SE_SE_FUMA |  | SENSOR FUMACA | 3aebcc61-8db9-4580-a2f9-cb7d23b92d56 | Status | GTA Trans | [8 empty] | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SP | 1 |  | UTR_GTD_1 | GTD_SE_SE_FUMA |  | c19bd17f-9939-49d9-abf6-6e0ce9f0bd1c | 20260408 | Status |  |  | SingleBit | 3436 | FALSE
GTD_SE_RET2_BATL |  | TENSAO BAIXA BATERIA | 36687448-2a53-49cc-bdf7-197046d06c07 | Status | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_GTD_1 | GTD_SE_RET2_BATL |  | aa059388-dab4-4c99-b3a7-a81f67ebaa7f | 20260408 | Status |  |  | SingleBit | 3427 | FALSE

## DNP3_AnalogSignals
Signal Details | [35 empty] | Remote Points
ASIGNAL | [26 empty] | ADVALMLIMITS | [8 empty] | REMOTEPOINT | [17 empty] | APROCESSING
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | MEASUREMENT_TYPE | IDOBJ_AORGROUP | SIGNAL_DEVICEMAPPING | [7 empty] | ASIGNAL_TYPE | MEASUREMENT_PHASE | MEASUREMENT_UNIT | MEASUREMENT_SIDE | SIGNAL_DIRECTION | SIGNAL_ANNUALSCH | ASIGNAL_FLOWDIRECTION | ASIGNAL_RATEDVALUE | ASIGNAL_MINSETPOINT | ASIGNAL_MAXSETPOINT | ASIGNAL_TRUST | ASIGNAL_ALARMLIMITS | MEASUREMENT_PSR | IDOBJ_NAME | ADVALMLIMITS_ROCALARMGROWTH | ADVALMLIMITS_ROCLIMITGROWTH | ADVALMLIMITS_ROCALARMDROP | ADVALMLIMITS_ROCLIMITDROP | ADVALMLIMITS_FLATLINEALARM | ADVALMLIMITS_FLATLINETIMEOUT | ADVALMLIMITS_CREEPALARM | ADVALMLIMITS_CREEPDEADBAND | IDOBJ_NAME | DELETE | IDOBJ_CUSTOMID | IDOBJ_ALIAS | REMOTEPOINT_TYPE | REMOTEPOINT_SCALING | REMOTEPOINT_INTERCEPT | REMOTEPOINT_ADCFAIL | REMOTEOUTPUT_CMDTIMEOUT | REMOTEOUTPUT_SBOMODE | REMOTEOUTPUT_SPTOL | REMOTEINPUTDNP3_INCOORDS¦REMOTEOUTPUTDNP3_INCOORDS | REMOTEINPUTDNP3_OUTREGISTER¦REMOTEOUTPUTDNP3_OUTREGISTER | AOUTPUTDNP3_OUTTYPE | REMOTEOUTPUTDNP3_OUTCOORDS | COUNTERDNP3_ENABLEROLLOVER | COUNTERDNP3_ROLLOVER | COUNTERDNP3_RESET | APROCESSING_LOCALDBCHECK | APROCESSING_USERELATIVEDB | APROCESSING_DEADBANDTYPE | APROCESSING_DEADBAND | APROCESSING_ZEROCLAMPINGDB | APROCESSING_LINEARFILTER | APROCESSING_LFFACTOR
Signal Name | Delete | Signal Alias | Signal Custom ID | Measurement Type | Signal AOR Group | Substation | Feeder | Feeder Object | Bank | Bay | Device | Device Mapping | Description | Signal Type | Phases | Display Unit | Side | Direction | Annual Schedule | Flow Direction | Rated Value | Min. Setpoint | Max. Setpoint | Trust Factor | Alarm Limits | Remote Unit | Advanced Alarms - Name | Advanced Alarms - Rate-Of-Growth Alarm | Advanced Alarms - Rate-Of-Growth Limit | Advanced Alarms - Rate-Of-Drop Alarm | Advanced Alarms - Rate-Of-Drop Limit | Advanced Alarm - Flatline Alarm | Advanced Alarm - Flatline Timeout [s] | Advanced Alarm - Creep Alarm | Advanced Alarm - Creep Deadband | Remote Point Name | Delete Remote Point | Remote Point Custom ID | Remote Point Alias | Remote Point Type | Scaling Factor | Intercept | ADC Fail | Command Timeout [s] | Commanding Mode | Setpoint Tolerance | Input Coordinates | Output Register | Output Data Type | Output Coordinates | Enable Rollover | Rollover Value | With Reset | Advanced Processing - Local Deadband Check | Advanced Processing - Use Relative Deadband | Deadband Type | Advanced Processing - Deadband | Advanced Processing - Zero Clamping Deadband | Advanced Processing - Apply Linear Filter | Advanced Processing - Linear Filter Factor
GTD_AL21_52-21_IC |  | IC | 4cb19ca6-7bed-448a-9bc5-60ae7f100885 | Current | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL21_52-21_IC |  | a42f52db-745b-444d-be3b-dc9c0b6b66eb | 20230330 | Analog | 1 | 0 | FALSE |  |  |  | 2402 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_AL21_AL21_IB |  | IB | f048afe2-1d7b-4c25-8e83-49e06ff11de3 | Current | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL21_AL21_IB |  | c6b9aac4-6254-4754-a643-6e2e107d031a | 20230330 | Analog | 1 | 0 | FALSE |  |  |  | 2401 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_AL21_52-21_P |  | P | 1b58c33d-0370-48da-823a-6c5674f6aac3 | ActivePower | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL21_52-21_P |  | 08155c84-c4c3-4956-a8e2-8fc555c51da9 | 20230330 | Analog | 1000 | 0 | FALSE |  |  |  | 2404 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_AL21_52-21_Q |  | Q | 0891ae46-fb6a-48d4-8021-b3595c3b9c3f | ReactivePower | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL21_52-21_Q |  | e3b612a6-9e02-4e3b-a15d-6c940026b9f8 | 20230330 | Analog | 1000 | 0 | FALSE |  |  |  | 2405 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TRSA_TRSA_Q |  | Q | bf69f16f-7300-41bc-aba4-9ed5767c76d1 | ReactivePower | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | MeasuredValue | ABC | kVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRSA_TRSA_Q |  | 47c27eee-2ac0-4003-8822-7866f190a7fe | 20260704 | Analog | 1 | 0 | FALSE |  |  |  | 3405 | FALSE
GTD_TRSA_TRSA_IA |  | IA | d3d57a19-a8c3-4b38-ac05-77f52b0da4c6 | Current | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRSA_TRSA_IA |  | 434dfa62-92b3-427f-8063-444af0b3965e | 20260704 | Analog | 1 | 0 | FALSE |  |  |  | 3400 | FALSE
GTD_AL21_52-21_VAB |  | VAB | 634219c5-033d-4bdb-8b53-572ed53774f9 | Voltage | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL21_52-21_VAB |  | aee0f5cf-1972-463a-93de-a23b4c654670 | 20230330 | Analog | 0.1 | 0 | FALSE |  |  |  | 2403 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_SE_RET2_VCC |  | VCC | 492dc645-34df-44a4-bdd9-972e72cfcd7d | Unitless | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | Default | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_SE_RET2_VCC |  | 013c77f1-69f1-4a15-bc62-8d8777e003c7 | 20260704 | Analog | 1 | 0 | FALSE |  |  |  | 3408 | FALSE
GTD_AL21_52-21_IA |  | IA | 8de4a26d-031b-467e-b72a-22d69dea337e | Current | GTD Distr | [6 empty] | GTD_AL21_52-21_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL21_52-21_IA |  | 6d1589de-0da1-4534-b928-290e7549113f | 20230330 | Analog | 1 | 0 | FALSE |  |  |  | 2400 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TRSA_TRSA_VCC |  | VCC | 33a97c71-0f06-44d3-a4a9-61ab2435c8b0 | Unitless | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | Default | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRSA_TRSA_VCC |  | 01e54382-d9af-4c79-bc62-fa5b40a44c95 | 20260704 | Analog | 1 | 0 | FALSE |  |  |  | 3406 | FALSE
GTD_LTGTA_LTGTA_Q |  | Q | 3ed50230-1f5a-4b29-8fed-ca512a074ff2 | ReactivePower | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_TC |  | MeasuredValue | ABC | MVAr | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTGTA_LTGTA_Q |  | GTD_AS_00009 | 20260113 | Analog | 1000 | 0 | FALSE |  |  |  | 8 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_LTGTA_LTGTA_VCA |  | VCA | 088f49f4-76cf-4fb9-b131-e1f2d7404392 | Voltage | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTGTA_LTGTA_VCA |  | GTD_AS_00006 | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 5 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_IB_52-18_VAB |  | VAB | 0d09c699-65f3-4fae-85a3-f02781c8b6f5 | Voltage | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_IB_52-18_VAB |  | ce25e7d2-d508-444d-97c4-c5a5e4560d6c |  | Analog | 1 | 0 | FALSE |  |  |  | 2303 | FALSE
GTD_IB_52-18_IA |  | IA | f4a36a47-3d24-4010-bb59-afee79cc373e | Current | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_IB_52-18_IA |  | c3ea8a45-f4c2-4b87-a8c1-a297f83cca07 |  | Analog | 1 | 0 | FALSE |  |  |  | 2300 | FALSE
GTD_LTGTA_LTGTA_A_KMDF |  | KMDF | c6c4b4ca-419f-40db-815f-ca1390f5d244 | Unitless | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | Default | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTGTA_LTGTA_A_KMDF |  | 0afe23e4-9527-4e57-b1b3-299ae61f3393 | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 10 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_LTGTA_LTGTA_KMDF |  | KMDF | bcfdc37f-36bc-40c1-96de-200ca51a9166 | Unitless | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | Custom | ABC | Default | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTGTA_LTGTA_KMDF |  | GTD_AS_00010 | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 9 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_IB_52-18_Q |  | Q | 1f836edd-7444-4ddd-a81b-41a4c0cb26b8 | ReactivePower | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_IB_52-18_Q |  | 89cabae6-7eb7-4af2-91e9-02ccf63af7bd |  | Analog | 1000 | 0 | FALSE |  |  |  | 2305 | FALSE
GTD_LTGTA_LTGTA_IB |  | IB | 1d109f2b-50b0-4b88-9406-c8e4451a4645 | Current | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_TC |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTGTA_LTGTA_IB |  | GTD_AS_00002 | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 1 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_LTKGC_LTKGC_IB |  | IB | 63e01680-c2df-4151-9fde-b33033941962 | Current | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_TC |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTKGC_LTKGC_IB |  | b45116da-c6ef-4d3f-9d10-1e3fc1149336 |  | Analog | 1 | 0 | FALSE |  |  |  | 201 | FALSE
GTD_LTKGC_LTKGC_Q |  | Q | d66d45d5-2516-41cf-8f4e-845f91a6cf68 | ReactivePower | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_TC |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTKGC_LTKGC_Q |  | f4a6db92-5a6d-4abf-8cd4-33405fdca7a7 |  | Analog | 1000 | 0 | FALSE |  |  |  | 208 | FALSE
GTD_LTKGC_LTKGC_IA |  | IA | 81c68ed2-aeb2-4784-9051-7aca1ef3b61f | Current | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_TC |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTKGC_LTKGC_IA |  | b61b5986-8c6a-4e93-ba19-43edf266d151 |  | Analog | 1 | 0 | FALSE |  |  |  | 200 | FALSE
GTD_LTKGC_LTKGC_KMDF |  | KMDF | 82a03581-5e12-45bf-960b-1fa02eed3a4d | Unitless | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | Default | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTKGC_LTKGC_KMDF |  | 22128eba-ac0a-4357-a297-017a087adaf4 | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 209 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_LTKGC_LTKGC_VB_L |  | VB LINHA | da38bda6-fbb6-46a9-b71d-0354a68b7585 | Voltage | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_TP |  | MeasuredValue | B | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTKGC_LTKGC_VB_L |  | aaef1c54-77d4-451b-92be-c9bd98ef63e6 |  | Analog | 1 | 0 | FALSE |  |  |  | 206 | FALSE
GTD_LTKGC_LTKGC_P |  | P | c15bb8c1-c8e0-4bcb-9319-5a7b182f7525 | ActivePower | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_TC |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTKGC_LTKGC_P |  | 262f9d16-1bc9-4e52-bc74-bb518604950c |  | Analog | 1000 | 0 | FALSE |  |  |  | 207 | FALSE
GTD_IB_52-18_IC |  | IC | 45a3d7ef-57af-4c32-8d56-be4f8789633c | Current | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_IB_52-18_IC |  | abdc223b-56f5-4e03-bfaf-b42753a1cc39 |  | Analog | 1 | 0 | FALSE |  |  |  | 2302 | FALSE
GTD_LTGTA_LTGTA_P |  | P | d3b6cb35-9dd7-4932-abdc-447a0ea8a78f | ActivePower | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_TC |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTGTA_LTGTA_P |  | GTD_AS_00008 | 20260113 | Analog | 1000 | 0 | FALSE |  |  |  | 7 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_LTKGC_LTKGC_IC |  | IC | a642f74d-960b-446d-bd95-4e93235f32d8 | Current | GTD Trans | [6 empty] | GTD_LTKGC_LTKGC_TC |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTKGC_LTKGC_IC |  | 101abcf4-1d16-4a1b-b1f3-d58f2d97b592 |  | Analog | 1 | 0 | FALSE |  |  |  | 202 | FALSE
GTD_SE_RET1_VCC |  | VCC | 306fe1b7-1c67-46c8-af78-8dac689f5784 | Unitless | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | Custom | ABC | Default | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_SE_RET1_VCC |  | 1d3867b4-e5b1-4e05-b7e3-34e6cafc2d44 | 20260704 | Analog | 1 | 0 | FALSE |  |  |  | 3407 | FALSE
GTD_LTGTA_LTGTA_IA |  | IA | 1466c4a5-a4dc-417d-a5de-651f9b43bafa | Current | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_TC |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTGTA_LTGTA_IA |  | GTD_AS_00001 | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 0 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_LTGTA_LTGTA_VAB |  | VAB | 59137b23-80e1-40e0-a5f2-f0a6077ad6e0 | Voltage | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTGTA_LTGTA_VAB |  | GTD_AS_00004 | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 3 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_IB_52-18_P |  | P | 695d4e20-c0ca-4d95-9f6e-6e07e3ce9348 | ActivePower | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_IB_52-18_P |  | fd166440-bbd4-4ee8-b718-f3f77c48cc5f |  | Analog | 1000 | 0 | FALSE |  |  |  | 2304 | FALSE
GTD_LTGTA_LTGTA_VBC |  | VBC | 7ab7dbca-198f-44d7-aa5b-a26524c74a6e | Voltage | GTD Trans | [6 empty] | GTD_LTGTA_52-1_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTGTA_LTGTA_VBC |  | GTD_AS_00005 | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 4 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_LTGTA_LTGTA_VB_L |  | VB | 91389bd0-cd3e-4eb2-a492-b4c10d781f2d | Voltage | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_TP |  | MeasuredValue | B | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTGTA_LTGTA_VB_L |  | GTD_AS_00007 | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 6 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_LTGTA_LTGTA_IC |  | IC | 2b0302f7-efcb-433f-b91a-047b1f8a3e0d | Current | GTD Trans | [6 empty] | GTD_LTGTA_LTGTA_TC |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTGTA_LTGTA_IC |  | GTD_AS_00003 | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 2 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR1AT_TR1AT_VAB |  | VAB | 2b349846-a4a7-48af-9172-a2df32cc0734 | Voltage | GTD Trans | [6 empty] | GTD_TR1AT_52-2_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | VBC_144.9@143.52_131.1@124.2_Trans | UTR_GTD_1 | [9 empty] | GTD_TR1AT_TR1AT_VAB |  | GTD_AS_00011 | 20260204 | Analog | 1 | 0 | FALSE |  |  |  | 603 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR1AT_TR1AT_IA |  | IA | d0e2bd93-9d52-46fa-8961-993d5be5a82c | Current | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_TC |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR1AT_TR1AT_IA |  | GTD_AS_00015 | 20260204 | Analog | 1 | 0 | FALSE |  |  |  | 600 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_IB_52-18_IB |  | IB | 15cc0fc0-30cf-40d1-82e8-b0a06f60fe74 | Current | GTD Trans | [6 empty] | IVB_IB_52-18_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_IB_52-18_IB |  | 0b712f01-fa0b-4941-adc2-45282098da7d |  | Analog | 1 | 0 | FALSE |  |  |  | 2301 | FALSE
GTD_TR1AT_TR1AT_IC |  | IC | 3dd28716-db8b-43a0-8325-0fddf768f000 | Current | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_TC |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR1AT_TR1AT_IC |  | GTD_AS_00017 | 20260204 | Analog | 1 | 0 | FALSE |  |  |  | 602 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR1BT_TR1BT_P |  | P | ce7a012b-72ac-447b-8044-0d955a25d80f | ActivePower | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_TC |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR1BT_TR1BT_P |  | GTD_AS_00027 | 20260204 | Analog | 1000 | 0 | FALSE |  |  |  | 614 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR1AT_TR1AT_IB |  | IB | e33c38ad-c43b-41bc-8bd0-390f56f6ab49 | Current | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_TC |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR1AT_TR1AT_IB |  | GTD_AS_00016 | 20260204 | Analog | 1 | 0 | FALSE |  |  |  | 601 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR1BT_TR1BT_IA |  | IA | 548a6011-474e-414e-97ad-91b9937eb9f2 | Current | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_TC |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR1BT_TR1BT_IA |  | GTD_AS_00024 | 20260204 | Analog | 1 | 0 | FALSE |  |  |  | 608 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR1AT_TR1AT_P |  | P | ca4e6c03-f310-415d-8f9c-2b3f19c0698e | ActivePower | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_TC |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR1AT_TR1AT_P |  | GTD_AS_00018 | 20260204 | Analog | 1000 | 0 | FALSE |  |  |  | 606 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR1AT_TR1AT_Q |  | Q | 3c047a21-38b5-42a5-8fd0-2c0dbe671b16 | ReactivePower | GTD Trans | [6 empty] | GTD_TR1AT_TR1AT_TC |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR1AT_TR1AT_Q |  | GTD_AS_00019 | 20260204 | Analog | 1000 | 0 | FALSE |  |  |  | 607 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR1AT_TR1AT_VBC |  | VBC | ae3d56ae-f527-4550-bfee-e4602fd225ef | Voltage | GTD Trans | [6 empty] | GTD_TR1AT_52-2_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR1AT_TR1AT_VBC |  | GTD_AS_00012 | 20260204 | Analog | 1 | 0 | FALSE |  |  |  | 604 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR1BT_TR1BT_VCA |  | VCA | a2872ab7-7311-476d-9af9-2e59602c8936 | Voltage | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR1BT_TR1BT_VCA |  | GTD_AS_00022 | 20260204 | Analog | 1 | 0 | FALSE |  |  |  | 613 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR1BT_TR1BT_VAB |  | VAB | bcf9852b-41bc-4f2d-b364-3e6133d564c5 | Voltage | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | V_24.2@23.9_21.9@21.6_Trans | UTR_GTD_1 | [9 empty] | GTD_TR1BT_TR1BT_VAB |  | GTD_AS_00020 | 20260204 | Analog | 1 | 0 | FALSE |  |  |  | 611 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR1BT_TR1BT_Q |  | Q | 9565c07e-f75e-4762-9e1a-84bd8faaa94d | ReactivePower | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_TC |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR1BT_TR1BT_Q |  | GTD_AS_00028 | 20260204 | Analog | 1000 | 0 | FALSE |  |  |  | 615 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR1BT_TR1BT_TENR |  | TENR | 5f08f9f7-746a-4cd0-afb0-dd60f304b8a0 | Temperature | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | C | None | Read |  | Undirected | 0 | 0 | 100 | -1 | TENR_105@95_0@0_Trans | UTR_GTD_1 | [9 empty] | GTD_TR1BT_TR1BT_TENR |  | GTD_AS_00030 | 20260204 | Analog | 1 | 0 | FALSE |  |  |  | 622 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR1BT_TR1BT_IB |  | IB | 33159824-cb22-4109-a7ed-f9732d3ea21a | Current | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_TC |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR1BT_TR1BT_IB |  | GTD_AS_00025 | 20260204 | Analog | 1 | 0 | FALSE |  |  |  | 609 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR1BT_TR1BT_F |  | F | da4d8872-0f66-4508-b624-88e867d7a16c | Frequency | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | MeasuredValue | ABC | Hz | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR1BT_TR1BT_F |  | GTD_AS_00029 | 20260204 | Analog | 1 | 0 | FALSE |  |  |  | 616 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR1_TR1_TOLE |  | TOLE | deacdfbd-5334-418f-bcd5-2de4de7c6f38 | Temperature | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | C | None | Read |  | Undirected | 0 | 0 | 100 | -1 | TOLE_95@85_0@0_Trans | UTR_GTD_1 | [9 empty] | GTD_TR1_TR1_TOLE |  | GTD_AS_00032 | 20260204 | Analog | 1 | 0 | FALSE |  |  |  | 620 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR1AT_TR1AT_TENR |  | TENR | 5c17ffa2-6bf3-474b-b7bd-4f9c51f53d3a | Temperature | GTD Trans | [6 empty] | GTD_TR1_TR1_TR |  | Custom | ABC | C | None | Read |  | Undirected | 0 | 0 | 100 | -1 | TENR_105@95_0@0_Trans | UTR_GTD_1 | [9 empty] | GTD_TR1AT_TR1AT_TENR |  | GTD_AS_00031 | 20260204 | Analog | 1 | 0 | FALSE |  |  |  | 621 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR1BT_TR1BT_VBC |  | VBC | 54679f85-de5c-451b-8cd7-1d0aa0a46596 | Voltage | GTD Trans | [6 empty] | GTD_TR1BT_52-10_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR1BT_TR1BT_VBC |  | GTD_AS_00021 | 20260204 | Analog | 1 | 0 | FALSE |  |  |  | 612 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR1AT_TR1AT_VCA |  | VCA | 034fd56c-7e9f-4fb3-899f-5bb8599a023a | Voltage | GTD Trans | [6 empty] | GTD_TR1AT_52-2_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR1AT_TR1AT_VCA |  | GTD_AS_00013 | 20260204 | Analog | 1 | 0 | FALSE |  |  |  | 605 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR1BT_TR1BT_IC |  | IC | a96f879a-34ee-4d61-bb8f-7905dc3a7ef8 | Current | GTD Trans | [6 empty] | GTD_TR1BT_TR1BT_TC |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR1BT_TR1BT_IC |  | GTD_AS_00026 | 20260204 | Analog | 1 | 0 | FALSE |  |  |  | 610 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2AT_TR2AT_VAB |  | VAB | 12dccf56-34d7-40dd-9a11-f9e1864f9cf4 | Voltage | GTD Trans | [6 empty] | GTD_TR2AT_52-6_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | VBC_144.9@143.52_131.1@124.2_Trans | UTR_GTD_1 | [9 empty] | GTD_TR2AT_TR2AT_VAB |  | GTD_AS_00033 | 20260210 | Analog | 1 | 0 | FALSE |  |  |  | 903 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2AT_TR2AT_VBC |  | VBC | 3f2e8e7b-af71-4197-9683-78eb7308244e | Voltage | GTD Trans | [6 empty] | GTD_TR2AT_52-6_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR2AT_TR2AT_VBC |  | GTD_AS_00034 | 20260210 | Analog | 1 | 0 | FALSE |  |  |  | 904 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2AT_TR2AT_VCA |  | VCA | 78d681da-8fcb-4fa3-8b64-bd820cd8b40b | Voltage | GTD Trans | [6 empty] | GTD_TR2AT_52-6_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR2AT_TR2AT_VCA |  | GTD_AS_00035 | 20260210 | Analog | 1 | 0 | FALSE |  |  |  | 905 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2BT_TR2BT_VAB |  | VAB | 9a39cac7-0467-40eb-91a1-9669039c178c | Voltage | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | V_24.2@23.9_21.9@21.6_Trans | UTR_GTD_1 | [9 empty] | GTD_TR2BT_TR2BT_VAB |  | GTD_AS_00041 | 20260210 | Analog | 1 | 0 | FALSE |  |  |  | 911 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2AT_TR2AT_IA |  | IA | ace48954-b27c-46e8-a2f2-309cc6dc9ea6 | Current | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_TC |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR2AT_TR2AT_IA |  | GTD_AS_00036 | 20260210 | Analog | 1 | 0 | FALSE |  |  |  | 900 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2BT_TR2BT_VCA |  | VCA | 219c90a5-56ea-4b11-a63c-87c558ff9f89 | Voltage | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR2BT_TR2BT_VCA |  | GTD_AS_00043 | 20260210 | Analog | 1 | 0 | FALSE |  |  |  | 913 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2_TR2_TOLE |  | TOLE | fe718600-e724-4625-bcc2-b1332a8c1222 | Temperature | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | C | None | Read |  | Undirected | 0 | 0 | 100 | -1 | TOLE_95@85_0@0_Trans | UTR_GTD_1 | [9 empty] | GTD_TR2_TR2_TOLE |  | GTD_AS_00052 | 20260210 | Analog | 1 | 0 | FALSE |  |  |  | 1022 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2BT_TR2BT_Q |  | Q | 7e4b124d-7e79-4779-9491-6d57fd59850f | ReactivePower | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_TC |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR2BT_TR2BT_Q |  | GTD_AS_00048 | 20260210 | Analog | 1000 | 0 | FALSE |  |  |  | 915 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2AT_TR2AT_IC |  | IC | 75194a08-dccb-4f5e-b875-103a35b7e6b6 | Current | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_TC |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR2AT_TR2AT_IC |  | GTD_AS_00038 | 20260210 | Analog | 1 | 0 | FALSE |  |  |  | 902 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2BT_TR2BT_IC |  | IC | 73ed7605-8886-41d0-abbf-cc586dfa25fa | Current | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_TC |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR2BT_TR2BT_IC |  | GTD_AS_00046 | 20260210 | Analog | 1 | 0 | FALSE |  |  |  | 910 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2BT_TR2BT_TENR |  | TENR | 9de08d91-b48e-4ed5-869e-1704edeaf8fc | Temperature | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | C | None | Read |  | Undirected | 0 | 0 | 100 | -1 | TENR_105@95_0@0_Trans | UTR_GTD_1 | [9 empty] | GTD_TR2BT_TR2BT_TENR |  | GTD_AS_00050 | 20260210 | Analog | 1 | 0 | FALSE |  |  |  | 1020 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2BT_TR2BT_IB |  | IB | 87740197-706e-4d7d-b2d6-ed8683f6b0fb | Current | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_TC |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR2BT_TR2BT_IB |  | GTD_AS_00045 | 20260210 | Analog | 1 | 0 | FALSE |  |  |  | 909 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2BT_TR2BT_P |  | P | 78fc1f8f-a0eb-4b8e-aa5f-2bd4882cfbf3 | ActivePower | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_TC |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR2BT_TR2BT_P |  | GTD_AS_00047 | 20260210 | Analog | 1000 | 0 | FALSE |  |  |  | 914 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2AT_TR2AT_IB |  | IB | 65227053-ac62-4bb6-9910-d58c654f9933 | Current | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_TC |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR2AT_TR2AT_IB |  | GTD_AS_00037 | 20260210 | Analog | 1 | 0 | FALSE |  |  |  | 901 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2BT_TR2BT_VBC |  | VBC | 86ac508e-57b5-4847-bd40-54371ee7f02e | Voltage | GTD Trans | [6 empty] | GTD_TR2BT_52-20_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR2BT_TR2BT_VBC |  | GTD_AS_00042 | 20260210 | Analog | 1 | 0 | FALSE |  |  |  | 912 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2BT_TR2BT_F |  | F | 8e1aced4-dd56-4efd-a2f8-704109bfb3b6 | Frequency | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | MeasuredValue | ABC | Hz | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR2BT_TR2BT_F |  | GTD_AS_00049 | 20260210 | Analog | 1 | 0 | FALSE |  |  |  | 916 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2AT_TR2AT_Q |  | Q | 30ec06e0-6e6e-4c8f-884a-f545459f79ea | ReactivePower | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_TC |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR2AT_TR2AT_Q |  | GTD_AS_00040 | 20260210 | Analog | 1000 | 0 | FALSE |  |  |  | 907 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2AT_TR2AT_TENR |  | TENR | fd2ef629-de21-4748-992a-86d02a14da49 | Temperature | GTD Trans | [6 empty] | GTD_TR2_TR2_TR |  | Custom | ABC | C | None | Read |  | Undirected | 0 | 0 | 100 | -1 | TENR_105@95_0@0_Trans | UTR_GTD_1 | [9 empty] | GTD_TR2AT_TR2AT_TENR |  | GTD_AS_00051 | 20260210 | Analog | 1 | 0 | FALSE |  |  |  | 1021 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2BT_TR2BT_IA |  | IA | b26114d3-e0e5-4e4b-9b47-4f66c259db9e | Current | GTD Trans | [6 empty] | GTD_TR2BT_TR2BT_TC |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR2BT_TR2BT_IA |  | GTD_AS_00044 | 20260210 | Analog | 1 | 0 | FALSE |  |  |  | 908 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2AT_TR2AT_P |  | P | b21e688b-0a01-49b3-8b8b-ffef9a25e5e9 | ActivePower | GTD Trans | [6 empty] | GTD_TR2AT_TR2AT_TC |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TR2AT_TR2AT_P |  | GTD_AS_00039 | 20260210 | Analog | 1000 | 0 | FALSE |  |  |  | 906 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TRF03_TRF03_P_KMDF |  | KMDF | 9a1f4faa-5c27-401c-8a09-f8f186a24aa8 | Unitless | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | Default | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRF03_TRF03_P_KMDF |  | bf730f25-fc23-4e85-bac6-3294ee8bf14b | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 409 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TRF03_TRF03_IA |  | IA | 9b662799-e49a-4b11-8954-0d0b66fcf7ac | Current | GTD Trans | [6 empty] | IVB_TRANS_TRANS_TC |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRF03_TRF03_IA |  | ad219f6f-ba12-4bd2-8b56-288e73f45ddc | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 400 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TRF03_TRF03_A_KMDF |  | KMDF | a1c9fc0b-1f52-4fe8-9fde-4b3f9da20242 | Unitless | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | Custom | ABC | Default | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRF03_TRF03_A_KMDF |  | 740400d1-5ddb-437d-a7bc-27e3fef28624 | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 410 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TRF03_TRF03_Q |  | Q | a6ba1173-d1e3-438a-83bd-391c0c2c4132 | ReactivePower | GTD Trans | [6 empty] | IVB_TRANS_TRANS_TC |  | MeasuredValue | ABC | MVAr | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRF03_TRF03_Q |  | 756ee55d-0e36-4b65-9a16-8cb59568fc82 | 20260113 | Analog | 1000 | 0 | FALSE |  |  |  | 408 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TRF03_TRF03_P |  | P | 4cc2aaaa-3097-4647-88e3-9520297cea15 | ActivePower | GTD Trans | [6 empty] | IVB_TRANS_TRANS_TC |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRF03_TRF03_P |  | 169c81cd-c47a-4f3c-823a-a5c03766e4e8 | 20260113 | Analog | 1000 | 0 | FALSE |  |  |  | 407 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TRF03_TRF03_IB |  | IB | cbc8ab35-48d9-4907-aee9-1b0eabd55eb3 | Current | GTD Trans | [6 empty] | IVB_TRANS_TRANS_TC |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRF03_TRF03_IB |  | 6a8d2d07-ab0f-4a6f-85e1-3b418fe1fa8b | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 401 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TRF03_BT1_VB |  | VB | 4b6de656-b1ca-43d1-b11b-6e64689a81fc | Voltage | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRF03_BT1_VB |  | dac684cc-db83-41bc-a840-d7f0ba91b68b | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 406 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TRF03_TRF03_VBC |  | VBC | 2fadac7c-700c-4956-b64d-67962f97e704 | Voltage | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRF03_TRF03_VBC |  | c5ef1fdd-70a5-496f-8fa4-accaaba8cf2d | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 404 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TRF03_TRF03_IC |  | IC | 2e6ac822-b0ec-4e76-8681-ebab24129054 | Current | GTD Trans | [6 empty] | IVB_TRANS_TRANS_TC |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRF03_TRF03_IC |  | 53d6717c-3117-498e-9cb3-cde2ba62ad58 | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 402 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TRF03_TRF03_VAB |  | VAB | 72950a09-b31a-4433-8088-666e0875bd5d | Voltage | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRF03_TRF03_VAB |  | 1da2afac-2920-4f79-b576-9fd91c9c3589 | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 403 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TRF03_TRF03_VCA |  | VCA | cf8ed885-9760-4f2e-b234-02953354660e | Voltage | GTD Trans | [6 empty] | GTD_TRANS_24-03_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRF03_TRF03_VCA |  | 8b29ff78-16a5-4724-8323-053cff7f9534 | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 405 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_LTKGC_LTKGC_VAB |  | VAB | c862aa55-7907-4489-a03a-c3297d058eb0 | Voltage | GTD Trans | [6 empty] | 52-3_GTD |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTKGC_LTKGC_VAB |  | 76feb61a-44aa-4626-bb2a-4963309d9124 | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 203 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_BC2_BC2_IB |  | IB | c0340398-7089-4f01-b224-449aabd78273 | Current | GTD Trans | [6 empty] | IVB_BC1_BC1_TC |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_BC2_BC2_IB |  | 8eeed5a0-363a-4b11-a9e3-d6ca19a95c3a |  | Analog | 1 | 0 | FALSE |  |  |  | 2201 | FALSE
GTD_BC2_BC2_IA |  | IA | b651a334-cc4d-4714-92e2-f062f9e283b4 | Current | GTD Trans | [6 empty] | IVB_BC1_BC1_TC |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_BC2_BC2_IA |  | 59bb5462-29c5-4959-a950-fa1dd5f63ff6 |  | Analog | 1 | 0 | FALSE |  |  |  | 2200 | FALSE
GTD_LTKGC_LTKGC_VCA |  | VCA | b327deb1-9a9a-4d35-a071-e11dcc41040a | Voltage | GTD Trans | [6 empty] | 52-3_GTD |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTKGC_LTKGC_VCA |  | 0d736aeb-8e93-493d-900e-319ffbf838c2 | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 205 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_BC1_BC1_IN61 |  | IN61 | 8010f272-2053-4aa7-9650-7b138a77e7b1 | Current | GTD Trans | [6 empty] | IVB_BC1_BC1_TC |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_BC1_BC1_IN61 |  | 5c1d1728-138a-41e2-8188-37877ec9db1c |  | Analog | 1 | 0 | FALSE |  |  |  | 2103 | FALSE
GTD_BC1_BC1_IA |  | IA | e271d3ff-21e3-4fbf-a384-d0f4f6a6f7d7 | Current | GTD Trans | [6 empty] | IVB_BC1_BC1_TC |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_BC1_BC1_IA |  | b8a47351-47fd-4a56-bddd-d573f2eccc69 |  | Analog | 1 | 0 | FALSE |  |  |  | 2100 | FALSE
GTD_BC1_BC1_IC |  | IC | bd7710fe-8f4f-4c84-90db-cf789f53ba4d | Current | GTD Trans | [6 empty] | IVB_BC1_BC1_TC |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_BC1_BC1_IC |  | 7cd4f9fd-0830-498f-b221-bb6c265c7c83 |  | Analog | 1 | 0 | FALSE |  |  |  | 2102 | FALSE
GTD_BC1_BC1_IB |  | IB | ae4896d2-7ab5-45af-b762-bc98170fcb8f | Current | GTD Trans | [6 empty] | IVB_BC1_BC1_TC |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_BC1_BC1_IB |  | ac02dd8e-9fbc-4776-827d-fd666533200f |  | Analog | 1 | 0 | FALSE |  |  |  | 2101 | FALSE
GTD_LTKGC_LTKGC_VBC |  | VBC | 038ae2fd-1773-4f14-a0cc-eb45bab31bd6 | Voltage | GTD Trans | [6 empty] | 52-3_GTD |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTKGC_LTKGC_VBC |  | a5b49b7e-1bce-4d8f-908f-e4c89d61def5 | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 204 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_AL12_52-12_IA |  | IA | 7b762977-a81c-4d72-9792-a35807883298 | Current | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL12_52-12_IA |  | d72e4083-52ce-49dc-b074-f596cb73f4ad |  | Analog | 1 | 0 | FALSE |  |  |  | 1600 | FALSE
GTD_AL12_52-12_IB |  | IB | 9885af56-c543-4be0-85fd-ab7a557cbe9a | Current | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL12_52-12_IB |  | 3f34bedf-ef90-45e5-ac4a-6d63f4c3d0c0 |  | Analog | 1 | 0 | FALSE |  |  |  | 1601 | FALSE
GTD_AL12_52-12_IC |  | IC | 10963e0c-c82f-4432-be8f-f31f708b7f6e | Current | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL12_52-12_IC |  | e9652723-6fde-4aab-9d93-fcc82b16d569 |  | Analog | 1 | 0 | FALSE |  |  |  | 1602 | FALSE
GTD_AL11_52-11_Q |  | Q | 80ce5b90-d6f4-48a9-b72e-d2bfbb6588c5 | ReactivePower | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL11_52-11_Q |  | bff17ef7-0552-4da5-b312-1ee996a0244c |  | Analog | 1000 | 0 | FALSE |  |  |  | 1505 | FALSE
GTD_AL12_52-12_Q |  | Q | 5fe3c483-e636-44e1-868c-916df3def9d6 | ReactivePower | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL12_52-12_Q |  | f4303da1-c2bb-403b-ab20-75367c19a3a2 |  | Analog | 1000 | 0 | FALSE |  |  |  | 1605 | FALSE
GTD_AL11_52-11_VAB |  | VAB | 60e8b57c-c965-4ecb-a1bc-ec061047024d | Voltage | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL11_52-11_VAB |  | c43cbf82-aac3-48a6-9a93-60178fd119d0 |  | Analog | 1 | 0 | FALSE |  |  |  | 1503 | FALSE
GTD_AL12_52-12_P |  | P | 5363b1ba-4459-4596-8fc3-8568ba32fcce | ActivePower | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL12_52-12_P |  | fefd1de1-02c8-41b6-a127-eb439ee2faed |  | Analog | 1000 | 0 | FALSE |  |  |  | 1604 | FALSE
GTD_AL11_52-11_IA |  | IA | b35bfc29-e410-4689-9ba4-2712cd6a00f2 | Current | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL11_52-11_IA |  | cec23ec7-2223-4eaf-8cf7-893f602f02a2 |  | Analog | 1 | 0 | FALSE |  |  |  | 1500 | FALSE
GTD_AL12_52-12_VAB |  | VAB | c9cdf74d-8a03-4277-8405-f3da2dfce20a | Voltage | GTD Distr | [6 empty] | GTD_AL12_52-12_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL12_52-12_VAB |  | 00c5d9cd-669f-4fd9-9925-1a9a0655878e |  | Analog | 1 | 0 | FALSE |  |  |  | 1603 | FALSE
GTD_AL11_52-11_IB |  | IB | 46c9af80-26bf-48cf-b4ab-b61f889eca78 | Current | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL11_52-11_IB |  | a413b418-a743-4d88-ad13-7bc042779820 |  | Analog | 1 | 0 | FALSE |  |  |  | 1501 | FALSE
GTD_AL11_52-11_P |  | P | 521b3696-0364-4842-9bba-5872ed3af866 | ActivePower | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL11_52-11_P |  | c54dc0d2-c49a-464a-a584-5d7b665ad430 |  | Analog | 1000 | 0 | FALSE |  |  |  | 1504 | FALSE
GTD_AL11_52-11_IC |  | IC | 7f464c5e-14f1-4d4c-b25d-330f13dcde73 | Current | GTD Distr | [6 empty] | GTD_AL11_52-11_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL11_52-11_IC |  | c4074a85-260b-449b-9044-69b2df46f7a7 |  | Analog | 1 | 0 | FALSE |  |  |  | 1502 | FALSE
GTD_TRSA_TRSA_VAB |  | VAB | 914543ee-e573-48ac-a9d6-2957a31d2084 | Voltage | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | MeasuredValue | AB | V | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRSA_TRSA_VAB |  | 66c2c8d4-bd00-46d9-b685-89f6bea2bc90 | 20260407 | Analog | 0.001 | 0 | FALSE |  |  |  | 3403 | FALSE
GTD_TRSA_TRSA_IC |  | IC | e0ad6f12-d4db-4450-b7ab-24d79d799f23 | Current | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRSA_TRSA_IC |  | 42140dc4-5e36-44ca-b683-6fdde88ce91c | 20260704 | Analog | 1 | 0 | FALSE |  |  |  | 3402 | FALSE
GTD_AL13_52-13_IA |  | IA | dc790203-67f0-4ef2-a297-2d8ca8870d6a | Current | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL13_52-13_IA |  | fa21f146-2d59-441a-afe2-d60e55a4833e |  | Analog | 1 | 0 | FALSE |  |  |  | 1700 | FALSE
GTD_AL13_52-13_IB |  | IB | 151e4e0e-1367-40a8-939f-d9283c45f701 | Current | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL13_52-13_IB |  | ac2adefd-5212-4f3f-a931-eae89811255d |  | Analog | 1 | 0 | FALSE |  |  |  | 1701 | FALSE
GTD_AL13_52-13_P |  | P | 7cd060cf-79b2-4d7a-a1f8-c08068bbb1e5 | ActivePower | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL13_52-13_P |  | e4770110-9cef-4965-b69c-472bb1fc510a |  | Analog | 1000 | 0 | FALSE |  |  |  | 1704 | FALSE
GTD_TRF1_24-1_IA |  | IA | a7b0f106-eb72-4484-b624-14421d8a3655 | Current | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_TRF1_24-1_IA |  | f7758601-02f6-4663-9db6-974049a1a642 |  | Analog | 1 | 0 | FALSE |  |  |  | 2000 | FALSE
GTD_AL14_52-14_IB |  | IB | 4acb545a-604c-44fc-930b-64d09fea748b | Current | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL14_52-14_IB |  | 2cbf5b58-8582-4e29-9d08-9d514a7bcdbc |  | Analog | 1 | 0 | FALSE |  |  |  | 1801 | FALSE
GTD_TRF1_24-1_IC |  | IC | b5956d47-7163-43d7-a281-9f3798c15edf | Current | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_TRF1_24-1_IC |  | 9679b25e-f016-49ef-8417-e089f7bea2aa |  | Analog | 1 | 0 | FALSE |  |  |  | 2002 | FALSE
GTD_AL15_52-15_IA |  | IA | ca497cab-63d7-400a-83af-f9334c0ba14a | Current | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL15_52-15_IA |  | f98a15f0-7360-4c56-8c12-7cf99062d37e |  | Analog | 1 | 0 | FALSE |  |  |  | 1900 | FALSE
GTD_AL15_52-15_Q |  | Q | 89f13200-6dcf-4249-b74f-ebbe018895ce | ReactivePower | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL15_52-15_Q |  | 90257486-4406-47de-8e3d-4cf98220ca37 |  | Analog | 1000 | 0 | FALSE |  |  |  | 1905 | FALSE
GTD_AL23_52-23_IA |  | IA | 5dba8356-d919-4d17-b590-f6b1555e95e1 | Current | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL23_52-23_IA |  | eb26eee0-82b7-4cd0-b61c-863a18ef0394 |  | Analog | 1 | 0 | FALSE |  |  |  | 2600 | FALSE
GTD_AL23_52-23_IB |  | IB | 7bffa30f-591c-4b6e-9e34-5c3eade62cce | Current | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL23_52-23_IB |  | 2fe9d75e-aa29-4188-afe4-22f9104c6ea0 |  | Analog | 1 | 0 | FALSE |  |  |  | 2601 | FALSE
GTD_AL23_52-23_IC |  | IC | 4a56cdb5-e090-4518-808a-7b825807760b | Current | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL23_52-23_IC |  | f5a5a6bc-571f-4a3e-a661-46f49f57bec0 |  | Analog | 1 | 0 | FALSE |  |  |  | 2602 | FALSE
GTD_AL23_52-23_Q |  | Q | 995f4e29-c1e1-40d5-8f10-8fdf62b8d08c | ReactivePower | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL23_52-23_Q |  | 53fbdf7d-8c7b-48bc-b260-854841f4a026 |  | Analog | 1000 | 0 | FALSE |  |  |  | 2605 | FALSE
GTD_AL14_52-14_P |  | P | 2779e7b4-fa8a-46c0-bc9d-af16665f799b | ActivePower | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL14_52-14_P |  | d2970b0a-dca2-4bfe-bc89-48709012fb24 |  | Analog | 1000 | 0 | FALSE |  |  |  | 1804 | FALSE
GTD_AL24_52-24_IA |  | IA | 2db49317-3e7a-49ad-b42a-e4f9a4aff5ca | Current | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL24_52-24_IA |  | 534ef9e6-e186-42ab-9abe-07ef2dbb6675 |  | Analog | 1 | 0 | FALSE |  |  |  | 2700 | FALSE
GTD_AL22_52-22_IB |  | IB | 69a8f9ab-0019-4263-980e-1d771dbd6cf8 | Current | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL22_52-22_IB |  | 8f179aea-74b7-4cfb-bf35-c76f8d86c5d0 |  | Analog | 1 | 0 | FALSE |  |  |  | 2501 | FALSE
GTD_AL24_52-24_IB |  | IB | b913ac60-8793-4b10-a2ae-2aca59cd63fc | Current | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL24_52-24_IB |  | e01e13dc-fd2e-4153-b809-e29e91b4f0a5 |  | Analog | 1 | 0 | FALSE |  |  |  | 2701 | FALSE
GTD_AL22_52-22_P |  | P | 5e41a944-bc4e-4a5a-a1ee-3f6332da574e | ActivePower | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL22_52-22_P |  | 3cec084e-4bd6-455c-a085-4fbdfddd8a12 |  | Analog | 1000 | 0 | FALSE |  |  |  | 2504 | FALSE
GTD_AL25_52-25_IB |  | IB | 816bb334-17a2-4202-89d5-476d7bb8de72 | Current | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL25_52-25_IB |  | 42646951-d06b-45a7-9d05-2e1a27d23d46 |  | Analog | 1 | 0 | FALSE |  |  |  | 2801 | FALSE
GTD_AL24_52-24_Q |  | Q | 40703bbc-a8e9-45b8-b2a6-dc31e7429f6c | ReactivePower | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL24_52-24_Q |  | 860f2360-a9aa-4942-9062-dc32cd1adccf |  | Analog | 1000 | 0 | FALSE |  |  |  | 2705 | FALSE
GTD_AL25_52-25_IA |  | IA | 627be606-6932-4dba-b340-10ffeac454c7 | Current | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL25_52-25_IA |  | 3416f422-333f-4ce1-ad07-68edf1345610 |  | Analog | 1 | 0 | FALSE |  |  |  | 2800 | FALSE
GTD_AL25_52-25_P |  | P | 744723d3-f287-418d-800d-c7395ad4ecd4 | ActivePower | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL25_52-25_P |  | 6aa32d7a-75e5-4bb0-ac4a-84faca409bd6 |  | Analog | 1000 | 0 | FALSE |  |  |  | 2804 | FALSE
GTD_AL25_52-25_Q |  | Q | 09093bf8-205f-405b-9cc3-5e6469c382e2 | ReactivePower | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL25_52-25_Q |  | 000a0f13-69c1-4d30-b1d3-03fe7f886e58 |  | Analog | 1000 | 0 | FALSE |  |  |  | 2805 | FALSE
GTD_TRF2_24-2_IB |  | IB | d1896ab0-600d-4f20-949f-a44a6ec0a3c1 | Current | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_TRF2_24-2_IB |  | 273adcf5-dbd5-464c-877f-4575a25db24e |  | Analog | 1 | 0 | FALSE |  |  |  | 2901 | FALSE
GTD_TRF2_24-2_IC |  | IC | 0c55c443-fe74-46e8-98ce-ee6e745497a1 | Current | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_TRF2_24-2_IC |  | fb3cb83b-695a-43b0-9e06-4aa11f5e7b26 |  | Analog | 1 | 0 | FALSE |  |  |  | 2902 | FALSE
GTD_TRF2_24-2_IA |  | IA | 55936831-05ce-4f35-84a6-d198e0a6b21a | Current | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_TRF2_24-2_IA |  | 999f34e1-f881-4ca3-ba13-3e35c565d950 |  | Analog | 1 | 0 | FALSE |  |  |  | 2900 | FALSE
GTD_TRF2_24-2_P |  | P | 80d3b593-ba52-457b-9f70-36f8de344d98 | ActivePower | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRF2_24-2_P |  | 1125b700-a72c-48ad-a3b4-62e86f9a0bc7 |  | Analog | 1000 | 0 | FALSE |  |  |  | 2904 | FALSE
GTD_AL24_52-24_IC |  | IC | 57139b6e-efd8-45e5-9717-5a10ecc4cbfd | Current | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL24_52-24_IC |  | 1d51cdd7-fd9e-488d-901f-bcb56885aff3 |  | Analog | 1 | 0 | FALSE |  |  |  | 2702 | FALSE
GTD_AL24_52-24_P |  | P | e970e47c-5c67-4fc8-8601-c027e746cc27 | ActivePower | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL24_52-24_P |  | 48e27e00-7916-46bd-9167-a64f983a4ed7 |  | Analog | 1000 | 0 | FALSE |  |  |  | 2704 | FALSE
GTD_AL25_52-25_VAB |  | VAB | 5acbf5a3-bb49-4be2-a156-a00b16ff29e7 | Voltage | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL25_52-25_VAB |  | bee05490-eaf2-465a-a465-fe15996a0b5b |  | Analog | 1 | 0 | FALSE |  |  |  | 2803 | FALSE
GTD_AL23_52-23_VAB |  | VAB | bbe0ed50-3cd1-454d-809d-09af32f134ea | Voltage | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL23_52-23_VAB |  | 5d61c01b-5a95-4344-bf12-9e3263f31294 |  | Analog | 1 | 0 | FALSE |  |  |  | 2603 | FALSE
GTD_AL23_52-23_P |  | P | 9567f1b0-ddfd-4f15-b7dc-daef5d3816b4 | ActivePower | GTD Distr | [6 empty] | GTD_AL23_52-23_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL23_52-23_P |  | 9b1cf0ac-3587-4e2e-9da8-68ed35340339 |  | Analog | 1000 | 0 | FALSE |  |  |  | 2604 | FALSE
GTD_AL22_52-22_VAB |  | VAB | 9391cc3e-af27-4935-884d-3aa46588af5e | Voltage | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL22_52-22_VAB |  | 13523f33-c0eb-4846-ae6a-323b6db198d4 |  | Analog | 1 | 0 | FALSE |  |  |  | 2503 | FALSE
GTD_TRF1_24-1_IB |  | IB | 00e6755e-9513-40f6-bd07-5a3f57b33352 | Current | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_TRF1_24-1_IB |  | 49c3f670-ab30-45da-a3df-8ee2404611f7 |  | Analog | 1 | 0 | FALSE |  |  |  | 2001 | FALSE
GTD_AL24_52-24_VAB |  | VAB | 34993fef-c469-4cc0-9699-f2ead1dd047a | Voltage | GTD Distr | [6 empty] | GTD_AL24_52-24_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL24_52-24_VAB |  | 659805e2-dfb5-4274-b99d-57415ab3df3d |  | Analog | 1 | 0 | FALSE |  |  |  | 2703 | FALSE
GTD_TRF1_24-1_P |  | P | efb4bc09-b275-4b23-ade8-87117719b7d5 | ActivePower | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRF1_24-1_P |  | 99bd846e-dc6d-4d7f-bf8d-3bd45bd8d04c |  | Analog | 1000 | 0 | FALSE |  |  |  | 2004 | FALSE
GTD_AL15_52-15_VAB |  | VAB | b4ed0ac1-290c-48f5-a7ee-98b5ad347683 | Voltage | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL15_52-15_VAB |  | ea315105-2085-4628-9890-37f2f7c3d2b3 |  | Analog | 1 | 0 | FALSE |  |  |  | 1903 | FALSE
GTD_AL14_52-14_Q |  | Q | ac9a617b-5ffe-40ea-ae06-43e4bf88cabe | ReactivePower | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL14_52-14_Q |  | abc66832-91f2-4f5b-831a-829edb3c4f90 |  | Analog | 1000 | 0 | FALSE |  |  |  | 1805 | FALSE
GTD_TRF1_24-1_VAB |  | VAB | 2a4881db-7c4c-45f1-bd83-633aa54c52dc | Voltage | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRF1_24-1_VAB |  | 10324d52-821a-4106-b373-a8aef6633748 |  | Analog | 1 | 0 | FALSE |  |  |  | 2003 | FALSE
GTD_AL22_52-22_Q |  | Q | 273eac41-a3b4-4af2-9672-9fec85bda3b0 | ReactivePower | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL22_52-22_Q |  | af0b8ea0-c84b-432a-8a8e-2cf7b57446bc |  | Analog | 1000 | 0 | FALSE |  |  |  | 2505 | FALSE
GTD_TRF2_24-2_VAB |  | VAB | ef81a5b2-cfda-485a-93b2-bf0a3b0e2927 | Voltage | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRF2_24-2_VAB |  | c59ed716-722e-4c6c-bf88-5f3c6c6f6be1 |  | Analog | 1 | 0 | FALSE |  |  |  | 2903 | FALSE
GTD_AL13_52-13_VAB |  | VAB | 843b4da4-44fc-4f3a-97a4-c1a7cfd1658e | Voltage | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL13_52-13_VAB |  | 5f6d5c0f-1666-44d9-83db-c60aea2912bc |  | Analog | 1 | 0 | FALSE |  |  |  | 1703 | FALSE
GTD_AL14_52-14_VAB |  | VAB | 3c2c2a12-3b92-4694-851b-2c3983158d14 | Voltage | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL14_52-14_VAB |  | 212347a6-eba9-4c74-bb4f-e460be336cb7 |  | Analog | 1 | 0 | FALSE |  |  |  | 1803 | FALSE
GTD_AL15_52-15_IB |  | IB | 60d90968-070d-4584-aeed-6f84af749082 | Current | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL15_52-15_IB |  | 93754c7b-e2c3-4a42-923c-1a0d83ea14ce |  | Analog | 1 | 0 | FALSE |  |  |  | 1901 | FALSE
GTD_AL25_52-25_IC |  | IC | 4d5c7837-cf87-4c23-b46b-a176a62079d2 | Current | GTD Distr | [6 empty] | GTD_AL25_52-25_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL25_52-25_IC |  | 33216592-e641-4140-873c-a6a17bdf95a2 |  | Analog | 1 | 0 | FALSE |  |  |  | 2802 | FALSE
GTD_AL22_52-22_IC |  | IC | 2d09405a-f532-4169-8f4c-f68cd79c0e63 | Current | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL22_52-22_IC |  | 57b64194-8a64-4542-af4c-4e88ecca8520 |  | Analog | 1 | 0 | FALSE |  |  |  | 2502 | FALSE
GTD_TRF2_24-2_Q |  | Q | 8a553073-3515-451d-b527-2c593a95a982 | ReactivePower | GTD Distr | [6 empty] | GTD_TRF2_24-02_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRF2_24-2_Q |  | 816dc3e7-9b9b-49ad-9ab5-3f840c20babf |  | Analog | 1000 | 0 | FALSE |  |  |  | 2905 | FALSE
GTD_AL13_52-13_Q |  | Q | 3af62c5d-a755-40b9-8160-408e06103175 | ReactivePower | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL13_52-13_Q |  | 01fb91bb-feb8-4787-b9f3-33b6d73a6125 |  | Analog | 1000 | 0 | FALSE |  |  |  | 1705 | FALSE
GTD_AL14_52-14_IA |  | IA | 8fc23970-419e-4038-a67a-f1b38ec66a1f | Current | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL14_52-14_IA |  | 8b87314a-f8bf-47b4-a75d-a9b4e9533b7e |  | Analog | 1 | 0 | FALSE |  |  |  | 1800 | FALSE
GTD_AL14_52-14_IC |  | IC | c5e15191-d30f-4adb-9239-5d821aca9363 | Current | GTD Distr | [6 empty] | GTD_AL14_52-14_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL14_52-14_IC |  | 6cf61756-fca0-455f-82b2-086dd55827cc |  | Analog | 1 | 0 | FALSE |  |  |  | 1802 | FALSE
GTD_AL15_52-15_P |  | P | 83f1850b-89d7-434a-831f-1017f31c6d92 | ActivePower | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_AL15_52-15_P |  | 0b6c3684-f66b-4286-80c4-74f74bd6e588 |  | Analog | 1000 | 0 | FALSE |  |  |  | 1904 | FALSE
GTD_AL22_52-22_IA |  | IA | 7ebe27d4-aebd-42cf-967f-1af512e0bb79 | Current | GTD Distr | [6 empty] | GTD_AL22_52-22_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL22_52-22_IA |  | a483130f-9ac2-40d8-baca-5833f4c9b25f |  | Analog | 1 | 0 | FALSE |  |  |  | 2500 | FALSE
GTD_AL13_52-13_IC |  | IC | 9b18a6c1-0711-4d80-9b25-1949517b0d13 | Current | GTD Distr | [6 empty] | GTD_AL13_52-13_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL13_52-13_IC |  | 0b2f22fa-c693-4d4e-ac53-ca6c5fd74dda |  | Analog | 1 | 0 | FALSE |  |  |  | 1702 | FALSE
GTD_AL15_52-15_IC |  | IC | b65bd4ff-a17c-401b-b1c2-74b2e49fa810 | Current | GTD Distr | [6 empty] | GTD_AL15_52-15_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_GTD_1 | [9 empty] | GTD_AL15_52-15_IC |  | 61d64ead-b87b-4ae0-8bce-062dc2529665 |  | Analog | 1 | 0 | FALSE |  |  |  | 1902 | FALSE
GTD_TRF1_24-1_Q |  | Q | 019eafac-23fb-4aab-a43e-fa380835cf27 | ReactivePower | GTD Distr | [6 empty] | GTD_TRF1_24-01_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRF1_24-1_Q |  | f7d264bc-7211-49d4-a7ce-05416f71549d |  | Analog | 1000 | 0 | FALSE |  |  |  | 2005 | FALSE
GTD_TRSA_TRSA_P |  | P | eb447a27-58bf-49b0-b158-2883c1b84aea | ActivePower | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | MeasuredValue | ABC | kW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRSA_TRSA_P |  | d15b9d5f-3568-4460-88d2-f02c72e36817 | 20260704 | Analog | 1 | 0 | FALSE |  |  |  | 3404 | FALSE
GTD_BC1_BC1_Q |  | Q | 5af76e58-add3-4127-ad79-6e9bbb00683c | ReactivePower | GTD Trans | [6 empty] | IVB_BC1_BC1_TC |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_BC1_BC1_Q |  | a1751ba0-4b53-4235-bb60-d07abcee32c8 |  | Analog | 1000 | 0 | FALSE |  |  |  | 2105 | FALSE
GTD_LTKGC_LTKGC_A_KMDF |  | KMDF | bf26613b-ec8f-4ce2-8634-cedd97d4655e | Unitless | GTD Trans | [6 empty] | 52-3_GTD |  | Custom | ABC | Default | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_LTKGC_LTKGC_A_KMDF |  | 8676abef-c0c0-4b90-8b43-0b6084e1b9af | 20260113 | Analog | 1 | 0 | FALSE |  |  |  | 210 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_BC1_BC1_VAB |  | VAB | c3faa758-36a3-4f0c-b6a5-8001728ae704 | Voltage | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | VAB_253@237.6_202.4@187_Trans | UTR_GTD_1 | [9 empty] | GTD_BC1_BC1_VAB |  | b2841e7a-190e-47f4-a867-625cf5247ac8 |  | Analog | 1 | 0 | FALSE |  |  |  | 2104 | FALSE
GTD_BC3_52-26_VAB |  | VAB | ddcf54e6-f581-4e0d-a7f4-1e164ea3dea7 | Voltage | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | VAB_253@237.6_202.4@187_Trans | UTR_GTD_1 | [9 empty] | GTD_BC3_52-26_VAB |  | 8d8a3002-612f-4f22-afe6-369388f7b164 |  | Analog | 1 | 0 | FALSE |  |  |  | 3004 | FALSE
GTD_BC3_BC3_IC |  | IC | e51a7ed3-4de7-4599-bc5a-516e15752aa2 | Current | GTD Trans | [6 empty] | IVB_BC1_BC1_TC |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_BC3_BC3_IC |  | 41796179-807f-4453-be6d-3b3a0af5ffa6 |  | Analog | 1 | 0 | FALSE |  |  |  | 3002 | FALSE
GTD_BC4_BC4_Q |  | Q | c9dc9a94-c4f1-4134-8461-0c5e8d8ef457 | ReactivePower | GTD Trans | [6 empty] | IVB_BC1_BC1_TC |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_BC4_BC4_Q |  | 91485155-4cf2-403a-8501-a8a9640e34d9 |  | Analog | 1000 | 0 | FALSE |  |  |  | 3105 | FALSE
GTD_BC4_BC4_IN61 |  | IN61 | a9ce44c2-c819-4679-a010-a135a4ba01cd | Current | GTD Trans | [6 empty] | IVB_BC1_BC1_TC |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_BC4_BC4_IN61 |  | d1ccb381-90d1-4f90-b467-d0bba84fa2ec |  | Analog | 1 | 0 | FALSE |  |  |  | 3103 | FALSE
GTD_BC4_52-27_VAB |  | VAB | 526651e8-1e78-42b2-a4b4-218389542f49 | Voltage | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | VAB_253@237.6_202.4@187_Trans | UTR_GTD_1 | [9 empty] | GTD_BC4_52-27_VAB |  | e76c291b-7dde-42f3-9bb3-0dcdebcd328c |  | Analog | 1 | 0 | FALSE |  |  |  | 3104 | FALSE
GTD_BC2_BC2_IC |  | IC | 18816d85-6bbf-475f-a5f4-4acc229264db | Current | GTD Trans | [6 empty] | IVB_BC1_BC1_TC |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_BC2_BC2_IC |  | e9bd2bec-eb90-45a5-9e49-55d1cf4b2394 |  | Analog | 1 | 0 | FALSE |  |  |  | 2202 | FALSE
GTD_BC2_52-17_VAB |  | VAB | a23a0c9c-054d-42df-a1f5-e030c75f903f | Voltage | GTD Trans | [6 empty] | IVB_BC1_52-16_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | VAB_253@237.6_202.4@187_Trans | UTR_GTD_1 | [9 empty] | GTD_BC2_52-17_VAB |  | f01f408a-3a3d-48d6-95fa-4030cfb49daf |  | Analog | 1 | 0 | FALSE |  |  |  | 2204 | FALSE
GTD_BC3_BC3_IB |  | IB | d49d41f2-dd65-436f-866d-70175a4b2ca2 | Current | GTD Trans | [6 empty] | IVB_BC1_BC1_TC |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_BC3_BC3_IB |  | d2b3a8fc-cd73-4c36-b002-07e0b2111ebc |  | Analog | 1 | 0 | FALSE |  |  |  | 3001 | FALSE
GTD_BC3_BC3_IA |  | IA | cca1f6fd-ed67-4423-8f12-5bf947c4a453 | Current | GTD Trans | [6 empty] | IVB_BC1_BC1_TC |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_BC3_BC3_IA |  | 01ec0c93-e9de-4c6f-b070-f58d59d8d26a |  | Analog | 1 | 0 | FALSE |  |  |  | 3000 | FALSE
GTD_BC3_BC3_Q |  | Q | 2612ced4-d21c-4a1c-8b58-4a094cfb2951 | ReactivePower | GTD Trans | [6 empty] | IVB_BC1_BC1_TC |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_BC3_BC3_Q |  | bb231ede-290c-460c-8515-c39fafd23fd2 |  | Analog | 1000 | 0 | FALSE |  |  |  | 3005 | FALSE
GTD_BC4_BC4_IC |  | IC | 1ea55f0b-779e-4e6a-95d7-8258a5bc6df2 | Current | GTD Trans | [6 empty] | IVB_BC1_BC1_TC |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_BC4_BC4_IC |  | 4c7c46c3-2a81-4ffb-b38a-d36cc887f3c6 |  | Analog | 1 | 0 | FALSE |  |  |  | 3102 | FALSE
GTD_BC3_BC3_IN61 |  | IN61 | bfab8946-8d0f-4fc5-b0bb-5608f988ed09 | Current | GTD Trans | [6 empty] | IVB_BC1_BC1_TC |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_BC3_BC3_IN61 |  | f39e710e-dc25-4155-973a-38bfdb4016ee |  | Analog | 1 | 0 | FALSE |  |  |  | 3003 | FALSE
GTD_BC4_BC4_IB |  | IB | ba559c37-1d72-4ea9-bec2-af09c440f939 | Current | GTD Trans | [6 empty] | IVB_BC1_BC1_TC |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_BC4_BC4_IB |  | 753cd651-c62a-4870-b671-a3954e004ce6 |  | Analog | 1 | 0 | FALSE |  |  |  | 3101 | FALSE
GTD_BC2_BC2_IN61 |  | IN61 | 9f774af1-d46f-4fa0-8764-52edb806e7da | Current | GTD Trans | [6 empty] | IVB_BC1_BC1_TC |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_BC2_BC2_IN61 |  | bb3cda5c-5f66-4ee3-8001-f0437add7c3d |  | Analog | 1 | 0 | FALSE |  |  |  | 2203 | FALSE
GTD_BC4_BC4_IA |  | IA | bd25fd66-2345-4a95-a126-a9abf8a85c6f | Current | GTD Trans | [6 empty] | IVB_BC1_BC1_TC |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_BC4_BC4_IA |  | 7cd5fd0d-c87c-4acf-9cb7-c56e15757ac2 |  | Analog | 1 | 0 | FALSE |  |  |  | 3100 | FALSE
GTD_BC2_BC2_Q |  | Q | ea9773a9-db73-4b0f-9efe-94e349d4b42e | ReactivePower | GTD Trans | [6 empty] | IVB_BC1_BC1_TC |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_BC2_BC2_Q |  | c44d39ea-eac8-45f3-8742-5a500df075a8 |  | Analog | 1000 | 0 | FALSE |  |  |  | 2205 | FALSE
GTD_TRSA_TRSA_IB |  | IB | 8a8d4771-2176-4413-bb16-925c19a396ae | Current | GTD Trans | [6 empty] | GTD_TRSA_RET_RET |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_GTD_1 | [9 empty] | GTD_TRSA_TRSA_IB |  | bc750f74-1ae3-4fe1-b88e-b96d25a00cb2 | 20260704 | Analog | 1 | 0 | FALSE |  |  |  | 3401 | FALSE
GTD_B69_B69_VAB |  | VAB | f5217f41-c4d7-4e5e-8f51-a81697592a10 | Voltage | GTD Trans | [6 empty] | ARV_B69_B69_BP |  | Custom | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | VBC_144.9@143.52_131.1@124.2_Trans | UTR_GTD_1 | [9 empty] | GTD_B69_B69_VAB |  | 32e2b1a3-55d2-47bf-aab3-ccfe69912d96 | 20260401 | Analog | 1 | 0 | FALSE |  |  |  | 1200 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_BP1_BP1_VAB |  | VAB | da031526-309b-4f83-bddc-d49762209177 | Voltage | GTD Trans | [6 empty] | ARV_BP1_BP1_BP |  | Custom | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | VAB_24.15@23.92_22.54@22.31_Trans | UTR_GTD_1 | [9 empty] | GTD_BP1_BP1_VAB |  | aed4d0a8-2b7b-40c6-a59f-da5b497774c6 | 20260401 | Analog | 1 | 0 | FALSE |  |  |  | 1201 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_BP2_BP2_VAB |  | VAB | ddd27748-771f-42fa-a01d-dbe43cad3f5a | Voltage | GTD Trans | [6 empty] | ARV_BP2_BP2_BP |  | Custom | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | VAB_24.15@23.92_22.54@22.31_Trans | UTR_GTD_1 | [9 empty] | GTD_BP2_BP2_VAB |  | a44e137d-3300-4711-b5e1-d5452b70a66c | 20260401 | Analog | 1 | 0 | FALSE |  |  |  | 1202 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0

## DNP3_DiscreteAnalog
Signal Details | [22 empty] | Remote Points
DSIGNAL | [22 empty] | REMOTEPOINT | [17 empty] | APROCESSING
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | MEASUREMENT_TYPE | IDOBJ_AORGROUP | SIGNAL_DEVICEMAPPING | [7 empty] | DSIGNAL_TYPE | MEASUREMENT_PHASE | MEASUREMENT_SIDE | SIGNAL_DIRECTION | SIGNAL_ANNUALSCH | DSIGNAL_NORMALVALUE | DSIGNAL_MAPPING | DSIGNAL_DOMCATALOG | MEASUREMENT_PSR | IDOBJ_NAME | DELETE | IDOBJ_CUSTOMID | IDOBJ_ALIAS | REMOTEPOINT_TYPE | REMOTEPOINT_SCALING | REMOTEPOINT_INTERCEPT | REMOTEPOINT_ADCFAIL | REMOTEOUTPUT_CMDTIMEOUT | REMOTEOUTPUT_SBOMODE | REMOTEOUTPUT_SPTOL | REMOTEINPUTDNP3_INCOORDS¦REMOTEOUTPUTDNP3_INCOORDS | REMOTEINPUTDNP3_OUTREGISTER¦REMOTEOUTPUTDNP3_OUTREGISTER | AOUTPUTDNP3_OUTTYPE | REMOTEOUTPUTDNP3_OUTCOORDS | COUNTERDNP3_ENABLEROLLOVER | COUNTERDNP3_ROLLOVER | COUNTERDNP3_RESET | APROCESSING_LOCALDBCHECK | APROCESSING_USERELATIVEDB | APROCESSING_DEADBANDTYPE | APROCESSING_DEADBAND | APROCESSING_ZEROCLAMPINGDB | APROCESSING_LINEARFILTER | APROCESSING_LFFACTOR
Signal Name | Delete | Signal Alias | Signal Custom ID | Measurement Type | Signal AOR Group | Substation | Feeder | Feeder Object | Bank | Bay | Device | Device Mapping | Description | Signal Type | Phases | Side | Direction | Annual Schedule | Normal Value | Message Mapping | DOM Catalog | Remote Unit | Remote Point Name | Delete Remote Point | Remote Point Custom ID | Remote Point Alias | Remote Point Type | Scaling Factor | Intercept | ADC Fail | Command Timeout [s] | Commanding Mode | Setpoint Tolerance | Input Coordinates | Output Register | Output Data Type | Output Coordinates | Enable Rollover | Rollover Value | With Reset | Advanced Processing - Local Deadband Check | Advanced Processing - Use Relative Deadband | Deadband Type | Advanced Processing - Deadband | Advanced Processing - Zero Clamping Deadband | Advanced Processing - Apply Linear Filter | Advanced Processing - Linear Filter Factor
GTD_TR1_TR1_TAP |  | TAP | 53cdfb7e-f157-4671-a791-7e711bf21d30 | Discrete | GTD Trans | [6 empty] | GTD_TR1_TR1_COMTAP |  | TapPosition | ABC | None | Read |  | 9 |  |  | UTR_GTD_1 | GTD_TR1_TR1_TAP |  | GTD_DA_00001 | 20260204 | Analog | 1 | 0 | FALSE |  |  |  | 623 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
GTD_TR2_TR2_TAP |  | TAP | a36fe97a-70e4-4859-a67e-99cd1c5b6c12 | Discrete | GTD Trans | [6 empty] | GTD_TR2_TR2_COMTAP |  | TapPosition | ABC | None | Read |  | 9 |  |  | UTR_GTD_1 | GTD_TR2_TR2_TAP |  | GTD_DA_00002 | 20260210 | Analog | 1 | 0 | FALSE |  |  |  | 1023 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0

## CalculationCode
Calculation Code
CALCCODE
IDOBJ_NAME | DELETE | PSR_LOCATION | CALCCODE_SHARED | CALCCODE_ROUTINE
Name | Delete | Description | Shared | Code

## CalculationParameter
Calculation Parameters
CALCPARAM
IDOBJ_NAME | CALCARG_PARAMTYPE | CALCARG_ISOUTPUT | CALCARG_CALCULATION
Name | Data Type | Output | Calculation

## Calculations
Calculation
CALCULATION
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_AORGROUP | EQUIPMENT_CONT |  | CALCULATION_TIMEOUT | CALCULATION_CODE | CALCULATION_SCHEDULE
Name | Delete | Alias | AOR Group | Container Name | Container Custom ID | Execution Timeout [s] | Code Name | Schedule

## ConstantCalculationArgument
Calculation Arguments
CALCCONSTARG
CALCARG_CALCULATION | CALCARG_PARAM | CALCCONSTARG_STRING
Calculation | Calculation Parameter | Value

## SignalCalculationArgument
Signal Calculation Arguments
CALCSIGNALARG
CALCARG_CALCULATION | CALCARG_PARAM | CALCSIGNALARG_SIGNAL | CALCSIGNALARG_INPUTTRIGGER | CALCSIGNALARG_DEADBAND
Calculation | Calculation Parameter | Signal Custom ID | Input Trigger | Deadband