## CAPA
RGE DISTRIBUIDORA GAÚCHA DE ENERGIA S.A. | [5 empty] | IMPLEMENTAÇÃO: |  | 2026
Esquema de Conexões da UTR
SE GUAPORÉ |  |  | SIGLA: GPR |  |  |  | END-COS: 120 | END-N2: 120
GERAL
1. Distribuição dos cartões:
|  | SLOT\FILE | 1
|  | A | RTAC 2241 |  |  | (*) - PROTOCOLO DNP3:
|  | B | PW 2243 |  |  | - IP Gateway: 10.7.120.1
|  | C | 24DI 2244-2 |  |  | - IP UTR NOVA: 10.7.120.10
|  | D | 24DI 2244-2 |  |  | - Mscara: 255.255.255.0
|  | E | 24DI 2244-2 |  |  | - Porta COS: 20000
|  | F | 24DI 2244-2 |  |  | - Porta Nível 2: 20001
|  | G | 16DO 2244-3 |  |  | - IP UTR Antiga: 10.7.120.2
|  | H | 16DO 2244-3 |  |  | - IP TS1: 10.7.120.11
|  | I | 8AI 2245-2
J
2. Medições com transdutores digitais
| TD | Equipamento | Comunic: | END: | Entrada |  | Medições:
| SACA | SCHNEIDER PM820 | Modbus | 9 | TS1-15 |  | Vca
| TR1 TM1 | TREETECH MEDIDOR TEMPERATURA | Modbus | 1 | TS1-3 |  | Temp
| TR1 TM2 | TREETECH MEDIDOR TEMPERATURA | Modbus | 2 | TS1-3 |  | Temp
| TR2 TM1 | TREETECH MEDIDOR TEMPERATURA | Modbus | 16 | TS1-4 |  | Temp
| TR2 TM2 | TREETECH MEDIDOR TEMPERATURA | Modbus | 15 | TS1-4 |  | Temp
| TR2 TR3 SPS | TREETECH SUPERV. PARALELISMO | Modbus | 14 | TS1-15 |  | R90
3. Medições com transdutores analógicos
| TA | Equipamento | Entrada: | Scaling(ohms): |  | Saída(mA): | Medições:
4. Relés de proteção
| Módulo | Relé |  | Ender. | Observações |  | Entrada | VELOCIDADE
| LTCAS_21 | 7SA63 |  | 9 | PROTOCOLO IEC-103 |  | TS1-9 | 9600
| LTCAS_67 | 7SJ64 |  | 10 | PROTOCOLO IEC-103 |  | TS1-11 | 9600
| LTPCH_21 | 7SA631 |  | 7 | PROTOCOLO IEC-103 |  | TS1-9 | 9600
| LTPCH_67 | 7SJ64 |  | 8 | PROTOCOLO IEC-103 |  | TS1-11 | 9600
| LTARV_21 | 7SA631 |  | 31 | PROTOCOLO IEC-103 |  | TS1-9 | 9600
| LTARV_67 | 7SJ64 |  | 30 | PROTOCOLO IEC-103 |  | TS1-11 | 9600
| LTKNP_21 | 7SA63 |  | 11 | PROTOCOLO IEC-103 |  | TS1-9 | 9600
| LTKNP_67 | 7SJ64 |  | 12 | PROTOCOLO IEC-103 |  | TS1-11 | 9600
| TR1AT | 7SJ63 |  | 14 | PROTOCOLO IEC-103 |  | TS1-11 | 9600
| TR1DIF | 7UT612 |  | 15 | PROTOCOLO IEC-103 |  | TS1-9 | 9600
| TR1BT | 7SJ621 |  | 16 | PROTOCOLO IEC-103 |  | TS1-9 | 9600
| TR2AT | 7SJ63 |  | 13 | PROTOCOLO IEC-103 |  | TS1-11 | 9600
| TR2DIF | 7UT612 |  | 1 | PROTOCOLO IEC-103 |  | TS1-11 | 9600
| TR2BT | 7SJ62 |  | 2 | PROTOCOLO IEC-103 |  | TS1-9 | 9600
| TR3AT | 7SJ63 |  | 17 | PROTOCOLO IEC-103 |  | TS1-9 | 9600
| TR3DIF | 7UT612 |  | 3 | PROTOCOLO IEC-103 |  | TS1-9 | 9600
| TR3BT | 7SJ62 |  | 4 | PROTOCOLO IEC-103 |  | TS1-11 | 9600
| GPR21 | 7SJ632 |  | 28 | PROTOCOLO IEC-103 |  | TS1-13 | 9600
| GPR22 | COOPER F6 |  | 4 | DNP3.0 |  | TS1-6 | 9600
| GPR23 | NULLEC ADVC |  | 26 | DNP3.0 |  | TS1-7 | 9600
| GPR24 | NULLEC ADVC |  | 27 | DNP3.0 |  | TS1-8 | 9600
| IB23 | 7SJ632 |  | 5 | PROTOCOLO IEC-103 |  | TS1-13 | 9600
| GPR31 | 7SJ632 |  | 18 | PROTOCOLO IEC-103 |  | TS1-13 | 9600
| GPR32 | 7SJ632 |  | 19 | PROTOCOLO IEC-103 |  | TS1-13 | 9600
| GPR33 | 7SJ632 |  | 20 | PROTOCOLO IEC-103 |  | TS1-13 | 9600
| GPR34 | 7SJ632 |  | 21 | PROTOCOLO IEC-103 |  | TS1-13 | 9600
| GPR35 | 7SJ632 |  | 22 | PROTOCOLO IEC-103 |  | TS1-13 | 9600
| GPR36 | 7SJ632 |  | 23 | PROTOCOLO IEC-103 |  | TS1-13 | 9600
| BC1 | 7SJ632 |  | 24 | PROTOCOLO IEC-103 |  | TS1-13 | 9600
| BC2 | 7SJ632 |  | 6 | PROTOCOLO IEC-103 |  | TS1-13 | 9600

## CALCULADOS
Pontos Calculados | [5 empty] | TESTE N2 |  | TESTE N3
EQUIPAMENTO | Módulo | Descrição do ponto: | Lógica | Identificação do ponto | DNP3 | SUL | RGE | SUL | RGE | NIVEL2 | NIVEL3
Analógicos
| B138 | TENSAO AB BARRA |  | BARRA138_TENSAO_VAB | 260
| B69 | TENSAO AB BARRA |  | BARRA69_TENSAO_VAB | 261
| B23P1 | TENSAO AB BARRA |  | BARRAP1_23_TENSAO_VAB | 262
| B23P2 | TENSAO AB BARRA |  | BARRAP2_23_TENSAO_VAB | 263
| TR1 | TAP |  | TR1_TAP | 196
Comandos
| SE | CA_Comando Sirene |  | SE_ALARME_LIGAR | 200
Digitais
| SE | CA_Sensor de Fumaça |  | SE_SENSOR_FUMACA | 1080
| SE | CA_central Armada |  | SE_ALARME_ATIVO | 1081
| SE | CA_Sensor Invasão Externa |  | SENSOR_EXTERNO | 1082
| SE | CA_Sensor Invasão Interna |  | SE_SENSOR_INTERNO | 1083
| SE | CA Sirene Disparada |  | SE_SIRENE_DISPARADA | 1084
| SE | CA VCC_Presente |  | CA_VCC_PRESENTE | 1085
| SE | CA Sensor Defeito |  | SE_SENSOR_DEFEITO | 1086

## SLOT C
SLOT C | UNIDADE TERMINAL REMOTA |  |  | UTR |  |  |  | LOCAL |  | COS |  | COS | S4
DI | Módulo | Descrição | Borne | Identif. | Lógica | Identificação na UTR | DNP3 | SUL | RGE | SUL | RGE | NIVEL2 | NIVEL3
DI-1 |  |  | R1SC-1 |  | CALCULADO | TR1_TAP_BIT1 | -
DI-2 |  |  | R1SC-2 |  | CALCULADO | TR1_TAP_BIT2 | -
DI-3 |  |  | R1SC-3 |  | CALCULADO | TR1_TAP_BIT3 | -
DI-4 |  |  | R1SC-4 |  | CALCULADO | TR1_TAP_BIT4 | -
DI-5 |  |  | R1SC-5 |  | CALCULADO | TR1_TAP_BIT5 | -
DI-6 |  |  | R1SC-6 |  | CALCULADO | TR1_TAP_BIT6 | -
DI-7 | TR1 | TR1 CDC em marcha | R1SC-7 |  |  | TR1_CDC_EM_MARCHA | 690
DI-8 | TR1 | TR1 CDC DJ - Desligado | R1SC-8 |  |  | TR1_CDC_DJ_DESLIGADO | 691
DI-9 | TR1BT | DJ Falta Vca Aquecimento | R1SC-9 |  |  | TR1BT_DJ_FVCA_AQUEC | 692
| COMUM (-) CC CONTATOS |  | R1SC-10
DI-10 | TR1BT | DJ Falta Vcc Circ Fechamento | R1SC-11 |  |  | TR1BT_DJ_FVCC_CIRC_CLOSE | 693
| COMUM (-) CC CONTATOS |  | R1SC-12
DI-11 | TR1AT | DJ Falta Vca Aquecimento | R1SC-13 |  |  | TR1AT_DJ_FALTA_VCA_AQUEC | 694
| COMUM (-) CC CONTATOS |  | R1SC-14
DI-12 | TR1AT | DJ Falta Vcc Circ Fechamento | R1SC-15 |  |  | TR1AT_DJ_FALTA_VCC_CLOSE | 695
| COMUM (-) CC CONTATOS |  | R1SC-16
DI-13 | TR1AT | Defeito Relé | R1SC-17 |  |  | TR1AT_DEFEITO_RELE | 696
DI-14 | TR1 | Defeito Relé | R1SC-18 |  |  | TR1DIF_DEFEITO_RELE | 697
DI-15 | TR1BT | Defeito Relé | R1SC-19 |  |  | TR1BT_DEFEITO_RELE | 698
DI-16 | TR1 | VF12 - Defeito | R1SC-20 |  |  | TR1_VF1_2_DEFEITO | 699
DI-17 | TR1 | VF1 - Ligada | R1SC-21 |  |  | TR1_VF1_LIGADA | 700
DI-18 | TR1 | VF2 - Ligada | R1SC-22 |  |  | TR1_VF2_LIGADA | 701
DI-19 | TR1 | 71T Max Min - Alarme | R1SC-23 |  |  | TR1_OLEO_TR_MAX_MIN_AL | 702
DI-20 | TR1 | 71C Max Min - Alarme | R1SC-24 |  |  | TR1_OLEO_CDC_MAX_MIN_AL | 703
DI-21 | TR1 | Relé 90 - Excluído | R1SC-25 |  |  | TR1_90_EXCLUIDO | 704
| COMUM (-) CC CONTATOS |  | R1SC-26
DI-22 | TR1 | TM11 - Defeito relé | R1SC-27 |  |  | TR1_DEFEITO_TM1_1 | 705
| COMUM (-) CC CONTATOS |  | R1SC-28
DI-23 | TR1 | TM12 - Defeito relé | R1SC-29 |  |  | TR1_DEFEITO_TM1_2 | 706
| COMUM (-) CC CONTATOS |  | R1SC-30
DI-24 | TR1 | 86T Falta Vcc Circuito | R1SC-31 |  |  | TR1_FVCC_86T1 | 707
| COMUM (-) CC CONTATOS |  | R1SC-32

## SLOT D
SLOT D | UNIDADE TERMINAL REMOTA |  |  | UTR |  |  |  | LOCAL |  | COS |  | COS | S4
DI | Módulo | Descrição | Borne | Identif. | Lógica | Identificação na UTR | DNP3 | SUL | RGE | SUL | RGE | NIVEL2 | NIVEL3
DI-1 | TR2AT | Defeito Relé | R1SD-1 |  |  | TR2AT_DEFEITO_RELE_15F1 | 541
DI-2 | TR2 | Defeito Relé | R1SD-2 |  |  | TR2DIF_DEFEITO_RELE_15F2 | 542
DI-3 | TR2BT | Defeito Relé | R1SD-3 |  |  | TR2BT_DEFEITO_RELE_15F3 | 543
DI-4 | TR2 | 71T Max Min - Alarme | R1SD-4 |  |  | TR2_NIVOLEO_TR_MAXMIN | 544
DI-5 | TR2 | 71C Max Min - Alarme | R1SD-5 |  |  | TR2_NIVOLEO_CDC_MAXMIN | 545
DI-6 | TR2 | VF1 - Defeito | R1SD-6 |  |  | TR2_VF1_DEFEITO | 546
DI-7 | TR2 | VF2 - Defeito | R1SD-7 |  |  | TR2_VF2_DEFEITO | 547
DI-8 | TR2 | VF1 - Ligada | R1SD-8 |  |  | TR2_VF1_LIGADO | 548
DI-9 | TR2 | VF2 - Ligada | R1SD-9 |  |  | TR2_VF2_LIGADO | 549
| COMUM (-) CC CONTATOS |  | R1SD-10
DI-10 | TR2 | TM - Defeito relé | R1SD-11 |  |  | TR2_TM12_DEFEITO_RELE | 550
| COMUM (-) CC CONTATOS |  | R1SD-12
DI-11 | TR3 | 71T Max Min - Alarme | R1SD-13 |  |  | TR3_OLEO_TR_MAX_MIN_AL | 444
| COMUM (-) CC CONTATOS |  | R1SD-14
DI-12 | TR3 | 71C Max Min - Alarme | R1SD-15 |  |  | TR3_OLEO_CDC_MAX_MIN_AL | 445
| COMUM (-) CC CONTATOS |  | R1SD-16
DI-13 |  | SENSORES EXTERNOS | R1SD-17 |  |  | SE_SENSOR_EXTERNO | CALC
DI-14 |  | SENSORES INTERNOS | R1SD-18 |  |  | SE_SENSOR_INTERNO | CALC
DI-15 |  | SENSORES FUMAÇA | R1SD-19 |  |  | SE_SENSOR_FUMACA | CALC
DI-16 |  | CHAVE LIGAR/DESLIGAR | R1SD-20 |  |  | CA_COMANDO_LOCAL | CALC
DI-17 |  | SUPERVISAO 125Vcc | R1SD-21 |  |  | CA_VCC_PRESENTE | CALC
DI-18 | TR3AT | Defeito Relé | R1SD-22 |  |  | TR3AT_DEFEITO_RELE_04F1 | 446
DI-19 | TR3 | Defeito Relé | R1SD-23 |  |  | TR3DIF_DEFEITO_RELE_04F2 | 447
DI-20 | TR3BT | Defeito Relé | R1SD-24 |  |  | TR3BT_DEFEITO_RELE_04F3 | 448
DI-21 | TR3 | VF1 - Defeito | R1SD-25 |  |  | TR3_VF1_DEFEITO | 449
| COMUM (-) CC CONTATOS |  | R1SD-26
DI-22 | TR3 | VF2 - Defeito | R1SD-27 |  |  | TR3_VF2_DEFEITO | 450
| COMUM (-) CC CONTATOS |  | R1SD-28
DI-23 | TR3 | VF1 - Ligada | R1SD-29 |  |  | TR3_VF1_LIGADA | 451
| COMUM (-) CC CONTATOS |  | R1SD-30
DI-24 | TR3 | VF2 - Ligada | R1SD-31 |  |  | TR3_VF2_LIGADA | 452
| COMUM (-) CC CONTATOS |  | R1SD-32

## SLOT E
SLOT E | UNIDADE TERMINAL REMOTA |  |  | UTR |  |  |  | LOCAL |  | COS |  | COS | S4
DI | Módulo | Descrição | Borne | Identif. | Lógica | Identificação na UTR | DNP3 | SUL | RGE | SUL | RGE | NIVEL2 | NIVEL3
DI-1 | TR3 | CDC - Falta Vca Painel | R1SE-1 |  |  | TR3_CDC_FALTA_VCA_PAINEL | 453
DI-2 | LT CAS | Defeito Relé | R1SE-2 |  |  | LT21CAS_DEFEITO_RELE_25F1 | 966
DI-3 | LT CAS | Defeito Relé | R1SE-3 |  |  | LT67CAS_DEFEITO_RELE_25F2 | 967
DI-4 | LT CAS | DJ Falta Vca Aquecimento | R1SE-4 |  |  | LTCAS_DJ_FALTA_VCA_AQUEC | 968
DI-5 | LT CAS | DJ Falta Vcc Circ Fechamento | R1SE-5 |  |  | LTCAS_DJ_FALTA_VCC_CLOSE | 969
DI-6 | LT KNP | Defeito Relé | R1SE-6 |  |  | LT21KNP_DEFEITO_RELE_02F1 | 880
DI-7 | LT KNP | Defeito Relé | R1SE-7 |  |  | LT67KNP_DEFEITO_RELE_02F2 | 881
DI-8 | LT ARV | Defeito Relé | R1SE-8 |  |  | LT21ARV_FALHA_RELE_26F1 | 1070
DI-9 | LT ARV | Defeito Relé | R1SE-9 |  |  | LT67ARV_FALHA_RELE_26F2 | 1071
| COMUM (-) CC CONTATOS |  | R1SE-10
DI-10 | GPR23 | Defeito Relé | R1SE-11 |  |  | ALGPR23_DEFEITO_RELE | 74
| COMUM (-) CC CONTATOS |  | R1SE-12
DI-11 | GPR23 | Telecomando (43TC) - Excluído | R1SE-13 |  |  | ALGPR23_43TC_EXCLUIDA | 75
| COMUM (-) CC CONTATOS |  | R1SE-14
DI-12 | GPR23 | Proteção 26/49 - Incluida | R1SE-15 |  |  | ALGPR23_26_49_INCLUIDA | 76
| COMUM (-) CC CONTATOS |  | R1SE-16
DI-13 | B138 | 86BF Falta Vcc Circuito | R1SE-17 |  |  | B138_FALTA_VCC_86FD | 796
DI-14 | LT PCH | Defeito Relé | R1SE-18 |  |  | LT21PCH_DEFEITO_RELE_24F1 | 797
DI-15 | LT PCH | Defeito Relé | R1SE-19 |  |  | LT67PCH_DEFEITO_RELE_24F2 | 798
DI-16 | LT PCH | MDJ TP Barra - Desligado | R1SE-20 |  |  | LTPCH_MDJ_TP_PROT_ABERTO | 799
DI-17 | LT PCH | MDJ TP Linha - Desligado | R1SE-21 |  |  | LTPCH_MINIDJ_TP_69_ABERTO | 800
DI-18 |  | Reserva | R1SE-22 |  |  |  | -
DI-19 |  | Reserva | R1SE-23 |  |  |  | -
DI-20 |  | Reserva | R1SE-24 |  |  |  | -
DI-21 |  | Reserva | R1SE-25 |  |  |  | -
| COMUM (-) CC CONTATOS |  | R1SE-26
DI-22 | GPR24 | Defeito Relé | R1SE-27 |  |  | ALGPR24_DEFEITO_RELE | 95
| COMUM (-) CC CONTATOS |  | R1SE-28
DI-23 | GPR24 | Telecomando (43TC) - Excluído | R1SE-29 |  |  | ALGPR24_43TC_EXCLUIDA | 96
| COMUM (-) CC CONTATOS |  | R1SE-30
DI-24 | GPR24 | Proteção 26/49 - Incluida | R1SE-31 |  |  | ALGPR24_26_49_INCLUIDA | 97
| COMUM (-) CC CONTATOS |  | R1SE-32

## SLOT F
SLOT F | UNIDADE TERMINAL REMOTA |  |  | UTR |  |  |  | LOCAL |  | COS |  | COS | S4
DI | Módulo | Descrição | Borne | Identif. | Lógica | Identificação na UTR | DNP3 | SUL | RGE | SUL | RGE | NIVEL2 | NIVEL3
DI-1 | BC1 | Defeito Relé | R1SF-1 |  |  | BC1_DEFEITO_RELE_19F1 | 329
DI-2 | BC2 | Defeito Relé | R1SF-2 |  |  | BC2_DEFEITO_RELE_22F1 | 353
DI-3 | GPR21 | Defeito Relé | R1SF-3 |  |  | ALGPR21_DEFEITO_RELE | 33
DI-4 | GPR22 | Defeito Relé | R1SF-4 |  |  | ALGPR22_DEFEITO_RELE | 55
DI-5 | GPR31 | Defeito Relé | R1SF-5 |  |  | ALGPR31_DEFEITO_RELE_11F1 | 128
DI-6 | GPR32 | Defeito Relé | R1SF-6 |  |  | ALGPR32_DEFEITO_RELE_10F1 | 160
DI-7 | GPR33 | Defeito Relé | R1SF-7 |  |  | ALGPR33_DEFEITO_RELE_09F1 | 193
DI-8 | GPR34 | Defeito Relé | R1SF-8 |  |  | ALGPR34_DEFEITO_RELE_08F1 | 223
DI-9 | GPR35 | Defeito Relé | R1SF-9 |  |  | ALGPR35_DEFEITO_RELE_07F1 | 253
| COMUM (-) CC CONTATOS |  | R1SF-10
DI-10 | GPR36 | Defeito Relé | R1SF-11 |  |  | ALGPR36_DEFEITO_RELE_06F1 | 283
| COMUM (-) CC CONTATOS |  | R1SF-12
DI-11 | IB23 | Defeito Relé | R1SF-13 |  |  | IB23_DEFEITO_RELE_14F1 | 309
| COMUM (-) CC CONTATOS |  | R1SF-14
DI-12 | SE |  | R1SF-15 |  |  | SE_PORTA_SAL_COM_ALARME | 1090
| COMUM (-) CC CONTATOS |  | R1SF-16
DI-13 | SA |  | R1SF-17 |  |  | SA_CA_RET_ALARME | 1091
DI-14 | SA |  | R1SF-18 |  |  | SACA_FALTA_FASE | 1092
DI-15 |  | Reserva | R1SF-19 |  |  |  | -
DI-16 |  | Reserva | R1SF-20 |  |  |  | -
DI-17 |  | Reserva | R1SF-21 |  |  |  | -
DI-18 |  | Reserva | R1SF-22 |  |  |  | -
DI-19 |  | Reserva | R1SF-23 |  |  |  | -
DI-20 |  | Reserva | R1SF-24 |  |  |  | -
DI-21 |  | Reserva | R1SF-25 |  |  |  | -
| COMUM (-) CC CONTATOS |  | R1SF-26
DI-22 |  | Reserva | R1SF-27 |  |  |  | -
| COMUM (-) CC CONTATOS |  | R1SF-28
DI-23 |  | Reserva | R1SF-29 |  |  |  | -
| COMUM (-) CC CONTATOS |  | R1SF-30
DI-24 |  | Reserva | R1SF-31 |  |  |  | -
| COMUM (-) CC CONTATOS |  | R1SF-32

## SLOT G
SLOT F | UNIDADE TERMINAL REMOTA |  |  | UTR |  |  |  | LOCAL |  | COS |  | N2 | COS
DI | Módulo | Descrição | BornF | Identif. | Lógica | Identificação na UTR | DNP3 | SUL | RGE | SUL | RGE | NIVEL2 | NIVEL3
DO-1 |  |  | R1SG-1/2
DO-2 |  |  | R1SG-3/4
DO-3 |  |  | R1SG-5/6
DO-4 |  |  | R1SG-7/8
DO-5 |  |  | R1SG-9/10
DO-6 |  |  | R1SG-11/12
DO-7 |  |  | R1SG-13/14
DO-8 |  |  | R1SG-15/16
DO-9 |  |  | R1SG-17/18
DO-10 |  |  | R1SG-19/20
DO-11 |  |  | R1SG-21/22
DO-12 |  |  | R1SG-23/24
DO-13 |  |  | R1SG-25/26
DO-14 |  |  | R1SG-27/28
DO-15 |  |  | R1SG-29/30
DO-16 |  |  | R1SG-31/32

## SLOT H
SLOT F | UNIDADE TERMINAL REMOTA |  |  | UTR |  |  |  | LOCAL |  | COS |  | N2 | COS
DI | Módulo | Descrição | BornF | Identif. | Lógica | Identificação na UTR | DNP3 | SUL | RGE | SUL | RGE | NIVEL2 | NIVEL3
DO-1 | TR1 | Comandos R90 | R1SH-1/2 |  | SET/RESET | TR1_COMANDOS_R90 | 156
DO-2 | TR1 | Comando TAP | R1SH-3/4 |  | PULSO | TR1_COMANDOS_TAP | 157
DO-3 |  |  | R1SH-5/6 |  | PULSO | TR1_COMANDOS_TAP | -
DO-4 | TR2 | Comando VF1 | R1SH-7/8 |  | SET/RESET | TR2_COMANDOS_VF1 | 138
DO-5 | TR2 | Comando VF2 | R1SH-9/10 |  | SET/RESET | TR2_COMANDOS_VF2 | 139
DO-6 | TR3 | Comando VF1 | R1SH-11/12 |  | PULSO | TR3_COMANDOS_VF1 | 118
DO-7 |  |  | R1SH-13/14 |  | PULSO | TR3_COMANDOS_VF1 | -
DO-8 | B138 | Comando Rearme 86B | R1SH-15/16 |  | PULSO | B138_COMANDOS_86FD | 201
DO-9 | B69 | Comando Rearme 86B | R1SH-17/18 |  | PULSO | B69_COMANDOS_86FD | 202
DO-10 | B23P1 | Comando Rearme 86B | R1SH-19/20 |  | PULSO | B23P1_COMANDOS_86FD | 203
DO-11 | B23P2 | Comando Rearme 86B | R1SH-21/22 |  | PULSO | B23P2_COMANDOS_86FD | 204
DO-12 | GPR23 | Desligamento 26/49 - Excluir/Incluir | R1SH-23/24 |  | PULSO | ALGPR23_COMANDOS_RC | 25
DO-13 |  |  | R1SH-25/26 |  | PULSO | ALGPR23_COMANDOS_RC | -
DO-14 | GPR24 | Desligamento 26/49 - Excluir/Incluir | R1SH-27/28 |  | PULSO | ALGPR24_COMANDOS_RC | 35
DO-15 |  |  | R1SH-29/30 |  | PULSO | ALGPR24_COMANDOS_RC | -
DO-16 |  | SIRENE ALARME | R1SH-31/32 |  | CALCULADO | SE_ALARME_DO | CALC

## SLOT I
SLOT I | UNIDADE TERMINAL REMOTA |  |  | UTR |  |  |  | LOCAL |  | COS |  | N2 | COS
DI | Módulo | Descrição | Borne | Identif. | Lógica | Identificação na UTR | DNP3 | SUL | RGE | SUL | RGE | NIVEL2 | NIVEL3
AI-1 | SA | Tensão Vcc | R1SI-1 |  |  | SA_VCC | 265
AI-2 | TR3 | Temperatura do óleo | R1SI-4 |  |  | TR3_TEMPERATURA_OLEO | 126
AI-3 |  |  | R1SI-6
AI-4 |  |  | R1SI-9
AI-5 |  |  | R1SI-11
AI-6 |  |  | R1SI-14
AI-7 |  |  | R1SI-16
AI-8 |  |  | R1SI-19
AI-9 |  |  | R1SI-21
AI-10 |  |  | R1SI-24
AI-11 |  |  | R1SI-26
AI-12 |  |  | R1SI-29
AI-13 |  |  | R1SI-31
AI-14 |  |  | R1SI-34
AI-15 |  |  | R1SI-36
AI-16 |  |  | R1SC-39

## GPR21
SE GUAPORÉ - AL GPR21 - 23 kV
RELÉ 21F1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
7SJ632(End.: 1Ch) | GPR21 | Tensão Barra A-B |  |  |  | AI Val | 134 | 137 | 2015-08-09 | GPR21_TENSAO_AB | 1 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Corrente Fase A |  |  |  | AI Val | 134 | 137 | 9/1 | GPR21_CORRENTE_FA | 2 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Corrente Fase B |  |  |  | AI Val | 134 | 137 | 9/2 | GPR21_CORRENTE_FB | 3 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Corrente Fase C |  |  |  | AI Val | 134 | 137 | 9/3 | GPR21_CORRENTE_FC | 4 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Potencia Ativa |  |  |  | AI Val | 134 | 137 | 9/11 | GPR21_POT_ATIVA | 5 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Potencia Reativa |  |  |  | AI Val | 134 | 137 | 9/12 | GPR21_POT_REATIVA | 6 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Disj. 52-13 (21QA) - Abrir / Fechar |  | 4/5 |  | DiSOEx2 | 240 | 160 | 20 | GPR21_COMANDOS_DJ | 1 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Religamento (79) - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 169 | 20 | GPR21_COMANDOS_79 | 2 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Relé Neutro (51N) - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 170 | 20 | GPR21_COMANDOS_PN | 3 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Desligamento 26/49 - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 171 | 20 | GPR21_COMANDOS_RC | 4 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Disj. 52-13 (21QA) - Aberto | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | GPR21_DJ_ABERTO | 1 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Disj. 52-13 (21QA) - Fechado | 2 |  |  | DiSOEx2 | 240 | 160 | 1 | GPR21_DJ_FECHADO | 2 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Disj.- Mola descarregada | 3 |  |  | DiVal | 240 | 191 | 1 | GPR21_DJ_MOLA_DESC | 3 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Disj.- Falta VCC Comando | 4 |  |  | DiVal | 240 | 192 | 1 | GPR21_DJ_FVCC_COMANDO | 4 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Disj.- Falta VCC Motor | 5 |  |  | DiVal | 240 | 193 | 1 | GPR21_DJ_FVCC_MOTOR | 5 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Disj.- Chave 43L/R em posição LOCAL | 6 |  |  | DiVal | 240 | 194 | 1 | GPR21_DJ_43LR_LOCAL | 6 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Disj.- Sup.Circuito de Abertura | 7 |  |  | DiVal | 170 | 56 | 1 | GPR21_DJ_CIRC_TRIP_ALM | 7 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Reserva | 8 - 15 |  |  | - | - | - | - | Reserva | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | TRIP de desligamento p/26/49 TR3 - Atuado | 16 | 4 |  | - | - | - | - | INTERTRAVAMENTO! | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Reserva | 17 - 20 |  |  | - | - | - | - | Reserva | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | TRIP de desligamento p/26/49 TR3 - Atuado | 21 | 4 |  | - | - | - | - | INTERTRAVAMENTO! | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Rele 86FD-TR2 - Atuado | 22 |  |  | - | - | - | - | INTERTRAVAMENTO! | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | TRIP de desligamento p/26/49 TR3 - Atuado | 23 | 4 |  | - | - | - | - | INTERTRAVAMENTO! | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Reserva | 24 |  |  | - | - | - | - | Reserva | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Telecomando (43TC) - Excluído |  |  |  | DiVal | 101 | 85 | 1 | GPR21_43TC_EXCLUIDA | 8 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 26/49 - Incluida |  |  |  | DiVal | 240 | 198 | 1 | GPR21_43RC_INCLUIDA | 9 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Grupo de Ajuste B Ativo - (51N Excluido) |  |  |  | DiVal | 240 | 199 | 1 | GPR21_GRPB_ATIVADO | 10 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Religamento - Disparo |  | 5 |  | AF | 160 | 128 | 2 | GPR21_79_DISPARO | 11 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Religamento - Excluído |  |  |  | DiVal | 40 | 81 | 1 | GPR21_79_EXCLUIDO | 12 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Religamento - Sucedido |  |  |  | DiVal | 40 | 162 | 1 | GPR21_79_SUCEDIDO | 13 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Religamento - Bloqueado |  |  |  | FDI | 40 | 163 | 2 | GPR21_79_BLOQUEADO | 14 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 50BF - Atuado |  | 15 |  | AF | 160 | 85 | 2 | GPR21_50BF_ATUADO | 15 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 50 ABC - Estágio 1 - Atuado |  | 4 |  | AF | 160 | 90 | 2 | GPR21_50ABC_E1_ATUADO | 16 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 50 ABC - Estágio 2 - Atuado |  | 4 |  | AF | 160 | 91 | 2 | GPR21_50ABC_E2_ATUADO | 17 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 50 N - Estágio 1 - Atuado |  | 4 |  | AF | 160 | 92 | 2 | GPR21_50N_E1_ATUADO | 18 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 50 N - Estágio 2 - Atuado |  | 4 |  | AF | 160 | 93 | 2 | GPR21_50N_E2_ATUADO | 19 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 50/51 Fase A - Atuado |  | 4 |  | FDI | 60 | 54 | 2 | GPR21_50FA_51FA_ATUADO | 20 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 50/51 Fase B - Atuado |  | 4 |  | FDI | 60 | 55 | 2 | GPR21_50FB_51FB_ATUADO | 21 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 50/51 Fase C - Atuado |  | 4 |  | FDI | 60 | 56 | 2 | GPR21_50FC_51FC_ATUADO | 22 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 51 ABC - Atuado |  | 4 |  | FDI | 60 | 58 | 2 | GPR21_51ABC_ATUADO | 23 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 51 N - Atuado |  | 4 |  | FDI | 60 | 66 | 2 | GPR21_51N_ATUADO | 24 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Sequência Negativa - Atuado |  | 4 |  | FDI | 70 | 149 | 2 | GPR21_46_ATUADO | 25 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Sub/Sobre Frequencia - Estágio 1 - Atuado |  | 4 |  | FDI | 70 | 234 | 2 | GPR21_81_E1_ATUADO | 26 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Sub/Sobre Frequencia - Estágio 2 - Atuado |  | 4 |  | FDI | 70 | 235 | 2 | GPR21_81_E2_ATUADO | 27 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Falta Sensitiva à Terra - Estágio 1 - Atuado |  | 4 |  | FDI | 151 | 126 | 2 | GPR21_50Ns_E1_ATUADO | 28 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Falta Sensitiva à Terra - Estágio 2 - Atuado |  | 4 |  | FDI | 151 | 123 | 2 | GPR21_50Ns_E2_ATUADO | 29 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 27 - Atuada |  | 4 |  | FDi | 74 | 81 | 2 | GPR21_27_ATUADO | 30 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 59 - Atuada |  | 4 |  | FDi | 74 | 83 | 2 | GPR21_59_ATUADO | 31 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Saude Comunicação |  |  |  | - | - | - | - | GPR21_SAUDE_COMUNIC | 32 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## GPR22
SE GUAPORÉ - AL GPR22 - 23 kV
RELÉ 22F1 |  | PONTO | RELÉ |  |  | DNP3.0 |  |  |  |  | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Objeto | ID | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
FORM 6 (End:4) | GPR22 | Tensão fase B |  |  |  | Analógico | 30 | 29 | GPR22_TENSAO_FB | 10 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Corrente fase A |  |  |  | Analógico | 30 | 0 | GPR22_CORRENTE_FA | 11 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Corrente fase B |  |  |  | Analógico | 30 | 1 | GPR22_CORRENTE_FB | 12 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Corrente fase C |  |  |  | Analógico | 30 | 2 | GPR22_CORRENTE_FC | 13 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Potencia Ativa |  |  |  | Analógico | 30 | 25 | GPR22_POT_ATIVA | 14 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Potencia Reativa |  |  |  | Analógico | 30 | 26 | GPR22_POT_REATIVA | 15 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Tensão Bateria |  |  |  | Analógico | 30 | 23 | GPR22_TENSAO_BATERIAS | 16 | [10 empty] | #N/A | #N/A | #N/A
| Controle | [19 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Disjuntor 52-12 Abrir/Fechar |  | 4/5 |  | Comando | 12 | 18 | GPR22_COMANDOS_DJ | 10 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Religador - Excluir/Incluir |  |  |  | Comando | 12 | 2 | GPR22_COMANDOS_79 | 11 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | 50/51N - Excluir/Incluir |  |  |  | Comando | 12 | 3 | GPR22_COMANDOS_PN | 12 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Perfil Normal - Ativar/Desativar |  |  |  | Comando | 12 | 7 | GPR22_COMANDOS_PERF0 | 13 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Perfil Altenativo - Ativar/Desativar |  |  |  | Comando | 12 | 8 | GPR22_COMANDOS_PERF1 | 14 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | 26/49 - Incluir |  |  |  | Comando | 12 | 32 | GPR22_INCLUIR_RC | 15 | 32 incluir 33 excluir | [9 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | 26/49 - Excluir |  |  |  | Comando | 12 | 33 | GPR22_EXCLUIR_RC | - | [10 empty] | #N/A | #N/A | #N/A
| Sinalização | [19 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Disjuntor 52-12 Aberto |  |  |  | DiSOE | 1 | 1 | GPR22_DJ_ABERTO | 34 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Disjuntor 52-12 Fechado |  |  |  | DiSOE | 1 | 0 | GPR22_DJ_FECHADO | 35 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Disj.- Falta VCA Aux.(1) |  |  |  | DiSOE | 1 | 21 | GPR22_FALTA_VCA | 36 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Religador - Bloqueado (1) |  |  |  | DiSOE | 1 | 2 | GPR22_79_BLOQUEADO | 37 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Dis.- Falta VCC/Anormal Baterias(1) |  |  |  | DiSOE | 1 | 22 | GPR22_FALTA_VCC | 38 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | 43TC - Excluida |  |  |  | DiSOE | 1 | 64 | GPR22_43TC_EXCLUIDA | 39 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | 26/49 Rejeição de Carga - Incluída |  |  |  | DiSOE | 1 | 65 | GPR22_43TE_INCLUIDA | 40 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Supervisão - Bloqueada (1) |  |  |  | DiSOE | 1 | 5 | GPR22_43LR_POS_LOCAL | 41 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Religador -Excluído (1) |  |  |  | DiSOE | 1 | 6 | GPR22_79_EXCLUIDO | 42 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | 50N/51N - Excluído (1) |  |  |  | DiSOE | 1 | 7 | GPR22_PN_EXCLUIDA | 43 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | 50BF Atuado |  |  |  | DiSOE | 1 | 63 | GPR22_50BF_ATUADO | 44 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Atuado SGF |  |  |  | DiSOE | 1 | 45 | GPR22_SGF_ATUADA | 45 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Atuado 50N/51 N |  |  |  | DiSOE | 1 | 44 | GPR22_50N_51N_ATUADA | 46 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Atuado 50/51-C |  |  |  | DiSOE | 1 | 43 | GPR22_50FC_51FC_ATUADA | 47 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Atuado 50/51-B |  |  |  | DiSOE | 1 | 42 | GPR22_50FB_51FB_ATUADA | 48 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Atuado 50/51-A |  |  |  | DiSOE | 1 | 41 | GPR22_50FA_51FA_ATUADA | 49 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Atuado 81-1 |  |  |  | DiSOE | 1 | 66 | GPR22_81_1_ATUADO | 50 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Atuado 81-2 |  |  |  | DiSOE | 1 | 67 | GPR22_81_2_ATUADO | 51 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Perfil Normal - Ativado |  |  |  | DiSOE | 1 | 11 | GPR22_PERF0_ATIVADO | 52 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Perfil Alternativo 1 - Ativado |  |  |  | DiSOE | 1 | 12 | GPR22_PERF1_ATIVADO | 53 | [10 empty] | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Saude Comunicação | [6 empty] | GPR22_SAUDE_COMUNIC | 54 | [10 empty] | #N/A | #N/A | #N/A

## GPR23
SE GUAPORÉ - AL GPR23 - 23 kV
RELÉ 23F1 |  | PONTO | RELÉ |  |  | DNP3.0 |  |  |  |  | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Objeto | ID | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
ADVC (End:26) | GPR23 | Corrente Fase A |  |  |  | Analógico | 30 | 0 | GPR23_CORRENTE_FA | 20 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Corrente Fase B |  |  |  | Analógico | 30 | 1 | GPR23_CORRENTE_FB | 21 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Corrente Fase C |  |  |  | Analógico | 30 | 2 | GPR23_CORRENTE_FC | 22 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Potência Reativa |  |  |  | Analógico | 30 | 5 | GPR23_POT_REATIVA | 23 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Tensão Trifásica |  |  |  | Analógico | 30 | 7 | GPR23_TENSAO_3F | 24 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Potência Ativa |  |  |  | Analógico | 30 | 17 | GPR23_POT_ATIVA | 25 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Tensão Bateria |  |  |  | Analógico | 30 | 19 | GPR23_TENSAO_BATERIA | 26 | [10 empty] | #N/A | #N/A | #N/A
| Controle | [19 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Disjuntor 52-11 Abrir/Fechar |  | 4/5 |  | Comando | 12 | 0 | GPR23_COMANDOS_DJ | 20 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Religador - Excluir/Incluir |  |  |  | Comando | 12 | 2 | GPR23_COMANDOS_79 | 21 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | 50/51N - Excluir/Incluir |  |  |  | Comando | 12 | 5 | GPR23_COMANDOS_PN | 22 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Perfil Normal - Ativar/Desativar |  |  |  | Comando | 12 | 6 | GPR23_COMANDOS_PERF0 | 23 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Perfil Altenativo - Ativar/Desativar |  |  |  | Comando | 12 | 7 | GPR23_COMANDOS_PERF1 | 24 | [10 empty] | #N/A | #N/A | #N/A
| Sinalização | [19 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Disjuntor 52-11 ABERTO |  |  |  | DiSOE | 1 | 0 | GPR23_DJ_ABERTO | 56 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Disjuntor 52-11 FECHADO |  |  |  | DiSOE | 1 | 1 | GPR23_DJ_FECHADO | 57 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Chave 43LR LOCAL |  |  |  | DiSOE | 1 | 2 | GPR23_43LR_POS_LOCAL | 58 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | 79 Bloqueado |  |  |  | DiSOE | 1 | 8 | GPR23_79_BLOQUEADO | 59 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Falta CA do Motor do DJ 52-11 |  |  |  | DiSOE | 1 | 9 | GPR23_FALTA_VCA | 60 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Falta CC Disjuntor 52-11 |  |  |  | DiSOE | 1 | 12 | GPR23_FALTA_VCC | 61 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | 51N - Excluído |  |  |  | DiSOE | 1 | 23 | GPR23_PN_EXCLUIDA | 62 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | 79 - Excluido |  |  |  | DiSOE | 1 | 25 | GPR23_79_EXCLUIDO | 63 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | 50/51 Fase A Atuado |  |  |  | DiSOE | 1 | 27 | GPR23_50FA_51FA_ATUADA | 64 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | 50/51 Fase B Atuado |  |  |  | DiSOE | 1 | 28 | GPR23_50FB_51FB_ATUADA | 65 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | 50/51 Fase C Atuado |  |  |  | DiSOE | 1 | 29 | GPR23_50FC_51FC_ATUADA | 66 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | 50N/51N Atuado |  |  |  | DiSOE | 1 | 30 | GPR23_50N_51N_ATUADA | 67 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Falta Sensitiva a Terra Estágio 1 |  |  |  | DiSOE | 1 | 31 | GPR23_SGF_ATUADA | 68 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | GPR AL23 Modo Normal |  |  |  | DiSOE | 1 | 32 | GPR23_PERF0_ATIVADO | 69 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | GPR AL23 Modo Perfil Alternativo 1 |  |  |  | DiSOE | 1 | 34 | GPR23_PERF1_ATIVADO | 70 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | 81 Estágio 1 Atuado |  |  |  | DiSOE | 1 | 45 | GPR23_81_E1_ATUADA | 71 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | 81 Estágio 2 Atuado |  |  |  | DiSOE | 1 | 46 | GPR23_81_E2_ATUADA | 72 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Saude Comunicação |  |  |  | DiSOE |  | - | GPR23_SAUDE_COMUNIC | 73 | [10 empty] | #N/A | #N/A | #N/A

## GPR24
SE GUAPORÉ - AL GPR24 - 23 kV
RELÉ 24F1 |  | PONTO | RELÉ |  |  | DNP3.0 |  |  |  |  | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Objeto | ID | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
ADVC (End:27) | GPR24 | Corrente Fase A |  |  |  | Analógico | 30 | 0 | GPR24_CORRENTE_FA | 30 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Corrente Fase B |  |  |  | Analógico | 30 | 1 | GPR24_CORRENTE_FB | 31 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Corrente Fase C |  |  |  | Analógico | 30 | 2 | GPR24_CORRENTE_FC | 32 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Potência Reativa |  |  |  | Analógico | 30 | 5 | GPR24_POT_REATIVA | 33 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Tensão Trifásica |  |  |  | Analógico | 30 | 7 | GPR24_TENSAO_3F | 34 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Potência Ativa |  |  |  | Analógico | 30 | 17 | GPR24_POT_ATIVA | 35 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Tensão Bateria |  |  |  | Analógico | 30 | 19 | GPR24_TENSAO_BATERIA | 36 | [10 empty] | #N/A | #N/A | #N/A
| Controle | [19 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Disjuntor 52-10 Abrir/Fechar |  | 4/5 |  | Comando | 12 | 0 | GPR24_COMANDOS_DJ | 30 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Religador - Excluir/Incluir |  |  |  | Comando | 12 | 2 | GPR24_COMANDOS_79 | 31 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | 50/51N - Excluir/Incluir |  |  |  | Comando | 12 | 5 | GPR24_COMANDOS_PN | 32 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Perfil Normal - Ativar/Desativar |  |  |  | Comando | 12 | 6 | GPR24_COMANDOS_PERF0 | 33 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Perfil Altenativo - Ativar/Desativar |  |  |  | Comando | 12 | 7 | GPR24_COMANDOS_PERF1 | 34 | [10 empty] | #N/A | #N/A | #N/A
| Sinalização | [19 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Disjuntor 52-10 ABERTO |  |  |  | DiSOE | 1 | 0 | GPR24_DJ_ABERTO | 77 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Disjuntor 52-10 FECHADO |  |  |  | DiSOE | 1 | 1 | GPR24_DJ_FECHADO | 78 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Chave 43LR LOCAL |  |  |  | DiSOE | 1 | 2 | GPR24_43LR_POS_LOCAL | 79 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | 79 Bloqueado |  |  |  | DiSOE | 1 | 8 | GPR24_79_BLOQUEADO | 80 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Falta CA do Motor do DJ 52-10 |  |  |  | DiSOE | 1 | 9 | GPR24_FALTA_VCA | 81 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Falta CC Disjuntor 52-10 |  |  |  | DiSOE | 1 | 12 | GPR24_FALTA_VCC | 82 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | 51N - Excluído |  |  |  | DiSOE | 1 | 23 | GPR24_PN_EXCLUIDA | 83 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | 79 - Excluido |  |  |  | DiSOE | 1 | 25 | GPR24_79_EXCLUIDO | 84 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | 50/51 Fase A Atuado |  |  |  | DiSOE | 1 | 27 | GPR24_50FA_51FA_ATUADA | 85 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | 50/51 Fase B Atuado |  |  |  | DiSOE | 1 | 28 | GPR24_50FB_51FB_ATUADA | 86 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | 50/51 Fase C Atuado |  |  |  | DiSOE | 1 | 29 | GPR24_50FC_51FC_ATUADA | 87 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | 50N/51N Atuado |  |  |  | DiSOE | 1 | 30 | GPR24_50N_51N_ATUADA | 88 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Falta Sensitiva a Terra Estágio 1 |  |  |  | DiSOE | 1 | 31 | GPR24_SGF_ATUADA | 89 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | GPR AL23 Modo Normal |  |  |  | DiSOE | 1 | 32 | GPR24_PERF0_ATIVADO | 90 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | GPR AL23 Modo Perfil Alternativo 1 |  |  |  | DiSOE | 1 | 34 | GPR24_PERF1_ATIVADO | 91 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | 81 Estágio 1 Atuado |  |  |  | DiSOE | 1 | 45 | GPR24_81_E1_ATUADA | 92 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | 81 Estágio 2 Atuado |  |  |  | DiSOE | 1 | 46 | GPR24_81_E2_ATUADA | 93 | [10 empty] | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Saude Comunicação |  |  |  | DiSOE |  | - | GPR24_SAUDE_COMUNIC | 94 | [10 empty] | #N/A | #N/A | #N/A

## GPR31
SE GUAPORÉ - AL GPR31 - 23 kV
RELÉ 31F1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
7SJ63 (End: 18d/12h) | GPR31 | Tensão A-B |  |  |  | AI Val | 134 | 137 | 2011-08-09 | GPR31_TENSAO_AB | 40 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Corrente Fase A |  |  |  | AiVal | 134 | 137 | 9/1 | GPR31_CORRENTE_FA | 41 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Corrente Fase B |  |  |  | AiVal | 134 | 137 | 9/2 | GPR31_CORRENTE_FB | 42 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Corrente Fase C |  |  |  | AiVal | 134 | 137 | 9/3 | GPR31_CORRENTE_FC | 43 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Potência Ativa |  |  |  | AiVal | 134 | 137 | 9/11 | GPR31_POT_ATIVA | 44 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Potência Reativa |  |  |  | AiVal | 134 | 137 | 9/12 | GPR31_POT_REATIVA | 45 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Disj. 52-09 (11Q0) - Abrir / Fechar |  | 4/5 |  | DiSOEx2 | 240 | 160 | 20 | GPR31_COMANDOS_DJ | 40 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Religamento (79) - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 169 | 20 | GPR31_COMANDOS_79 | 41 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Relé Neutro (51N) - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 170 | 20 | GPR31_COMANDOS_PN | 42 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Desligamento 26/49 - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 171 | 20 | GPR31_COMANDOS_RC | 43 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Disj. 52-09 (11Q0) - Aberto | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | GPR31_DJ_ABERTO | 100 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Disj. 52-09 (11Q0) - Fechado | 2 |  |  | DiSOEx2 | 240 | 160 | 1 | GPR31_DJ_FECHADO | 101 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Disj.- Mola Descarregada | 3 |  |  | DiVal | 240 | 192 | 1 | GPR31_MOLA_DESC | 102 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Disj.- Chave 43LR em posição LOCAL | 4 |  |  | DiVal | 240 | 193 | 1 | GPR31_43LR_LOCAL | 103 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Disj.- Sup.Circuito de Abertura | 7 |  |  | DiVal | 170 | 56 | 1 | GPR31_CIRC_TRIP_FALHADO | 104 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 26/49 TR3 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 22 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 86FD/Barra P1 - Atuado (TRIP e Bloqueio DJ) | 8 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 26/49 TR2 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 16 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 86T3 - Atuado (TRIP e Bloqueio DJ) | 21 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Reserva |  |  |  | - | - | - | - | Reserva | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Telecomando (43TC) - Excluído |  |  |  | DiVal | 101 | 85 | 1 | GPR31_43TC_EXCLUIDA | 105 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Grupo de Ajustes B - Ativado (51N Excluido) |  |  |  | DiVal | 160 | 24 | 1 | GPR31_GRPB_ATIVADO | 106 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Chave 26/49 (Rejeição de Carga) - Incluida |  |  |  | DiVal | 240 | 196 | 1 | GPR31_43RC_INCLUIDA | 107 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 79 - Disparo |  |  |  | AF | 160 | 128 | 2 | GPR31_79_DISPARO | 108 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 79 - Excluído |  |  |  | DiVal | 40 | 81 | 1 | GPR31_79_EXCLUIDO | 109 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 79 - Sucedido |  |  |  | DiVal | 40 | 162 | 1 | GPR31_RELIGAM_SUCEDIDO | 110 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 79 - Bloqueado |  |  |  | FDI | 40 | 163 | 2 | GPR31_79_BLOQUEADO | 111 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 50BF - Atuado |  | 3 |  | AF | 160 | 85 | 2 | GPR31_50BF_ATUADO | 112 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 50 ABC - Estágio 1 - Atuado |  | 4 |  | AF | 160 | 90 | 2 | GPR31_50_E1_ATUADO | 113 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 50 ABC - Estágio 2 - Atuado |  | 4 |  | AF | 160 | 91 | 2 | GPR31_50_E2_ATUADO | 114 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 50 N - Estágio 1 - Atuado |  | 4 |  | AF | 160 | 92 | 2 | GPR31_50N_E1_ATUADO | 115 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 50 N - Estágio 2 - Atuado |  | 4 |  | AF | 160 | 93 | 2 | GPR31_50N_E2_ATUADO | 116 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 50/51 Fase A - Atuado |  |  |  | FDI | 60 | 54 | 2 | GPR31_50FA_51FA_ATUADO | 117 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 50/51 Fase B - Atuado |  |  |  | FDI | 60 | 55 | 2 | GPR31_50FB_51FB_ATUADO | 118 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 50/51 Fase C - Atuado |  |  |  | FDI | 60 | 56 | 2 | GPR31_50FC_51FC_ATUADO | 119 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 51 ABC - Atuado |  | 4 |  | FDI | 60 | 58 | 2 | GPR31_51ABC_ATUADO | 120 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 51 N - Atuado |  | 4 |  | FDI | 60 | 66 | 2 | GPR31_51N_ATUADO | 121 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 46 (Sequência Negativa) - Atuado |  | 4 |  | FDI | 70 | 149 | 2 | GPR31_46_ATUADO | 122 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 81 (Sub/Sobre Frequencia) - Estágio 1 - Atuado |  | 4 |  | FDI | 70 | 234 | 2 | GPR31_81_E1_ATUADO | 123 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 81 (Sub/Sobre Frequencia) - Estágio 2 - Atuado |  | 4 |  | FDI | 70 | 235 | 2 | GPR31_81_E2_ATUADO | 124 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 50Ns (Falta Sensitiva à Terra) - Estágio 1 - Atuado |  | 4 |  | FDI | 151 | 126 | 2 | GPR31_50Ns_E1_ATUADO | 125 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 50Ns (Falta Sensitiva à Terra) - Estágio 2 - Atuado |  | 4 |  | FDI | 151 | 123 | 2 | GPR31_50Ns_E2_ATUADO | 126 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Saude Comunicação |  |  |  | - | - | - | - | GPR31_SAUDE_COMUNIC | 127 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## GPR32
SE GUAPORÉ - AL GPR32 - 23 kV
RELÉ 32F1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
7SJ63 (End: 19d/13h) | GPR32 | Tensão A-B |  |  |  | AI Val | 134 | 137 | 2011-08-09 | GPR32_TENSAO_AB | 50 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Corrente Fase A |  |  |  | AiVal | 134 | 137 | 9/1 | GPR32_CORRENTE_FA | 51 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Corrente Fase B |  |  |  | AiVal | 134 | 137 | 9/2 | GPR32_CORRENTE_FB | 52 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Corrente Fase C |  |  |  | AiVal | 134 | 137 | 9/3 | GPR32_CORRENTE_FC | 53 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Potência Ativa |  |  |  | AiVal | 134 | 137 | 9/11 | GPR32_POT_ATIVA | 54 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Potência Reativa |  |  |  | AiVal | 134 | 137 | 9/12 | GPR32_POT_REATIVA | 55 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Disj. 24-01 (10Q0) - Abrir / Fechar |  | 4/5 |  | DiSOEx2 | 240 | 160 | 20 | GPR32_COMANDOS_DJ | 50 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Religamento (79) - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 169 | 20 | GPR32_COMANDOS_79 | 51 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Relé Neutro (51N) - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 170 | 20 | GPR32_COMANDOS_PN | 52 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Desligamento 26/49 - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 171 | 20 | GPR32_COMANDOS_RC | 53 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Disj. 24-01 (11Q0) - Aberto | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | GPR32_DJ_ABERTO | 130 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Disj. 24-01 (11Q0) - Fechado | 2 |  |  | DiSOEx2 | 240 | 160 | 1 | GPR32_DJ_FECHADO | 131 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Disj.- Mola Descarregada | 3 |  |  | DiVal | 240 | 192 | 1 | GPR32_MOLA_DESC | 132 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Disj.- Chave 43LR em posição LOCAL | 4 |  |  | DiVal | 240 | 193 | 1 | GPR32_43LR_LOCAL | 133 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Disj.- Sup.Circuito de Abertura | 7 |  |  | DiVal | 170 | 56 | 1 | GPR32_CIRC_TRIP_FALHADO | 134 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 26/49 TR3 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 22 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 86FD/Barra P1 - Atuado (TRIP e Bloqueio DJ) | 8 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 26/49 TR2 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 16 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 86T3 - Atuado (TRIP e Bloqueio DJ) | 21 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Reserva |  |  |  | - | - | - | - | Reserva | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Disj.- Falta Vcc Comando | ? |  |  | DiVal | 240 | 194 | 1 | ALGPR32_FVCC_COMANDO | 135 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Disj.- Falta Vca Aquecimento | ? |  |  | DiVal | 240 | 195 | 1 | ALGPR32_FVCA_AQUECIMENT | 136 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Telecomando (43TC) - Excluído |  |  |  | DiVal | 101 | 85 | 1 | GPR32_43TC_EXCLUIDA | 137 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Grupo de Ajustes B - Ativado (51N Excluido) |  |  |  | DiVal | 160 | 24 | 1 | GPR32_GRPB_ATIVADO | 138 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Chave 26/49 (Rejeição de Carga) - Incluida |  |  |  | DiVal | 240 | 196 | 1 | GPR32_43RC_INCLUIDA | 139 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 79 - Disparo |  |  |  | AF | 160 | 128 | 2 | GPR32_79_DISPARO | 140 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 79 - Excluído |  |  |  | DiVal | 40 | 81 | 1 | GPR32_79_EXCLUIDO | 141 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 79 - Sucedido |  |  |  | DiVal | 40 | 162 | 1 | GPR32_RELIGAM_SUCEDIDO | 142 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 79 - Bloqueado |  |  |  | FDI | 40 | 163 | 2 | GPR32_79_BLOQUEADO | 143 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 50BF - Atuado |  | 3 |  | AF | 160 | 85 | 2 | GPR32_50BF_ATUADO | 144 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 50 ABC - Estágio 1 - Atuado |  | 4 |  | AF | 160 | 90 | 2 | GPR32_50_E1_ATUADO | 145 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 50 ABC - Estágio 2 - Atuado |  | 4 |  | AF | 160 | 91 | 2 | GPR32_50_E2_ATUADO | 146 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 50 N - Estágio 1 - Atuado |  | 4 |  | AF | 160 | 92 | 2 | GPR32_50N_E1_ATUADO | 147 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 50 N - Estágio 2 - Atuado |  | 4 |  | AF | 160 | 93 | 2 | GPR32_50N_E2_ATUADO | 148 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 50/51 Fase A - Atuado |  |  |  | FDI | 60 | 54 | 2 | GPR32_50FA_51FA_ATUADO | 149 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 50/51 Fase B - Atuado |  |  |  | FDI | 60 | 55 | 2 | GPR32_50FB_51FB_ATUADO | 150 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 50/51 Fase C - Atuado |  |  |  | FDI | 60 | 56 | 2 | GPR32_50FC_51FC_ATUADO | 151 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 51 ABC - Atuado |  | 4 |  | FDI | 60 | 58 | 2 | GPR32_51ABC_ATUADO | 152 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 51 N - Atuado |  | 4 |  | FDI | 60 | 66 | 2 | GPR32_51N_ATUADO | 153 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 46 (Sequência Negativa) - Atuado |  | 4 |  | FDI | 70 | 149 | 2 | GPR32_46_ATUADO | 154 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 81 (Sub/Sobre Frequencia) - Estágio 1 - Atuado |  | 4 |  | FDI | 70 | 234 | 2 | GPR32_81_E1_ATUADO | 155 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 81 (Sub/Sobre Frequencia) - Estágio 2 - Atuado |  | 4 |  | FDI | 70 | 235 | 2 | GPR32_81_E2_ATUADO | 156 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 50Ns (Falta Sensitiva à Terra) - Estágio 1 - Atuado |  | 4 |  | FDI | 151 | 126 | 2 | GPR32_50Ns_E1_ATUADO | 157 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 50Ns (Falta Sensitiva à Terra) - Estágio 2 - Atuado |  | 4 |  | FDI | 151 | 123 | 2 | GPR32_50Ns_E2_ATUADO | 158 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Saude Comunicação |  |  |  | - | - | - | - | GPR32_SAUDE_COMUNIC | 159 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## GPR33
SE GUAPORÉ - AL GPR33 - 23 kV
RELÉ 33F1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
7SJ63 (End: 20d/14h) | GPR33 | Tensão A-B |  |  |  | AI Val | 134 | 137 | 2011-08-09 | GPR33_TENSAO_AB | 60 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Corrente Fase A |  |  |  | AiVal | 134 | 137 | 9/1 | GPR33_CORRENTE_FA | 61 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Corrente Fase B |  |  |  | AiVal | 134 | 137 | 9/2 | GPR33_CORRENTE_FB | 62 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Corrente Fase C |  |  |  | AiVal | 134 | 137 | 9/3 | GPR33_CORRENTE_FC | 63 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Potência Ativa |  |  |  | AiVal | 134 | 137 | 9/11 | GPR33_POT_ATIVA | 64 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Potência Reativa |  |  |  | AiVal | 134 | 137 | 9/12 | GPR33_POT_REATIVA | 65 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Disj. 52-08 (09Q0) - Abrir / Fechar |  | 4/5 |  | DiSOEx2 | 240 | 160 | 20 | GPR33_COMANDOS_DJ | 60 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Religamento (79) - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 169 | 20 | GPR33_COMANDOS_79 | 61 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Relé Neutro (51N) - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 170 | 20 | GPR33_COMANDOS_PN | 62 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Desligamento 26/49 - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 171 | 20 | GPR33_COMANDOS_RC | 63 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Disj. 52-08 (09Q0) - Aberto | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | GPR33_DJ_ABERTO | 165 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Disj. 52-08 (09Q0) - Fechado | 2 |  |  | DiSOEx2 | 240 | 160 | 1 | GPR33_DJ_FECHADO | 166 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Disj.- Mola Descarregada | 3 |  |  | DiVal | 240 | 192 | 1 | GPR33_MOLA_DESC | 167 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Disj.- Chave 43LR em posição LOCAL | 4 |  |  | DiVal | 240 | 193 | 1 | GPR33_43LR_LOCAL | 168 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Disj.- Sup.Circuito de Abertura | 7 |  |  | DiVal | 170 | 56 | 1 | GPR33_CIRC_TRIP_FALHADO | 169 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 26/49 TR3 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 22 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 86FD/Barra P1 - Atuado (TRIP e Bloqueio DJ) | 8 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 26/49 TR2 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 16 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 86T3 - Atuado (TRIP e Bloqueio DJ) | 21 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Reserva |  |  |  | - | - | - | - | Reserva | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Telecomando (43TC) - Excluído |  |  |  | DiVal | 101 | 85 | 1 | GPR33_43TC_EXCLUIDA | 170 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Grupo de Ajustes B - Ativado (51N Excluido) |  |  |  | DiVal | 160 | 24 | 1 | GPR33_GRPB_ATIVADO | 171 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Chave 26/49 (Rejeição de Carga) - Incluida |  |  |  | DiVal | 240 | 196 | 1 | GPR33_43RC_INCLUIDA | 172 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 79 - Disparo |  |  |  | AF | 160 | 128 | 2 | GPR33_79_DISPARO | 173 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 79 - Excluído |  |  |  | DiVal | 40 | 81 | 1 | GPR33_79_EXCLUIDO | 174 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 79 - Sucedido |  |  |  | DiVal | 40 | 162 | 1 | GPR33_RELIGAM_SUCEDIDO | 175 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 79 - Bloqueado |  |  |  | FDI | 40 | 163 | 2 | GPR33_79_BLOQUEADO | 176 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 50BF - Atuado |  | 3 |  | AF | 160 | 85 | 2 | GPR33_50BF_ATUADO | 177 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 50 ABC - Estágio 1 - Atuado |  | 4 |  | AF | 160 | 90 | 2 | GPR33_50_E1_ATUADO | 178 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 50 ABC - Estágio 2 - Atuado |  | 4 |  | AF | 160 | 91 | 2 | GPR33_50_E2_ATUADO | 179 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 50 N - Estágio 1 - Atuado |  | 4 |  | AF | 160 | 92 | 2 | GPR33_50N_E1_ATUADO | 180 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 50 N - Estágio 2 - Atuado |  | 4 |  | AF | 160 | 93 | 2 | GPR33_50N_E2_ATUADO | 181 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 50/51 Fase A - Atuado |  |  |  | FDI | 60 | 54 | 2 | GPR33_50FA_51FA_ATUADO | 182 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 50/51 Fase B - Atuado |  |  |  | FDI | 60 | 55 | 2 | GPR33_50FB_51FB_ATUADO | 183 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 50/51 Fase C - Atuado |  |  |  | FDI | 60 | 56 | 2 | GPR33_50FC_51FC_ATUADO | 184 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 51 ABC - Atuado |  | 4 |  | FDI | 60 | 58 | 2 | GPR33_51ABC_ATUADO | 185 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 51 N - Atuado |  | 4 |  | FDI | 60 | 66 | 2 | GPR33_51N_ATUADO | 186 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 46 (Sequência Negativa) - Atuado |  | 4 |  | FDI | 70 | 149 | 2 | GPR33_46_ATUADO | 187 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 81 (Sub/Sobre Frequencia) - Estágio 1 - Atuado |  | 4 |  | FDI | 70 | 234 | 2 | GPR33_81_E1_ATUADO | 188 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 81 (Sub/Sobre Frequencia) - Estágio 2 - Atuado |  | 4 |  | FDI | 70 | 235 | 2 | GPR33_81_E2_ATUADO | 189 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 50Ns (Falta Sensitiva à Terra) - Estágio 1 - Atuado |  | 4 |  | FDI | 151 | 126 | 2 | GPR33_50Ns_E1_ATUADO | 190 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 50Ns (Falta Sensitiva à Terra) - Estágio 2 - Atuado |  | 4 |  | FDI | 151 | 123 | 2 | GPR33_50Ns_E2_ATUADO | 191 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Saude Comunicação |  |  |  | - | - | - | - | GPR33_SAUDE_COMUNIC | 192 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | - | - | - | -
[6 empty] | - | - | - | -

## GPR34
SE GUAPORÉ - AL GPR34 - 23 kV
RELÉ 34F1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
7SJ63 (End: 21d/15h) | GPR34 | Tensão A-B |  |  |  | AI Val | 134 | 137 | 2011-08-09 | GPR34_TENSAO_AB | 70 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Corrente Fase A |  |  |  | AiVal | 134 | 137 | 9/1 | GPR34_CORRENTE_FA | 71 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Corrente Fase B |  |  |  | AiVal | 134 | 137 | 9/2 | GPR34_CORRENTE_FB | 72 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Corrente Fase C |  |  |  | AiVal | 134 | 137 | 9/3 | GPR34_CORRENTE_FC | 73 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Potência Ativa |  |  |  | AiVal | 134 | 137 | 9/11 | GPR34_POT_ATIVA | 74 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Potência Reativa |  |  |  | AiVal | 134 | 137 | 9/12 | GPR34_POT_REATIVA | 75 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Disj. 52-07 (08Q0) - Abrir / Fechar |  | 4/5 |  | DiSOEx2 | 240 | 160 | 20 | GPR34_COMANDOS_DJ | 70 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Religamento (79) - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 169 | 20 | GPR34_COMANDOS_79 | 71 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Relé Neutro (51N) - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 170 | 20 | GPR34_COMANDOS_PN | 72 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Desligamento 26/49 - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 171 | 20 | GPR34_COMANDOS_RC | 73 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Disj. 52-07(08Q0) - Aberto | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | GPR34_DJ_ABERTO | 195 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Disj. 52-07(08Q0) - Fechado | 2 |  |  | DiSOEx2 | 240 | 160 | 1 | GPR34_DJ_FECHADO | 196 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Disj.- Mola Descarregada | 3 |  |  | DiVal | 240 | 192 | 1 | GPR34_MOLA_DESC | 197 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Disj.- Chave 43LR em posição LOCAL | 4 |  |  | DiVal | 240 | 193 | 1 | GPR34_43LR_LOCAL | 198 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Disj.- Sup.Circuito de Abertura | 7 |  |  | DiVal | 170 | 56 | 1 | GPR34_CIRC_TRIP_FALHADO | 199 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 26/49 TR3 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 22 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 86FD/Barra P1 - Atuado (TRIP e Bloqueio DJ) | 8 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 26/49 TR2 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 16 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 86T3 - Atuado (TRIP e Bloqueio DJ) | 21 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Reserva |  |  |  | - | - | - | - | Reserva | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Telecomando (43TC) - Excluído |  |  |  | DiVal | 101 | 85 | 1 | GPR34_43TC_EXCLUIDA | 200 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Grupo de Ajustes B - Ativado (51N Excluido) |  |  |  | DiVal | 160 | 24 | 1 | GPR34_GRPB_ATIVADO | 201 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Chave 26/49 (Rejeição de Carga) - Incluida |  |  |  | DiVal | 240 | 196 | 1 | GPR34_43RC_INCLUIDA | 202 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 79 - Disparo |  |  |  | AF | 160 | 128 | 2 | GPR34_79_DISPARO | 203 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 79 - Excluído |  |  |  | DiVal | 40 | 81 | 1 | GPR34_79_EXCLUIDO | 204 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 79 - Sucedido |  |  |  | DiVal | 40 | 162 | 1 | GPR34_RELIGAM_SUCEDIDO | 205 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 79 - Bloqueado |  |  |  | FDI | 40 | 163 | 2 | GPR34_79_BLOQUEADO | 206 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 50BF - Atuado |  | 3 |  | AF | 160 | 85 | 2 | GPR34_50BF_ATUADO | 207 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 50 ABC - Estágio 1 - Atuado |  | 4 |  | AF | 160 | 90 | 2 | GPR34_50_E1_ATUADO | 208 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 50 ABC - Estágio 2 - Atuado |  | 4 |  | AF | 160 | 91 | 2 | GPR34_50_E2_ATUADO | 209 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 50 N - Estágio 1 - Atuado |  | 4 |  | AF | 160 | 92 | 2 | GPR34_50N_E1_ATUADO | 210 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 50 N - Estágio 2 - Atuado |  | 4 |  | AF | 160 | 93 | 2 | GPR34_50N_E2_ATUADO | 211 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 50/51 Fase A - Atuado |  |  |  | FDI | 60 | 54 | 2 | GPR34_50FA_51FA_ATUADO | 212 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 50/51 Fase B - Atuado |  |  |  | FDI | 60 | 55 | 2 | GPR34_50FB_51FB_ATUADO | 213 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 50/51 Fase C - Atuado |  |  |  | FDI | 60 | 56 | 2 | GPR34_50FC_51FC_ATUADO | 214 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 51 ABC - Atuado |  | 4 |  | FDI | 60 | 58 | 2 | GPR34_51ABC_ATUADO | 215 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 51 N - Atuado |  | 4 |  | FDI | 60 | 66 | 2 | GPR34_51N_ATUADO | 216 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 46 (Sequência Negativa) - Atuado |  | 4 |  | FDI | 70 | 149 | 2 | GPR34_46_ATUADO | 217 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 81 (Sub/Sobre Frequencia) - Estágio 1 - Atuado |  | 4 |  | FDI | 70 | 234 | 2 | GPR34_81_E1_ATUADO | 218 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 81 (Sub/Sobre Frequencia) - Estágio 2 - Atuado |  | 4 |  | FDI | 70 | 235 | 2 | GPR34_81_E2_ATUADO | 219 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 50Ns (Falta Sensitiva à Terra) - Estágio 1 - Atuado |  | 4 |  | FDI | 151 | 126 | 2 | GPR34_50Ns_E1_ATUADO | 220 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 50Ns (Falta Sensitiva à Terra) - Estágio 2 - Atuado |  | 4 |  | FDI | 151 | 123 | 2 | GPR34_50Ns_E2_ATUADO | 221 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Saude Comunicação |  |  |  | - | - | - | - | GPR34_SAUDE_COMUNIC | 222 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | - | - | - | -
[6 empty] | - | - | - | -

## GPR35
SE GUAPORÉ - AL GPR35 - 23 kV
RELÉ 35F1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
7SJ63 (End: 22d/16h) | GPR35 | Tensão A-B |  |  |  | AI Val | 134 | 137 | 2011-08-09 | GPR35_TENSAO_AB | 80 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Corrente Fase A |  |  |  | AiVal | 134 | 137 | 9/1 | GPR35_CORRENTE_FA | 81 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Corrente Fase B |  |  |  | AiVal | 134 | 137 | 9/2 | GPR35_CORRENTE_FB | 82 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Corrente Fase C |  |  |  | AiVal | 134 | 137 | 9/3 | GPR35_CORRENTE_FC | 83 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Potência Ativa |  |  |  | AiVal | 134 | 137 | 9/11 | GPR35_POT_ATIVA | 84 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Potência Reativa |  |  |  | AiVal | 134 | 137 | 9/12 | GPR35_POT_REATIVA | 85 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Disj. 52-06 (07Q0) - Abrir / Fechar |  | 4/5 |  | DiSOEx2 | 240 | 160 | 20 | GPR35_COMANDOS_DJ | 80 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Religamento (79) - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 169 | 20 | GPR35_COMANDOS_79 | 81 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Relé Neutro (51N) - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 170 | 20 | GPR35_COMANDOS_PN | 82 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Desligamento 26/49 - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 171 | 20 | GPR35_COMANDOS_RC | 83 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Disj. 52-06 (07Q0) - Aberto | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | GPR35_DJ_ABERTO | 225 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Disj. 52-06 (07Q0) - Fechado | 2 |  |  | DiSOEx2 | 240 | 160 | 1 | GPR35_DJ_FECHADO | 226 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Disj.- Mola Descarregada | 3 |  |  | DiVal | 240 | 192 | 1 | GPR35_MOLA_DESC | 227 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Disj.- Chave 43LR em posição LOCAL | 4 |  |  | DiVal | 240 | 193 | 1 | GPR35_43LR_LOCAL | 228 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Disj.- Sup.Circuito de Abertura | 7 |  |  | DiVal | 170 | 56 | 1 | GPR35_CIRC_TRIP_FALHADO | 229 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 26/49 TR3 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 22 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 86FD/Barra P1 - Atuado (TRIP e Bloqueio DJ) | 8 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 26/49 TR2 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 16 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 86T3 - Atuado (TRIP e Bloqueio DJ) | 21 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Reserva |  |  |  | - | - | - | - | Reserva | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Telecomando (43TC) - Excluído |  |  |  | DiVal | 101 | 85 | 1 | GPR35_43TC_EXCLUIDA | 230 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Grupo de Ajustes B - Ativado (51N Excluido) |  |  |  | DiVal | 160 | 24 | 1 | GPR35_GRPB_ATIVADO | 231 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Chave 26/49 (Rejeição de Carga) - Incluida |  |  |  | DiVal | 240 | 196 | 1 | GPR35_43RC_INCLUIDA | 232 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 79 - Disparo |  |  |  | AF | 160 | 128 | 2 | GPR35_79_DISPARO | 233 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 79 - Excluído |  |  |  | DiVal | 40 | 81 | 1 | GPR35_79_EXCLUIDO | 234 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 79 - Sucedido |  |  |  | DiVal | 40 | 162 | 1 | GPR35_RELIGAM_SUCEDIDO | 235 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 79 - Bloqueado |  |  |  | FDI | 40 | 163 | 2 | GPR35_79_BLOQUEADO | 236 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 50BF - Atuado |  | 3 |  | AF | 160 | 85 | 2 | GPR35_50BF_ATUADO | 237 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 50 ABC - Estágio 1 - Atuado |  | 4 |  | AF | 160 | 90 | 2 | GPR35_50_E1_ATUADO | 238 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 50 ABC - Estágio 2 - Atuado |  | 4 |  | AF | 160 | 91 | 2 | GPR35_50_E2_ATUADO | 239 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 50 N - Estágio 1 - Atuado |  | 4 |  | AF | 160 | 92 | 2 | GPR35_50N_E1_ATUADO | 240 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 50 N - Estágio 2 - Atuado |  | 4 |  | AF | 160 | 93 | 2 | GPR35_50N_E2_ATUADO | 241 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 50/51 Fase A - Atuado |  |  |  | FDI | 60 | 54 | 2 | GPR35_50FA_51FA_ATUADO | 242 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 50/51 Fase B - Atuado |  |  |  | FDI | 60 | 55 | 2 | GPR35_50FB_51FB_ATUADO | 243 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 50/51 Fase C - Atuado |  |  |  | FDI | 60 | 56 | 2 | GPR35_50FC_51FC_ATUADO | 244 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 51 ABC - Atuado |  | 4 |  | FDI | 60 | 58 | 2 | GPR35_51ABC_ATUADO | 245 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 51 N - Atuado |  | 4 |  | FDI | 60 | 66 | 2 | GPR35_51N_ATUADO | 246 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 46 (Sequência Negativa) - Atuado |  | 4 |  | FDI | 70 | 149 | 2 | GPR35_46_ATUADO | 247 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 81 (Sub/Sobre Frequencia) - Estágio 1 - Atuado |  | 4 |  | FDI | 70 | 234 | 2 | GPR35_81_E1_ATUADO | 248 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 81 (Sub/Sobre Frequencia) - Estágio 2 - Atuado |  | 4 |  | FDI | 70 | 235 | 2 | GPR35_81_E2_ATUADO | 249 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 50Ns (Falta Sensitiva à Terra) - Estágio 1 - Atuado |  | 4 |  | FDI | 151 | 126 | 2 | GPR35_50Ns_E1_ATUADO | 250 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 50Ns (Falta Sensitiva à Terra) - Estágio 2 - Atuado |  | 4 |  | FDI | 151 | 123 | 2 | GPR35_50Ns_E2_ATUADO | 251 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Saude Comunicação |  |  |  | - | - | - | - | GPR35_SAUDE_COMUNIC | 252 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | - | - | - | -
[6 empty] | - | - | - | -

## GPR36
SE GUAPORÉ - AL GPR36 - 23 kV
RELÉ 36F1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
7SJ63 (End: 23d/17h) | GPR36 | Tensão A-B |  |  |  | AI Val | 134 | 137 | 2011-08-09 | GPR36_TENSAO_AB | 90 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Corrente Fase A |  |  |  | AiVal | 134 | 137 | 9/1 | GPR36_CORRENTE_FA | 91 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Corrente Fase B |  |  |  | AiVal | 134 | 137 | 9/2 | GPR36_CORRENTE_FB | 92 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Corrente Fase C |  |  |  | AiVal | 134 | 137 | 9/3 | GPR36_CORRENTE_FC | 93 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Potência Ativa |  |  |  | AiVal | 134 | 137 | 9/11 | GPR36_POT_ATIVA | 94 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Potência Reativa |  |  |  | AiVal | 134 | 137 | 9/12 | GPR36_POT_REATIVA | 95 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Disj. 52-05 (06Q0) - Abrir / Fechar |  | 4/5 |  | DiSOEx2 | 240 | 160 | 20 | GPR36_COMANDOS_DJ | 90 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Religamento (79) - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 169 | 20 | GPR36_COMANDOS_79 | 91 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Relé Neutro (51N) - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 170 | 20 | GPR36_COMANDOS_PN | 92 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Desligamento 26/49 - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 171 | 20 | GPR36_COMANDOS_RC | 93 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Disj. 52-05 (06Q0) - Aberto | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | GPR36_DJ_ABERTO | 255 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Disj. 52-05 (06Q0) - Fechado | 2 |  |  | DiSOEx2 | 240 | 160 | 1 | GPR36_DJ_FECHADO | 256 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Disj.- Mola Descarregada | 3 |  |  | DiVal | 240 | 192 | 1 | GPR36_MOLA_DESC | 257 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Disj.- Chave 43LR em posição LOCAL | 4 |  |  | DiVal | 240 | 193 | 1 | GPR36_43LR_LOCAL | 258 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Disj.- Sup.Circuito de Abertura | 7 |  |  | DiVal | 170 | 56 | 1 | GPR36_CIRC_TRIP_FALHADO | 259 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 26/49 TR3 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 22 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 86FD/Barra P1 - Atuado (TRIP e Bloqueio DJ) | 8 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 26/49 TR2 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 16 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 86T3 - Atuado (TRIP e Bloqueio DJ) | 21 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Reserva |  |  |  | - | - | - | - | Reserva | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Telecomando (43TC) - Excluído |  |  |  | DiVal | 101 | 85 | 1 | GPR36_43TC_EXCLUIDA | 260 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Grupo de Ajustes B - Ativado (51N Excluido) |  |  |  | DiVal | 160 | 24 | 1 | GPR36_GRPB_ATIVADO | 261 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Chave 26/49 (Rejeição de Carga) - Incluida |  |  |  | DiVal | 240 | 196 | 1 | GPR36_43RC_INCLUIDA | 262 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 79 - Disparo |  |  |  | AF | 160 | 128 | 2 | GPR36_79_DISPARO | 263 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 79 - Excluído |  |  |  | DiVal | 40 | 81 | 1 | GPR36_79_EXCLUIDO | 264 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 79 - Sucedido |  |  |  | DiVal | 40 | 162 | 1 | GPR36_RELIGAM_SUCEDIDO | 265 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 79 - Bloqueado |  |  |  | FDI | 40 | 163 | 2 | GPR36_79_BLOQUEADO | 266 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 50BF - Atuado |  | 3 |  | AF | 160 | 85 | 2 | GPR36_50BF_ATUADO | 267 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 50 ABC - Estágio 1 - Atuado |  | 4 |  | AF | 160 | 90 | 2 | GPR36_50_E1_ATUADO | 268 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 50 ABC - Estágio 2 - Atuado |  | 4 |  | AF | 160 | 91 | 2 | GPR36_50_E2_ATUADO | 269 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 50 N - Estágio 1 - Atuado |  | 4 |  | AF | 160 | 92 | 2 | GPR36_50N_E1_ATUADO | 270 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 50 N - Estágio 2 - Atuado |  | 4 |  | AF | 160 | 93 | 2 | GPR36_50N_E2_ATUADO | 271 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 50/51 Fase A - Atuado |  |  |  | FDI | 60 | 54 | 2 | GPR36_50FA_51FA_ATUADO | 272 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 50/51 Fase B - Atuado |  |  |  | FDI | 60 | 55 | 2 | GPR36_50FB_51FB_ATUADO | 273 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 50/51 Fase C - Atuado |  |  |  | FDI | 60 | 56 | 2 | GPR36_50FC_51FC_ATUADO | 274 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 51 ABC - Atuado |  | 4 |  | FDI | 60 | 58 | 2 | GPR36_51ABC_ATUADO | 275 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 51 N - Atuado |  | 4 |  | FDI | 60 | 66 | 2 | GPR36_51N_ATUADO | 276 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 46 (Sequência Negativa) - Atuado |  | 4 |  | FDI | 70 | 149 | 2 | GPR36_46_ATUADO | 277 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 81 (Sub/Sobre Frequencia) - Estágio 1 - Atuado |  | 4 |  | FDI | 70 | 234 | 2 | GPR36_81_E1_ATUADO | 278 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 81 (Sub/Sobre Frequencia) - Estágio 2 - Atuado |  | 4 |  | FDI | 70 | 235 | 2 | GPR36_81_E2_ATUADO | 279 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 50Ns (Falta Sensitiva à Terra) - Estágio 1 - Atuado |  | 4 |  | FDI | 151 | 126 | 2 | GPR36_50Ns_E1_ATUADO | 280 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 50Ns (Falta Sensitiva à Terra) - Estágio 2 - Atuado |  | 4 |  | FDI | 151 | 123 | 2 | GPR36_50Ns_E2_ATUADO | 281 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Saude Comunicação |  |  |  | - | - | - | - | GPR36_SAUDE_COMUNIC | 282 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | - | - | - | -
[6 empty] | - | - | - | -

## IB23
SE GUAPORÉ - IB23 - 23 kV
RELÉ XXF1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
7SJ63 (End: 05) | IB23 | Tensão A-B |  |  |  | AI Val | 134 | 137 | 2011-08-09 | IB23_TENSAO_AB | 100 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Corrente Fase A |  |  |  | AiVal | 134 | 137 | 9/1 | IB23_CORRENTE_FA | 101 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Corrente Fase B |  |  |  | AiVal | 134 | 137 | 9/2 | IB23_CORRENTE_FB | 102 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Corrente Fase C |  |  |  | AiVal | 134 | 137 | 9/3 | IB23_CORRENTE_FC | 103 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Potência Ativa |  |  |  | AiVal | 134 | 137 | 9/11 | IB23_POT_ATIVA | 104 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Potência Reativa |  |  |  | AiVal | 134 | 137 | 9/12 | IB23_POT_REATIVA | 105 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj. 52-15 (06Q0) - Abrir / Fechar |  | 4/5 |  | DiSOEx2 | 240 | 160 | 20 | IB23_COMANDOS_DJ | 95 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Relé Neutro (51N) - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 170 | 20 | IB23_COMANDOS_PN | 96 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj. 52-15 (06Q0) - Aberto/Fechado | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | IB23_DJ_ABERTO | 285 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj. 52-15 (06Q0) - Aberto/Fechado | 2 |  |  | DiSOEx2 | 240 | 160 | 1 | IB23_DJ_FECHADO | 286 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj.- Mola Descarregada | 3 |  |  | DiVal | 240 | 192 | 1 | IB23_MOLA_DESC | 287 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj.- Falta VCC de Comando | 4 |  |  | DiVal | 240 | 195 | 1 | IB23_FCC_COMANDO | 288 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj.- Falta VCC Motor | 5 |  |  | DiVal | 240 | 196 | 1 | IB23_FCC_MOTOR | 289 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj.- Baixa Pressão SF6 - Estágio 1 - Alarme | 6 |  |  | DiVal | 240 | 190 | 1 | IB23_BP_SF6_ALARME | 290 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj.- Sup.Circuito de Abertura | 7 |  |  | DiVal | 170 | 56 | 1 | IB23_CIRC_TRIP_FALHADO | 291 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Reserva | 8 |  |  | - | - | - | - | Reserva | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 86FD/TR3 - Atuado (TRIP e Bloqueio DJ) | 9 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 86T3 - Atuado (TRIP e Bloqueio DJ) | 10 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Reserva | 11 |  |  | - | - | - | - | Reserva | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 86FD/TR2 - Atuado (TRIP e Bloqueio DJ) | 12 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 86T2 - Atuado (TRIP e Bloqueio DJ) | 13 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Reserva | 14-15 |  |  | - | - | - | - | Reserva | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj.- Baixa Pressão SF6 - Estágio 2 - Desligamento e Bloqueio | 16 |  |  | DiVal | 240 | 191 | 1 | IB23_BP_SF6_BLOQUEIO | 292 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj.- Chave 43LR em posição LOCAL | 17 |  |  | DiVal | 240 | 193 | 1 | IB23_43LR_LOCAL | 293 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj.- Permissão p/FECHAMENTO PARALELISMO TR3 (SPS) | 18 |  |  | DiVal | 240 | 194 | 1 | IB23_PARALEL_TR3_OK | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Secc.89-24 (689D) do TR3/BT - Aberta/Fechada (*) | 19/20 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj.- Permissão p/FECHAMENTO PARALELISMO TR2 (SPS) | 22 |  |  | DiVal | 240 | 197 | 1 | IB23_PARALEL_TR2_OK | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Secc.89-62 (689D) do TR2/BT - Aberta/Fechada | 23/24 |  |  | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Telecomando (43TC) - Excluído |  |  |  | DiVal | 101 | 85 | 1 | IB23_43TC_EXCLUIDA | 294 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Grupo de Ajustes B - Ativado (51N Excluido) |  |  |  | DiVal | 160 | 24 | 1 | IB23_GRPB_ATIVADO | 295 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 50BF - Atuado |  | 3/10 |  | AF | 160 | 85 | 2 | IB23_50BF_ATUADO | 296 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 50 ABC - Estágio 1 - Atuado |  | 4 |  | AF | 160 | 90 | 2 | IB23_50_E1_ATUADO | 297 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 50 ABC - Estágio 2 - Atuado |  | 4 |  | AF | 160 | 91 | 2 | IB23_50_E2_ATUADO | 298 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 50 N - Estágio 1 - Atuado |  | 4 |  | AF | 160 | 92 | 2 | IB23_50N_E1_ATUADO | 299 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 50 N - Estágio 2 - Atuado |  | 4 |  | AF | 160 | 93 | 2 | IB23_50N_E2_ATUADO | 300 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 50/51 Fase A - Atuado |  |  |  | FDI | 60 | 54 | 2 | IB23_50FA_51FA_ATUADO | 301 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 50/51 Fase B - Atuado |  |  |  | FDI | 60 | 55 | 2 | IB23_50FB_51FB_ATUADO | 302 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 50/51 Fase C - Atuado |  |  |  | FDI | 60 | 56 | 2 | IB23_50FC_51FC_ATUADO | 303 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 51 ABC - Atuado |  | 4 |  | FDI | 60 | 58 | 2 | IB23_51ABC_ATUADO | 304 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 51 N - Atuado |  | 4 |  | FDI | 60 | 66 | 2 | IB23_51N_ATUADO | 305 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Saude Comunicação |  |  |  | - | - | - | - | IB23_SAUDE_COMUNIC | 306 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | - | - | - | -
[6 empty] | - | - | - | -

## BC1
SE GUAPORÉ - BC1 - 23 kV
RELÉ XXF1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
7SJ63 (End: 24d/18h) | BC1 | Tensão A-B |  |  |  | AI Val | 134 | 137 | 2011-08-09 | BC1_TENSAO_AB | 107 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Disj. 52-19 (06Q0) - Abrir / Fechar |  | 4/5 |  | DiSOEx2 | 240 | 160 | 20 | BC1_COMANDOS_DJ | 100 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Automatismo - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 170 | 20 | BC1_COMANDOS_AUTO | 101 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Relé Neutro (51N) - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 171 | 20 | BC1_COMANDOS_86BC | 102 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Disj. 52-19 (06Q0) - Aberto/Fechado | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | BC1_DJ_ABERTO | 310 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Disj. 52-19 (06Q0) - Aberto/Fechado | 2 |  |  | DiSOEx2 | 240 | 160 | 1 | BC1_DJ_FECHADO | 311 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Disj. 52-19 (06Q0) - Mola Descarregada | ? |  |  | DiVal | 240 | 192 | 1 | BC1_DJ_MOLA_DESC | 312 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Disj. 52-19 (06Q0) - Falta Vcc Motor/Comando | ? |  |  | DiVal | 240 | 195 | 1 | BC1_FVCC_COM_MOT | 313 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Disj.- Sup.Circuito de Abertura | 7 |  |  | DiVal | 170 | 56 | 1 | BC1_CIRC_TRIP_FALHADO | 314 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Telecomando (43TC) - Excluído |  |  |  | DiVal | 101 | 85 | 1 | BC1_43TC_EXCLUIDA | 315 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | AUTOMATISMO - Incluído |  |  |  | DiVal | 240 | 197 | 1 | BC1_AUTOMAT_INCLUIDO | 316 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | AUTOMATISMO - Atuado |  |  |  | DiVal | 240 | 198 | 1 | BC1_AUTOMAT_ATUADO | 317 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Disj.52-04 - Fechamento Bloqueado 5 minutos |  |  |  | DiVal | 240 | 199 | 1 | BC1_DJ_FECH_BLOQ_5M | 318 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | 86BC - Atuado |  |  |  | DiVal | 240 | 200 | 1 | BC1_86BC_ATUADO | 319 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | 50BF - Atuado |  | 3 |  | AF | 160 | 85 | 2 | BC1_50BF_ATUADO | 320 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | 50 N - Estágio 1 - Atuado |  | 4 |  | AF | 160 | 92 | 2 | BC1_50N_E1_ATUADO | 321 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | 50 N - Estágio 2 - Atuado |  | 4 |  | AF | 160 | 93 | 2 | BC1_50N_E2_ATUADO | 322 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | 51 N - Atuado |  | 4 |  | FDI | 60 | 66 | 2 | BC1_51N_ATUADO | 323 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | 27 Estágio 1 - Atuado |  | 4 |  | FDI | 74 | 39 | 2 | BC1_27_E1_ATUADO | 324 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | 27 Estágio 2 - Atuado |  | 4 |  | FDI | 74 | 40 | 2 | BC1_27_E2_ATUADO | 325 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | 59 Estágio 1 - Atuado |  | 4 |  | FDI | 74 | 70 | 2 | BC1_59_E1_ATUADO | 326 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | 59 Estágio 2 - Atuado |  | 4 |  | FDI | 74 | 71 | 2 | BC1_59_E2_ATUADO | 327 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Saude Comunicação | [7 empty] | BC1_SAUDE_COMUNIC | 328 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | - | - | - | -
[6 empty] | - | - | - | -

## BC2
SE GUAPORÉ - BC2 - 23 kV
RELÉ XXF1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
7SJ62 (End: 6) | BC2 | Tensão A-B |  |  |  | AI Val | 134 | 137 | 2011-08-09 | BC2_TENSAO_AB | 108 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Disj. 52-14 (06Q0) - Abrir / Fechar |  | 4/5 |  | DiSOEx2 | 240 | 160 | 20 | BC2_COMANDOS_DJ | 105 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Automatismo - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 170 | 20 | BC2_COMANDOS_AUTO | 106 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Relé Neutro (51N) - Excluir/Incluir |  |  |  | DiSOEx2 | 240 | 171 | 20 | BC2_COMANDOS_86BC | 107 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Disj. 52-14 (06Q0) - Aberto/Fechado | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | BC2_DJ_ABERTO | 330 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Disj. 52-14 (06Q0) - Aberto/Fechado | 2 |  |  | DiSOEx2 | 240 | 160 | 1 | BC2_DJ_FECHADO | 331 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Telecomando (43TC) - Excluído | 4 |  |  | DiVal | 101 | 85 | 1 | BC2_43TC_EXCLUIDA | 332 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | AUTOMATISMO - Excluído | 3 |  |  | DiVal | 240 | 187 | 1 | BC2_AUTOMAT_INCLUIDO | 333 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | AUTOMATISMO - Atuado | 5 |  |  | DiVal | 240 | 188 | 1 | BC2_AUTOMAT_ATUADO | 334 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Disj. 52-14 (06Q0) - Mola Descarregada |  |  |  | DiVal | 240 | 195 | 1 | BC2_MOLA_DESCARREGADA | 335 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Disj. 52-14 (06Q0) - Falta Vcc Motor/Cmd |  |  |  | DiVal | 240 | 194 | 1 | BC2_FALTA_VCC_DJ | 336 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Disj. 52-14 (06Q0) - 43LR em Local |  |  |  | DiVal | 240 | 193 | 1 | BC2_43_LR_LOCAL | 337 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Disj.- Sup.Circuito de Abertura |  |  |  | DiVal | 240 | 196 | 1 | BC2_BI_SUP_TRIP | 338 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Disj. - Fechamento Bloqueado 5 minutos |  |  |  | DiVal | 240 | 200 | 1 | BC2_DJ_FECH_BLOQ_5M | 339 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 86BC - Atuado |  |  |  | DiVal | 240 | 199 | 1 | BC2_86BC_ATUADO | 340 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 50BF - Atuado |  |  |  | AF | 160 | 85 | 2 | BC2_50BF_ATUADO | 341 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 50F - Estágio 1 - Atuado |  |  |  | AF | 160 | 94 | 2 | BC2_50_1_ATUADO | 342 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 50F - Estágio 2 - Atuado |  |  |  | AF | 160 | 95 | 2 | BC2_50_2_ATUADO | 343 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 51F - Atuado |  |  |  | FDI | 60 | 67 | 2 | BC2_51_ATUADO | 344 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 50 N - Estágio 1 - Atuado |  |  |  | AF | 160 | 92 | 2 | BC2_50N_E1_ATUADO | 345 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 50 N - Estágio 2 - Atuado |  |  |  | AF | 160 | 93 | 2 | BC2_50N_E2_ATUADO | 346 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 51 N - Atuado |  |  |  | FDI | 60 | 66 | 2 | BC2_51N_ATUADO | 347 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 27 Estágio 1 - Atuado |  |  |  | FDI | 74 | 39 | 2 | BC2_27_E1_ATUADO | 348 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 27 Estágio 2 - Atuado |  |  |  | FDI | 74 | 40 | 2 | BC2_27_E2_ATUADO | 349 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 59 Estágio 1 - Atuado |  |  |  | FDI | 74 | 70 | 2 | BC2_59_E1_ATUADO | 350 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 59 Estágio 2 - Atuado |  |  |  | FDI | 74 | 71 | 2 | BC2_59_E2_ATUADO | 351 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Saude Comunicação |  |  |  | - | - | - | - | BC2_SAUDE_COMUNIC | 352 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | - | - | - | -

## TR3AT
SE GUAPORÉ - TR3 AT 69kV
RELÉ xxF1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
7SJ63 (End.: 17d/11h) | TR3AT | Tensão Fase B da Barra de 69 kV |  |  |  | AI Val | 134 | 137 | 9/6 | TR3AT_TENSAO_FB | 110 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Corrente Fase A |  |  |  | AI Val | 134 | 137 | 9/1 | TR3AT_CORRENTE_FA | 111 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Corrente Fase B |  |  |  | AI Val | 134 | 137 | 9/2 | TR3AT_CORRENTE_FB | 112 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Corrente Fase C |  |  |  | AI Val | 134 | 137 | 9/3 | TR3AT_CORRENTE_FC | 113 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Potência Ativa |  |  |  | AI Val | 134 | 137 | 9/11 | TR3AT_POT_ATIVA | 114 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Potência Reativa |  |  |  | AI Val | 134 | 137 | 9/12 | TR3AT_POT_REATIVA | 115 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Disj.52-02 (XXQA) - Abrir/Fechar |  | 4/5 |  | Command | 240 | 160 | 20 | TR3AT_COMANDOS_DJ | 110 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Secc.89-04 (XXQD) - Abrir/Fechar |  | 1/2 |  | Command | 240 | 161 | 20 | TR3AT_COMANDOS_S8904 | 111 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Disj.52-02 – Aberto | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | TR3AT_DJ_ABERTO | 355 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Disj.52-02 – Fechado | 2 |  |  | DiSOEx2 | 240 | 160 | 1 | TR3AT_DJ_FECHADO | 356 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Secc.89-04 (XXQD) - Aberto | 8 |  |  | DiSOEx2 | 240 | 161 | 1 | TR3AT_S8904_ABERTO | 357 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Secc.89-04 (XXQD) - Fechado | 9 |  |  | DiSOEx2 | 240 | 161 | 1 | TR3AT_S8904_FECHADO | 358 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Disj. 52-02 - 43LR em posição LOCAL | 3 |  |  | DI Val | 240 | 190 | 1 | TR3AT_DJ_43LR_LOCAL | 359 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Disj. 52-02 - Mola Descarregada | 4 |  |  | DI Val | 240 | 191 | 1 | TR3AT_DJ_MOLA_DESC | 360 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Oper.Indevida Seccionadora 89-04/24 (XXSD/E) | 5 |  |  | DI Val | 240 | 192 | 1 | TR3AT_OP_IND_SECC | 361 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 86T3 - Atuado | 6 |  |  | DI Val | 240 | 193 | 1 | TR3_86T3_ATUADO | 362 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Disj. 52-02 - SF6 - Alarme | ? |  |  | DI Val | 240 | 194 | 1 | TR3AT_SF6_ALARME | 363 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Disj. 52-02 - SF6 - Bloqueio | ? |  |  | DI Val | 240 | 195 | 1 | TR3AT_SF6_BLOQUEIO | 364 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Disj. 52-02 - Falta Vcc Motor/Comando | ? |  |  | DI Val | 240 | 196 | 1 | TR3AT_FVCC_CMD_MOT | 365 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Disj.52-02 - Superv.Circuito TRIP - Alarme | 7 |  |  | DI Val | 170 | 57 | 1 | TR3AT_CIRC_TRIP_FALHADO | 366 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 63T - Alarme | 10 |  |  | DI Val | 101 | 10 | 1 | TR3_63T_ALARME | 367 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 63T - Desligamento | 11 |  |  | DI Val | 101 | 11 | 1 | TR3_63T_ATUADO | 368 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 63C - Desligamento | 12 |  |  | DI Val | 101 | 12 | 1 | TR3_63C_ATUADO | 369 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 63C - Alarme - FUTURO | 13 |  |  | DI Val | 101 | 13 | 1 | Reserva | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Reserva | 14 |  |  | - | - | - | - | Reserva | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Reserva | 15 |  |  | - | - | - | - | Reserva | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 26T - Alarme | 16 |  |  | DI Val | 101 | 13 | 1 | TR3_26T_ALARME | 370 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 26T - Desligamento | 17 |  |  | DI Val | 101 | 14 | 1 | TR3_26T_ATUADO | 371 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 49BT - Alarme | 18 |  |  | DI Val | 101 | 15 | 1 | TR3_49BT_ALARME | 372 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 49BT - Desligamento | 19 |  |  | DI Val | 101 | 16 | 1 | TR3_49BT_ATUADO | 373 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 49AT - Alarme | 20 |  |  | DI Val | 101 | 17 | 1 | TR3_49_ALARME | 374 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 49AT - Desligamento | 21 |  |  | DI Val | 101 | 18 | 1 | TR3_49_ATUADO | 375 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Partida Externa do 62BF | 22 |  |  | - | - | - | - | (Uso Interno) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | B23P1 | 86FD/BT (23kV) - Abertura e Bloqueio Disj.52-02 | 23 |  |  | DI Val | 240 | 199 | 1 | (Somente p/Intertravamento!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | B69 | 86FD/AT (69 kV) - Abertura e Bloqueio Disj.52-02 | 24 |  |  | - | - | - | - | (Somente p/Intertravamento!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 43TC - Excluída | - |  |  | DI Val | 101 | 85 | 1 | TR3AT_43TC_EXCLUIDA | 377 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | TRIP da Prot.26/49 - Atuado | - |  | 15 | DI Val | 240 | 200 | 1 | TR3_26_49_TRIP_ATUADO | 378 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | TRIP da Prot.50/63T/63C - Atuado | - |  | 14 | - | - | - | - | (Somente p/Intertravamento!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 62BF - Atuado | - |  | 3 | Auto Fault | 160 | 85 | 2 | TR3AT_62BF_ATUADO | 379 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 50 ABC - Estágio 1 - Atuado | - |  | 4/10 | Auto Fault | 160 | 90 | 2 | TR3AT_50ABC_E1_ATUADO | 380 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 50 ABC - Estágio 2 - Atuado | - |  | 4/10 | Auto Fault | 160 | 91 | 2 | TR3AT_50ABC_E2_ATUADO | 381 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 50 N - Estágio 1 - Atuado | - |  | 4 | Auto Fault | 160 | 92 | 2 | TR3AT_50N_E1_ATUADO | 382 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 50 N - Estágio 2 - Atuado | - |  | 4 | Auto Fault | 160 | 93 | 2 | TR3AT_50N_E2_ATUADO | 383 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 50/51 Fase A - Atuado | - |  | - | Fault DI | 60 | 54 | 2 | TR3AT_50FA_51FA_ATUADO | 384 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 50/51 Fase B - Atuado | - |  | - | Fault DI | 60 | 55 | 2 | TR3AT_50FB_51FB_ATUADO | 385 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 50/51 Fase C - Atuado | - |  | - | Fault DI | 60 | 56 | 2 | TR3AT_50FC_51FC_ATUADO | 386 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 51 ABC - Atuado | - |  | 4/10 | Fault DI | 60 | 58 | 2 | TR3AT_51ABC_ATUADO | 387 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 51 N - Atuado | - |  | 4/10 | Fault DI | 60 | 66 | 2 | TR3AT_51N_ATUADO | 388 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Prot.67 - Bloqueada | - |  | - | DiVal | 63 | 11 | 1 | TR3AT_67_BLOQUEADA | 389 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Atuado 67 - Estágio 1 | - |  | 4 | Fault Di | 63 | 25 | 2 | TR3AT_67_E1_ATUADO | 390 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Atuado 67 - Estágio 2 | - |  | 4 | Fault Di | 63 | 72 | 2 | TR3AT_67_E2_ATUADO | 391 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Atuado 67 - TOC | - |  | 4 | Fault Di | 63 | 35 | 2 | TR3AT_67TOC_ATUADO | 392 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Atuado 67N - Estágio 1 | - |  | 4 | Fault Di | 63 | 43 | 2 | TR3AT_67N_E1_ATUADO | 393 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Atuado 67N - Estágio 2 | - |  | 4 | Fault Di | 63 | 64 | 2 | TR3AT_67N_E2_ATUADO | 394 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Atuado 67N - TOC | - |  | 4 | Fault Di | 63 | 46 | 2 | TR3AT_67N_TOC_ATUADO | 395 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Atuado 67 - Fase A | - |  | - | Fault Di | 63 | 75 | 2 | TR3AT_67_FA_ATUADO | 396 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Atuado 67 - Fase B | - |  | - | Fault Di | 63 | 76 | 2 | TR3AT_67_FB_ATUADO | 397 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Atuado 67 - Fase C | - |  | - | Fault Di | 63 | 77 | 2 | TR3AT_67_FC_ATUADO | 398 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Supervisão Medição: Falha Fusível TPs | - |  | - | DiVal | 135 | 149 | 1 | TR3AT_60FF_ALARME | 399 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Saúde Comunicação | - |  | - |  |  |  |  | TR3AT_SAUDE_COMUNIC | 400 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## TR3DIF
SE GUAPORÉ - TR3 DIF
RELÉ xxF1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 03) | TR3 | 87 Trip Geral - Atuado |  |  |  | AF | 176 | 68 | 2 | TR3DIF_87_ATUADO | 410 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 03) | TR3 | 87 Fase A - Atuado |  | 1 | X | AF | 176 | 86 | 2 | TR3DIF_87_FA_ATUADO | 411 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 03) | TR3 | 87 Fase B - Atuado |  | 2 | X | AF | 176 | 87 | 2 | TR3DIF_87_FB_ATUADO | 412 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 03) | TR3 | 87 Fase C - Atuado |  | 3 | X | AF | 176 | 88 | 2 | TR3DIF_87_FC_ATUADO | 413 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 03) | TR3 | 87 - Excluído |  | 4 | X | DiVal | 75 | 15 | 1 | TR3DIF_87_EXCLUIDO | 414 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 03) | TR3 | 20 ALarme | 1 |  | X | DiVal | 101 | 10 | 1 | TR3DIF_20_ALARME | 415 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 03) | TR3 | 20 Desligamento | 2 |  | X | DiVal | 101 | 11 | 1 | TR3DIF_20_DESLIGAMENTO | 416 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 03) | TR3 | Saúde Comunicação | [7 empty] | TR3DIF_SAUDE_COMUNIC | 417 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## TR3BT
SE GUAPORÉ - TR3 BT 23kV
RELÉ xxF1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
7SJ62 (End.: 04) | TR3BT | Tensão Fase B da Barra P1 23kV |  |  |  | AiVal | 134 | 137 | 9/6 | TR3BT_TENSAO_FB | 120 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Corrente Fase A |  |  |  | AiVal | 134 | 137 | 9/1 | TR3BT_CORRENTE_FA | 121 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Corrente Fase B |  |  |  | AiVal | 134 | 137 | 9/2 | TR3BT_CORRENTE_FB | 122 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Corrente Fase C |  |  |  | AiVal | 134 | 137 | 9/3 | TR3BT_CORRENTE_FC | 123 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Potência Ativa |  |  |  | AiVal | 134 | 137 | 9/11 | TR3BT_POT_ATIVA | 124 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Potência Reativa |  |  |  | AiVal | 134 | 137 | 9/12 | TR3BT_POT_REATIVA | 125 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Secc.89-24 (03Q4) - Abrir / Fechar |  | 5/6 |  | Double | 240 | 161 | 20 | TR3BT_COMANDOS_S8924 | 115 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Trocar Grupo de Ajuste A/B |  |  |  | Double | 240 | 188 | 20 | TR3BT_COMANDOS_GRUPO | 116 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 81 - Inclui / Excliu |  |  |  | Double | 240 | 220 | 20 | TR3BT_81_I_E | 117 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Secc.89-24 – Aberta | 1 |  | 3 | DiSOEx2 | 240 | 161 | 1 | TR3BT_SECC89D_ABERTA | 420 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Secc.89-24 – Fechada | 2 |  | 3 | DiSOEx2 | 240 | 161 | 1 | TR3BT_SECC89D_FECHADA | 421 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 02) | TR3BT | Secc.89-24 – Falta VCC Comando | 8 |  |  | DI Val | 240 | 191 | 1 | TR3BT_FALTA_VCC_COMANDO | 422 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 04) | TR3BT | Secc.89-24 – 43TC - Excluída |  |  |  | DI Val | 101 | 85 | 1 | TR3BT_43TC_EXCLUIDA | 423 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Secc.89-24 – Chave Local/Remoto - Pos. Local | 5 |  |  | DiVal | 240 | 189 | 1 | TR3BT_43LR_POS_LOCAL | 424 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Secc.89-24 – Falta VCC Motor | 4 |  |  | DiVal | 240 | 190 | 1 | TR3BT_FALTA_VCC_MOTOR | 425 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 04) | B23P1 | 86FD P1 23kV Atuado | 6 |  |  | DI Val | 240 | 199 | 1 | B23P1_86FD_P1_ATUADO | 426 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Grupo A Ativo |  |  |  | DI Val | 160 | 23 | 1 | TR3BT_GRUPO_A_ATIVO | 427 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Grupo B Ativo |  |  |  | DI Val | 160 | 24 | 1 | TR3BT_GRUPO_B_ATIVO | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 51 ABC - Atuado |  |  | 1/4 | FDI | 60 | 58 | 2 | TR3BT_51ABC_ATUADO | 429 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 50 ABC - Estágio 1 - Atuado |  |  | 1/4 | AF | 160 | 90 | 2 | TR3BT_50ABC_1_ATUADO | 430 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 50 ABC - Estágio 2 - Atuado |  |  | 1/4 | AF | 160 | 91 | 2 | TR3BT_50ABC_2_ATUADO | 431 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 50 N - Estágio 1 - Atuado |  |  | 1/4 | AF | 160 | 92 | 2 | TR3BT_50N_1_ATUADO | 432 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 50 N - Estágio 2 - Atuado |  |  | 1/4 | AF | 160 | 93 | 2 | TR3BT_50N_2_ATUADO | 433 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 50/51 Fase A - Atuado |  |  | 1/4 | FDI | 60 | 54 | 2 | TR3BT_50FA_51FA_ATUADO | 434 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 50/51 Fase B - Atuado |  |  | 1/4 | FDI | 60 | 55 | 2 | TR3BT_50FB_51FB_ATUADO | 435 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 50/51 Fase C - Atuado |  |  | 1/4 | FDI | 60 | 56 | 2 | TR3BT_50FC_51FC_ATUADO | 436 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 51 N - Atuado |  |  | 1/4 | FDI | 60 | 66 | 2 | TR3BT_51N_ATUADO | 437 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 62BF - Atuado |  |  |  | Auto Fault | 160 | 85 | 2 | TR3BT_50BF_ATUADO | 438 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 81 Estagio 1 Atuado |  |  | 1/4 | FDI | 70 | 234 | 2 | TR3BT_81_E1 | 439 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 81 Estagio 2 Atuado |  |  | 1/4 | FDI | 70 | 235 | 2 | TR3BT_81_E2 | 440 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 81 - Excluido |  |  |  |  | 240 | 221 | 1 | TR3BT_81_Excluido | 441 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Saude Comunicação | [7 empty] | TR3BT_SAUDE_COMUNIC | 442 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## TR2AT
SE GUAPORÉ - TR3 AT 69kV
RELÉ xxF1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
7SJ63 (End.: 13d/0Dh) | TR2AT | Tensão Fase B da Barra de 69 kV |  |  |  | AI Val | 134 | 137 | 9/6 | TR2AT_TENSAO_FB | 135 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Corrente Fase A |  |  |  | AI Val | 134 | 137 | 9/1 | TR2AT_CORRENTE_FA | 136 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Corrente Fase B |  |  |  | AI Val | 134 | 137 | 9/2 | TR2AT_CORRENTE_FB | 137 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Corrente Fase C |  |  |  | AI Val | 134 | 137 | 9/3 | TR2AT_CORRENTE_FC | 138 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Potência Ativa |  |  |  | AI Val | 134 | 137 | 9/11 | TR2AT_POT_ATIVA | 139 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Potência Reativa |  |  |  | AI Val | 134 | 137 | 9/12 | TR2AT_POT_REATIVA | 140 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Disj.52-03 (15QA) - Abrir/Fechar |  | 4/5 |  | Command | 240 | 160 | 20 | TR2AT_COMANDOS_DJ | 130 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Secc.89-08 (15QD) - Abrir/Fechar |  | 1/2 |  | Command | 240 | 161 | 20 | TR2AT_COMANDOS_S8908 | 131 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Disj.52-03 – Aberto | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | TR2AT_DJ_ABERTO | 460 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Disj.52-03 – Fechado | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | TR2AT_DJ_FECHADO | 461 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Secc.89-08 (15QD) - Aberto | 8 |  |  | DiSOEx2 | 240 | 161 | 1 | TR2AT_S8908_ABERTA | 462 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Secc.89-08 (15QD) - Fechado | 9 |  |  | DiSOEx2 | 240 | 161 | 1 | TR2AT_S8908_FECHADA | 463 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Disj. 52-03 - 43LR em posição LOCAL | 3 |  |  | DI Val | 240 | 190 | 1 | TR2AT_DJ_43LR_LOCAL | 464 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Disj. 52-03 - Mola Descarregada | 4 |  |  | DI Val | 240 | 191 | 1 | TR2AT_DJ_MOLA_DESC | 465 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Disj. 52-03 - SF6 Alarme | ? |  |  | DI Val | 240 | 194 | 1 | TR2AT_SF6_Alarme | 466 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Disj. 52-03 - SF6 Bloqueio | ? |  |  | DI Val | 240 | 195 | 1 | TR2AT_SF6_BLOQUEIO | 467 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Oper.Indevida Seccionadora 89-08 (S89D) | 5 |  |  | DI Val | 240 | 192 | 1 | TR2AT_OP_IND_SECC | 468 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 86T2 - Atuado | 6 |  |  | DI Val | 240 | 193 | 1 | TR2_86T2_ATUADO | 469 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Disj.52-03 - Superv.Circuito TRIP - Alarme | 7 |  |  | DI Val | 170 | 57 | 1 | TR2AT_CIRC_TRIP_FALHADO | 470 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 63T - Alarme | 10 |  |  | DI Val | 101 | 10 | 1 | TR2_63T_ALARME | 471 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 63T - Desligamento | 11 |  |  | DI Val | 101 | 11 | 1 | TR2_63T_ATUADO | 472 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Reserva | 12 |  |  | - | - | - | - | Reserva | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Reserva | 13 |  |  | - | - | - | - | Reserva | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 63C - Alarme | 14 |  |  | DI Val | 101 | 12 | 1 | TR2_63C_ALARME | 473 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 63C - Desligamento | 15 |  |  | DI Val | 101 | 13 | 1 | TR2_63C_ATUADO | 474 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 26T - Alarme | 16 |  |  | DI Val | 101 | 14 | 1 | TR2_26T_ALARME | 475 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 26T - Desligamento | 17 |  |  | DI Val | 101 | 15 | 1 | TR2_26T_ATUADO | 476 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 49BT - Alarme | 18 |  |  | DI Val | 101 | 16 | 1 | TR2_49BT_ALARME | 477 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 49BT - Desligamento | 19 |  |  | DI Val | 101 | 17 | 1 | TR2_49BT_ATUADO | 478 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 49AT - Alarme | 20 |  |  | DI Val | 101 | 18 | 1 | TR2_49_ALARME | 479 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 49AT - Desligamento | 21 |  |  | DI Val | 101 | 19 | 1 | TR2_49_ATUADO | 480 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Partida Externa do 62BF | 22 |  |  | - | - | - | - | (Uso Interno) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | B23P2 | 86FD/BT (23kV) - Abertura e Bloqueio Disj.52-03 | 23 |  |  | - | - | - | - | (Somente p/Intertravamento!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | B69 | 86FD/AT (69kV) - Abertura e Bloqueio Disj.52-03 | 24 |  |  | - | - | - | - | (Somente p/Intertravamento!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 43TC - Excluída | - |  |  | DI Val | 101 | 85 | 1 | TR2AT_43TC_EXCLUIDA | 481 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | TRIP da Prot.26/49 - Atuado | - |  | 15 | DI Val | 240 | 200 | 1 | TR2_26_49_TRIP_ATUADO | 482 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | TRIP da Prot.50/63T/63C - Atuado | - |  | 14 | - | - | - | - | (Somente p/Intertravamento!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 62BF - Atuado | - |  | 3 | Auto Fault | 160 | 85 | 2 | TR2AT_62BF_ATUADO | 483 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 50 ABC - Estágio 1 - Atuado | - |  | 4/10 | Auto Fault | 160 | 90 | 2 | TR2AT_50ABC_E1_ATUADO | 484 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 50 ABC - Estágio 2 - Atuado | - |  | 4/10 | Auto Fault | 160 | 91 | 2 | TR2AT_50ABC_E2_ATUADO | 485 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 50 N - Estágio 1 - Atuado | - |  | 4 | Auto Fault | 160 | 92 | 2 | TR2AT_50N_E1_ATUADO | 486 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 50 N - Estágio 2 - Atuado | - |  | 4 | Auto Fault | 160 | 93 | 2 | TR2AT_50N_E2_ATUADO | 487 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 50/51 Fase A - Atuado | - |  | - | Fault DI | 60 | 54 | 2 | TR2AT_50FA_51FA_ATUADO | 488 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 50/51 Fase B - Atuado | - |  | - | Fault DI | 60 | 55 | 2 | TR2AT_50FB_51FB_ATUADO | 489 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 50/51 Fase C - Atuado | - |  | - | Fault DI | 60 | 56 | 2 | TR2AT_50FC_51FC_ATUADO | 490 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 51 ABC - Atuado | - |  | 4/10 | Fault DI | 60 | 58 | 2 | TR2AT_51ABC_ATUADO | 491 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 51 N - Atuado | - |  | 4/10 | Fault DI | 60 | 66 | 2 | TR2AT_51N_ATUADO | 492 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Prot.67 - Bloqueada | - |  | - | DiVal | 63 | 11 | 1 | TR2AT_67_BLOQUEADA | 493 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Atuado 67 - Estágio 1 | - |  | 4 | Fault Di | 63 | 25 | 2 | TR2AT_67_E1_ATUADO | 494 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Atuado 67 - Estágio 2 | - |  | 4 | Fault Di | 63 | 72 | 2 | TR2AT_67_E2_ATUADO | 495 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Atuado 67 - TOC | - |  | 4 | Fault Di | 63 | 35 | 2 | TR2AT_67TOC_ATUADO | 496 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Atuado 67N - Estágio 1 | - |  | 4 | Fault Di | 63 | 43 | 2 | TR2AT_67N_E1_ATUADO | 497 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Atuado 67N - Estágio 2 | - |  | 4 | Fault Di | 63 | 64 | 2 | TR2AT_67N_E2_ATUADO | 498 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Atuado 67N - TOC | - |  | 4 | Fault Di | 63 | 46 | 2 | TR2AT_67N_TOC_ATUADO | 499 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Atuado 67 - Fase A | - |  |  | Fault Di | 63 | 75 | 2 | TR2AT_67_FA_ATUADO | 500 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Atuado 67 - Fase B | - |  | - | Fault Di | 63 | 76 | 2 | TR2AT_67_FB_ATUADO | 501 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Atuado 67 - Fase C | - |  | - | Fault Di | 63 | 77 | 2 | TR2AT_67_FC_ATUADO | 502 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Supervisão Medição: Falha Fusível TPs | - |  | - | DiVal | 135 | 149 | 1 | TR2AT_60FF_ALARME | 503 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Saúde Comunicação | - |  | - |  |  |  |  | TR2AT_SAUDE_COMUNIC | 504 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## TR2DIF
SE GUAPORÉ - TR2 DIF
RELÉ xxF1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 01) | TR2 | 87 Trip Geral - Atuado |  | 1/2 |  | AF | 176 | 68 | 2 | TR2DIF_87_ATUADO | 510 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 01) | TR2 | 87 Fase A - Atuado |  |  | 1 | AF | 176 | 86 | 2 | TR2DIF_87_FA_ATUADO | 511 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 01) | TR2 | 87 Fase B - Atuado |  |  | 2 | AF | 176 | 87 | 2 | TR2DIF_87_FB_ATUADO | 512 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 01) | TR2 | 87 Fase C - Atuado |  |  | 3 | AF | 176 | 88 | 2 | TR2DIF_87_FC_ATUADO | 513 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 01) | TR2 | 87 - Excluído |  |  |  | DiVal | 75 | 15 | 1 | TR2DIF_87_EXCLUIDO | 514 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 01) | TR2 | 20 - Alarme | 1 | 1/2 |  | DiVal | 101 | 10 | 1 | TR2DIF_20_ALARME | 515 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 01) | TR2 | 20 - Desligamento | 2 | 1/2 |  | DiVal | 101 | 11 | 1 | TR2DIF_20_DESLIGAMENTO | 516 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 01) | TR2 | Saúde Comunicação | [7 empty] | TR2DIF_SAUDE_COMUNIC | 517 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## TR2BT
SE GUAPORÉ - TR2 BT 23kV
RELÉ xxF1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
7SJ62 (End.: 02) | TR2BT | Tensão Fase B da Barra P2 23kV |  |  |  | AiVal | 134 | 137 | 9/6 | TR2BT_TENSAO_FB | 145 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Corrente Fase A |  |  |  | AiVal | 134 | 137 | 9/1 | TR2BT_CORRENTE_FA | 146 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Corrente Fase B |  |  |  | AiVal | 134 | 137 | 9/2 | TR2BT_CORRENTE_FB | 147 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Corrente Fase C |  |  |  | AiVal | 134 | 137 | 9/3 | TR2BT_CORRENTE_FC | 148 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Potência Ativa |  |  |  | AiVal | 134 | 137 | 9/11 | TR2BT_POT_ATIVA | 149 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Potência Reativa |  |  |  | AiVal | 134 | 137 | 9/12 | TR2BT_POT_REATIVA | 150 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Secc. 89-62 (15QE) – Abrir / Fechar |  | 5/6 |  | Double | 240 | 161 | 20 | TR2BT_COMANDOS_S8962 | 135 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Trocar Grupo de Ajuste A/B |  |  |  | Double | 240 | 188 | 20 | TR2BT_COMANDOS_GRUPO | 136 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 81 - Inclui / Excliu |  |  |  | Double | 240 | 220 | 20 | TR2BT_81_I_E | 137 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Secc. 89-62 (15QE) – Aberta | 1 |  |  | DiSOEx2 | 240 | 161 | 1 | TR2BT_S8962_ABERTA | 520 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Secc. 89-62 (15QE) – Fechada | 2 |  |  | DiSOEx2 | 240 | 161 | 1 | TR2BT_S8962_FECHADA | 521
7SJ62 (End.: 02) | TR2BT | Secc. 89-62 (15QE) – Falta VCC Comando | 8 |  |  | DiVal | 240 | 190 | 1 | TR2BT_FALTA_VCC_COMANDO | 522 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Secc. 89-62 (15QE) – Falta VCC Motor | 4 |  |  | DiVal | 240 | 191 | 1 | TR2BT_FALTA_VCC_MOTOR | 523 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Secc. 89-62 (15QE) – Chave Local/Remoto - Pos. Local | 5 |  |  | DiVal | 240 | 189 | 1 | TR2BT_43LR_POS_LOCAL | 524 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Secc. 89-62 (15QE) – 43TC - Excluída |  |  |  | DI Val | 101 | 85 | 1 | TR2BT_43TC_EXCLUIDA | 525 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | B23P2 | 86FD Barra P2 23kV Atuado | 6 |  |  | DiVal | 240 | 199 | 1 | B23P2_86FD_P2_ATUADO | 526 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 50 ABC - Estágio 1 - Atuado |  |  |  | AF | 160 | 90 | 2 | TR2BT_50ABC_1_ATUADO | 527 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 50 ABC - Estágio 2 - Atuado |  |  |  | AF | 160 | 91 | 2 | TR2BT_50ABC_2_ATUADO | 528 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 50 N - Estágio 1 - Atuado |  |  |  | AF | 160 | 92 | 2 | TR2BT_50N_1_ATUADO | 529 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 50 N - Estágio 2 - Atuado |  |  |  | AF | 160 | 93 | 2 | TR2BT_50N_2_ATUADO | 530 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 50/51 Fase A - Atuado |  |  |  | FDI | 60 | 54 | 2 | TR2BT_50FA_51FA_ATUADO | 531 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 50/51 Fase B - Atuado |  |  |  | FDI | 60 | 55 | 2 | TR2BT_50FB_51FB_ATUADO | 532 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 50/51 Fase C - Atuado |  |  |  | FDI | 60 | 56 | 2 | TR2BT_50FC_51FC_ATUADO | 533 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 51 ABC - Atuado |  |  |  | FDI | 60 | 58 | 2 | TR2BT_51ABC_ATUADO | 534 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 51 N - Atuado |  |  |  | FDI | 60 | 66 | 2 | TR2BT_51N_ATUADO | 535 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Grupo A Ativo |  |  |  | DiVal | 160 | 23 | 1 | TR2BT_GRUPO_A_ATIVO | 536 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Grupo B Ativo |  |  |  | DiVal | 160 | 24 | 1 | TR2BT_GRUPO_B_ATIVO | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 81 - Estágio 1 - Atuado (Subfrequencia) |  |  |  | FDI | 70 | 234 | 2 | TR2BT_81_E1 | 537 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 81 - Estágio 2 - Atuado |  |  |  | FDI | 70 | 235 | 2 | TR2BT_81_E2 | 538 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 81 - Excluido |  |  |  | DiVal | 240 | 221 | 1 | TR2BT_81_Excluido | 539 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Saude Comunicação | [7 empty] | TR2BT_SAUDE_COMUNIC | 540 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## TR2AT-TM1
TREETECH |  | Descrição do ponto: | RELE |  |  | MODBUS | SLAVE |  |  | MASTER |  | LOCAL |  | COS |  | S6
EQUIPAMENTO | MÓDULO |  | FUNÇÃO MODBUS | REGISTRADOR | BIT | TIPO | VARIAVEIS | Identificação do ponto: | Lógica | Identificação do ponto: | DNP3 | SUL | RGE | SUL | RGE | NIVEL2
Medição
TREETECH TM (End: 16) | TR2 | Temperatura do óleo | 3 (Read Holding Reg) | 40020 |  | 16 Bits |  | TR2_TM11_TEMP_OLEO | IDF | TR2_TEMP_OLEO | 151
TREETECH TM (End: 16) | TR2AT | Temperatura do enrolamento 1 | 3 (Read Holding Reg) | 40021 |  | 16 Bits |  | TR2_TM11_TEMP_ENROL_AT |  | TR2_TEMP_ENROL_AT | 152
Sinalização
TREETECH TM (End: 16) | TR2 | Temp.Óleo - Alarme | 3 (Read Holding Reg) | 40024 | 0 |  |  | TR2_TM11_26T_ALARME |  | TR2_26T_ALARME | -
TREETECH TM (End: 16) | TR2 | Temp.Óleo - Desligamento | 3 (Read Holding Reg) | 40024 | 1 |  |  | TR2_TM11_26T_ATUADO |  | TR2_26T_ATUADO | -
TREETECH TM (End: 16) | TR2AT | Temp.Enrolamento AT- Alarme | 3 (Read Holding Reg) | 40024 | 4 |  |  | TR2_TM11_49_ALARME |  | TR2AT_49AT_ALARME | -
TREETECH TM (End: 16) | TR2AT | Temp.Enrolamento AT- Desligamento | 3 (Read Holding Reg) | 40024 | 5 |  |  | TR2_TM11_49_ATUADO |  | TR2AT_49AT_ATUADO | -
TREETECH TM (End: 16) | TR2 | SAÚDE COMUNICAÇÃO | [7 empty] | TR2_TM11_SAUDE_COMUNIC | 555

## TR2BT-TM2
TREETECH |  | Descrição do ponto: | RELE |  |  | MODBUS | SLAVE |  |  | MASTER |  | LOCAL |  | COS |  | S6
EQUIPAMENTO | MÓDULO |  | FUNÇÃO MODBUS | REGISTRADOR | BIT | TIPO | VARIAVEIS | Identificação do ponto: | Lógica | Identificação do ponto: | DNP3 | SUL | RGE | SUL | RGE | NIVEL2
Medição
TREETECH TM (End: 15) | TR2 | Temperatura do óleo | 3 (Read Holding Reg) | 40020 |  | 16 Bits |  | TR2_TM12_TEMP_OLEO | IDF | TR2_TEMP_OLEO | -
TREETECH TM (End: 15) | TR2BT | Temperatura do enrolamento 1 | 3 (Read Holding Reg) | 40021 |  | 16 Bits |  | TR2_TM12_TEMP_ENROL_BT |  | TR2_TEMP_ENROL_BT | 154
Sinalização
TREETECH TM (End: 15) | TR2 | VF1 - Ligada | 3 (Read Holding Reg) | 40001 | 0 |  |  | TR2_TM1BT_VF1_LIGADA |  | TR2_VF1_LIGADA | -
TREETECH TM (End: 15) | TR2 | VF2 - Ligada | 3 (Read Holding Reg) | 40001 | 1 |  |  | TR2_TM1BT_VF2_LIGADA |  | TR2_VF2_LIGADA | -
TREETECH TM (End: 15) | TR2 | Temp.Óleo - Alarme | 3 (Read Holding Reg) | 40024 | 0 |  |  | TR2_TM12_26T_ALARME |  | TR2_26T_ALARME | -
TREETECH TM (End: 15) | TR2 | Temp.Óleo - Desligamento | 3 (Read Holding Reg) | 40024 | 1 |  |  | TR2_TM12_26T_ATUADO |  | TR2_26T_ATUADO | -
TREETECH TM (End: 15) | TR2BT | Temp.Enrolamento BT- Alarme | 3 (Read Holding Reg) | 40024 | 4 |  |  | TR2_TM12_49_ALARME |  | TR2BT_49BT_ALARME | -
TREETECH TM (End: 15) | TR2BT | Temp.Enrolamento BT- Desligamento | 3 (Read Holding Reg) | 40024 | 5 |  |  | TR2_TM12_49_ATUADO |  | TR2BT_49BT_ATUADO | -
TREETECH TM (End: 15) | TR2 | SAÚDE COMUNICAÇÃO | [7 empty] | TR2_TM12_SAUDE_COMUNIC | 560

## SPS-TR2-TR3
SPS |  | Descrição do ponto: | RELE |  |  | MODBUS | SLAVE |  |  | MASTER |  | LOCAL |  | COS |  | S6
EQUIPAMENTO | MÓDULO |  | FUNÇÃO MODBUS | REGISTRADOR | BIT | TIPO | VARIAVEIS | Identificação do ponto: | Lógica | Identificação do ponto: | DNP3 | SUL | RGE | SUL | RGE | NIVEL2
Medição
SPS (End: 14) | TR2 | Medida TAP ATUAL | 3 (Read Holding Reg) | 40009 |  | 16 Bits |  | TR2_TAP | SPS | TR2_TAP | 153
SPS (End: 14) | TR3 | Medida TAP ATUAL | 3 (Read Holding Reg) | 40018 |  | 16 Bits |  | TR3_TAP | SPS | TR3_TAP | 127
Comando
SPS (End: 14) | TR2 | Comando TAP | 3 (Read Holding Reg) | 40788 | 0_1 |  |  | TR2_TELECOM_TAP | SPS | TR2_TELECOM_TAP | 140
SPS (End: 14) | TR2 | Comandos R90 | 3 (Read Holding Reg) | 40788 | 5_6 |  |  | TR2_TELECOM_R90 | SPS | TR2_TELECOM_R90 | 141
SPS (End: 14) | TR3 | Comando TAP | 3 (Read Holding Reg) | 41556 | 0_1 |  |  | TR3_TELECOM_TAP | SPS | TR3_TELECOM_TAP | 119
SPS (End: 14) | TR3 | Comandos R90 | 3 (Read Holding Reg) | 41556 | 5_6 |  |  | TR3_TELECOM_R90 | SPS | TR3_TELECOM_R90 | 120
SPS (End: 14) | TR2 | Comandos Mestre TR2 | 3 (Read Holding Reg) | 40788 | 2 |  |  | TR2_TELECOM_MESTRE | SPS | TR2_TELECOM_MESTRE | 142
SPS (End: 14) | TR3 | Comandos Mestre TR3 | 3 (Read Holding Reg) | 41556 | 2 |  |  | TR3_TELECOM_MESTRE | SPS | TR3_TELECOM_MESTRE | 121
SPS (End: 14) | TR2 | Comando Individual | 3 (Read Holding Reg) | 40788 | 4 |  |  | TR2_TELECOM_INDIVIDUAL | SPS | TR2_TELECOM_INDIVIDUAL | 143
SPS (End: 14) | TR3 | Comando Individual | 3 (Read Holding Reg) | 41556 | 4 |  |  | TR3_TELECOM_INDIVIDUAL | SPS | TR3_TELECOM_INDIVIDUAL | 122
Sinalização
SPS (End: 14) | TR2 | Relé 90 Excluído/Incluído | 3 (Read Holding Reg) | 40010 | 3 |  |  | TR2_R90_EXCLUIDO | SPS | TR2_R90_EXCLUIDO | 561
SPS (End: 14) | TR2 | Posição MESTRE | 3 (Read Holding Reg) | 40010 | 0 |  |  | TR2_MESTRE | SPS | TR2_MESTRE | 562
SPS (End: 14) | TR2 | Posição COMANDADO | 3 (Read Holding Reg) | 40010 | 1 |  |  | TR2_COMANDADO | SPS | TR2_COMANDADO | 563
SPS (End: 14) | TR2 | Posição INDIVIDUAL | [5 empty] | TR2_INDIVIDUAL | SPS | TR2_INDIVIDUAL | 564
SPS (End: 14) | TR2 | Chave L/R - Pos. Local | 3 (Read Holding Reg) | 40010 | 2 |  |  | TR2_SPS_43LR_LOCAL | SPS | TR2_SPS_43LR_LOCAL | 565
SPS (End: 14) | TR2 | Erro Paralelismo | 3 (Read Holding Reg) | 40011 | 1 |  |  | TR2_SPS_ERRO_PARALEL | SPS | TR2_SPS_ERRO_PARALEL | 566
SPS (End: 14) | TR3 | Relé 90 Excluído/Incluído | 3 (Read Holding Reg) | 40019 | 3 |  |  | TR3_R90_EXCLUIDO | SPS | TR3_R90_EXCLUIDO | 454
SPS (End: 14) | TR3 | Posição MESTRE | 3 (Read Holding Reg) | 40019 | 0 |  |  | TR3_MESTRE | SPS | TR3_MESTRE | 455
SPS (End: 14) | TR3 | Posição COMANDADO | 3 (Read Holding Reg) | 40019 | 1 |  |  | TR3_COMANDADO | SPS | TR3_COMANDADO | 456
SPS (End: 14) | TR3 | Posição INDIVIDUAL | [5 empty] | TR3_INDIVIDUAL | SPS | TR3_INDIVIDUAL | 457
SPS (End: 14) | TR3 | Chave L/R - Pos.Local | 3 (Read Holding Reg) | 40019 | 2 |  |  | TR3_SPS_43LR_LOCAL | SPS | TR3_SPS_43LR_LOCAL | 458
SPS (End: 14) | TR3 | Erro Paralelismo | 3 (Read Holding Reg) | 40020 | 1 |  |  | TR3_SPS_ERRO_PARALEL | SPS | TR3_SPS_ERRO_PARALEL | 459
SPS (End: 14)
SPS (End: 14) | TR2 | Saúde Comunicação | 3 (Read Holding Reg) | [5 empty] | SPS | SPS_SAUDE_COMUNIC | 567
SPS (End: 14)

## TR1AT
SE GUAPORÉ - TR1 AT 138kV
RELÉ xxF1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
7SJ63 (End.: 14d/0Eh) | TR1AT | Tensão Fase B da Barra de 138 kV |  |  |  | AI Val | 134 | 137 | 9/6 | TR1AT_TENSAO_FB | 180 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Corrente Fase A |  |  |  | AI Val | 134 | 137 | 9/1 | TR1AT_CORRENTE_FA | 181 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Corrente Fase B |  |  |  | AI Val | 134 | 137 | 9/2 | TR1AT_CORRENTE_FB | 182 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Corrente Fase C |  |  |  | AI Val | 134 | 137 | 9/3 | TR1AT_CORRENTE_FC | 183 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Potência Ativa |  |  |  | AI Val | 134 | 137 | 9/11 | TR1AT_POT_ATIVA | 184 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Potência Reativa |  |  |  | AI Val | 134 | 137 | 9/12 | TR1AT_POT_REATIVA | 185 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Disj.52-17 - Abrir/Fechar |  | 4/5 |  | Command | 240 | 160 | 20 | TR1AT_COMANDOS_DJ | 150 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-112 (S89D) - Abrir/Fechar |  | 1/2 |  | Command | 240 | 161 | 20 | TR1AT_COMANDOS_S89D | 151 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-114 (S89E) - Abrir/Fechar |  | 8/9 |  | Command | 240 | 162 | 20 | TR1AT_COMANDOS_S89E | 152 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-116 (S89C) - Abrir/Fechar |  | 11/12 |  | Command | 240 | 163 | 20 | TR1AT_COMANDOS_S89C | 153 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Disj.52-17 – Aberto | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | TR1AT_DJ_ABERTO | 600 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Disj.52-17 – Fechado | 2 |  |  | DiSOEx2 | 240 | 160 | 1 | TR1AT_DJ_FECHADO | 601 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-112 (S89D) - Aberto | 8 |  |  | DiSOEx2 | 240 | 161 | 1 | TR1AT_S89D_ABERTO | 602 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-112 (S89D) - Fechado | 9 |  |  | DiSOEx2 | 240 | 161 | 1 | TR1AT_S89D_FECHADO | 603 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-114 (S89E) - Aberto | 11 |  |  | DiSOEx2 | 240 | 162 | 1 | TR1AT_S89E_ABERTO | 604 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-114 (S89E) - Fechado | 12 |  |  | DiSOEx2 | 240 | 162 | 1 | TR1AT_S89E_FECHADO | 605 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-116 (S89C) - Aberto | 16 |  |  | DiSOEx2 | 240 | 163 | 1 | TR1AT_S89C_ABERTO | 606 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-116 (S89C) - Fechado | 17 |  |  | DiSOEx2 | 240 | 163 | 1 | TR1AT_S89C_FECHADO | 607 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Disj. 52-17 - BP SF6 (1o.Estágio) - ALARME | 3 |  |  | DI Val | 240 | 190 | 1 | TR1AT_DJ_SF6_ALARME | 608 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Disj. 52-17 - BP SF6 (2o.Estágio) - ALARME | 4 |  |  | DI Val | 240 | 191 | 1 | TR1AT_DJ_SF6_BLOQUEIO | 609 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Disj. 52-17 - Mola Descarregada/Falta VCC Motor | 5 |  |  | DI Val | 240 | 192 | 1 | TR1AT_DJ_MOLA_DESC | 610 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Disj. 52-17 - 43LR em posição LOCAL | 6 |  |  | DI Val | 240 | 193 | 1 | TR1AT_DJ_43LR_LOCAL | 611 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Disj. 52-17 - Superv.Circuito TRIP - Alarme | 7 |  |  | DI Val | 170 | 57 | 1 | TR1AT_CIRC_TRIP_FALHADO | 612 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-112/114/116 - 43LR em posição LOCAL | 10 |  |  | DI Val | 240 | 194 | 1 | TR1AT_SECC_43LR_LOCAL | 613 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-112/114/116 - Falta VCC COM/MOTOR | 13 |  |  | DI Val | 240 | 195 | 1 | TR1AT_SECC_FALTA_VCC | 614 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 43TC - Excluída | - |  |  | DI Val | 101 | 85 | 1 | TR1AT_43TC_EXCLUIDA | 615 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1 | 26T/49AT/49BT - Alarme | 14 |  |  | DI Val | 101 | 10 | 1 | TR1_26T_49HX_ALARME | 616 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1 | 26T/49AT/49BT - Desligamento | 15 |  | 4 | DI Val | 101 | 11 | 1 | TR1_26T_49HX_ATUADOI | 617 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Oper.Indevida Seccionadoras | 18 |  |  | DI Val | 240 | 198 | 1 | TR1AT_OP_IND_SECC | 618 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1 | 86T1 - Atuado | 19 |  |  | DI Val | 240 | 199 | 1 | TR1_86T1_ATUADO | 619 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1 | 63T - Alarme | 20 |  |  | DI Val | 101 | 12 | 1 | TR1_63T_ALARME | 620 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1 | 63T - Desligamento | 21 |  |  | DI Val | 101 | 13 | 1 | TR1_63T_ATUADO | 621 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Reserva | 22 |  |  | - | - | - | - | Reserva | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Trip externo do 62BF do Disj.52-01 (BT) | 23 |  |  | - | - | - | - | (Somente p/Intertravamento!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | B138 | 86FD/AT (138 kV) - Abertura e Bloqueio Disj.52-17 | 24 |  |  | - | - | - | - | (Somente p/Intertravamento!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89--116 (S89C) - Libera Manobra | - | 13 |  | - | - | - | - | (Somente p/Intertravamento!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | ??? | - | 14 |  | - | - | - | - | (Somente p/Intertravamento!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 62BF - Atuado | - | 3 |  | Auto Fault | 160 | 85 | 2 | TR1AT_62BF_ATUADO | 622 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 50 ABC - Estágio 1 - Atuado | - | 4 |  | Auto Fault | 160 | 90 | 2 | TR1AT_50ABC_E1_ATUADO | 623 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 50 ABC - Estágio 2 - Atuado | - | 4 |  | Auto Fault | 160 | 91 | 2 | TR1AT_50ABC_E2_ATUADO | 624 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 50 N - Estágio 1 - Atuado | - | 4 |  | Auto Fault | 160 | 92 | 2 | TR1AT_50N_E1_ATUADO | 625 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 50 N - Estágio 2 - Atuado | - | 4 |  | Auto Fault | 160 | 93 | 2 | TR1AT_50N_E2_ATUADO | 626 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 50/51 Fase A - Atuado | - |  |  | Fault DI | 60 | 54 | 2 | TR1AT_50FA_51FA_ATUADO | 627 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 50/51 Fase B - Atuado | - |  |  | Fault DI | 60 | 55 | 2 | TR1AT_50FB_51FB_ATUADO | 628 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 50/51 Fase C - Atuado | - |  |  | Fault DI | 60 | 56 | 2 | TR1AT_50FC_51FC_ATUADO | 629 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 51 ABC - Atuado | - | 4 |  | Fault DI | 60 | 58 | 2 | TR1AT_51ABC_ATUADO | 630 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 51 N - Atuado | - | 4 |  | Fault DI | 60 | 66 | 2 | TR1AT_51N_ATUADO | 631 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Prot.67 - Bloqueada |  |  |  | DiVal | 63 | 11 | 1 | TR1AT_67_BLOQUEADA | 632 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Atuado 67 - Estágio 1 |  | 4 |  | Fault Di | 63 | 25 | 2 | TR1AT_67_E1_ATUADO | 633 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Atuado 67 - Estágio 2 |  | 4 |  | Fault Di | 63 | 72 | 2 | TR1AT_67_E2_ATUADO | 634 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Atuado 67 - TOC |  | 4 |  | Fault Di | 63 | 35 | 2 | TR1AT_67TOC_ATUADO | 635 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Atuado 67N - Estágio 1 |  | 4 |  | Fault Di | 63 | 43 | 2 | TR1AT_67N_E1_ATUADO | 636 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Atuado 67N - Estágio 2 |  | 4 |  | Fault Di | 63 | 64 | 2 | TR1AT_67N_E2_ATUADO | 637 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Atuado 67N - TOC |  | 4 |  | Fault Di | 63 | 46 | 2 | TR1AT_67N_TOC_ATUADO | 638 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Atuado 67 - Fase A |  |  |  | Fault Di | 63 | 75 | 2 | TR1AT_67_FA_ATUADO | 639 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Atuado 67 - Fase B |  |  |  | Fault Di | 63 | 76 | 2 | TR1AT_67_FB_ATUADO | 640 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Atuado 67 - Fase C |  |  |  | Fault Di | 63 | 77 | 2 | TR1AT_67_FC_ATUADO | 641 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Supervisão Medição: Falha Fusível TPs |  |  |  | DiVal | 135 | 149 | 1 | TR1AT_60FF_ALARME | 642 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Saúde Comunicação | - | [6 empty] | TR1AT_SAUDE_COMUNIC | 643 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## TR1DIF
SE GUAPORÉ - TR1 DIF
RELÉ xxF1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[22 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | 87 Trip Geral - Atuado |  |  |  | AF | 176 | 68 | 2 | TR1DIF_87_ATUADO | 650 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | 87 Fase A - Atuado |  |  |  | AF | 176 | 86 | 2 | TR1DIF_87_FA_ATUADO | 651 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | 87 Fase B - Atuado |  |  |  | AF | 176 | 87 | 2 | TR1DIF_87_FB_ATUADO | 652 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | 87 Fase C - Atuado |  |  |  | AF | 176 | 88 | 2 | TR1DIF_87_FC_ATUADO | 653 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | 87 - Excluído |  |  |  | DiVal | 75 | 15 | 1 | TR1DIF_87_EXCLUIDO | 654 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | 87 - Bloqueado |  |  |  | DiVal | 75 | 16 | 1 | TR1DIF_87_BLOQUEADO | 655 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | 62BF - Atuado |  |  |  | AF | 166 | 193 | 2 | TR1DIF_62BF_ATUADO | 656 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | Estado seccionadora 29-120 | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | TR1DIF_S329D_ABERTA | 657 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | Estado seccionadora 29-120 | 2 |  |  | DiSOEx2 | 240 | 160 | 1 | TR1DIF_S329D_FECHADA | 658 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | 20T - Atuado | 3 |  |  | DiVal | 101 | 10 | 1 | TR1DIF_20T_ATUADO | 659 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | Saúde Comunicação | [7 empty] | TR1DIF_SAUDE_COMUNIC | 660 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## TR1BT
SE GUAPORÉ - TR1 BT 69kV
RELÉ xxF1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
7SJ621 (End.: 16d/10h) | TR1BT | Tensão Fase B da Barra de 69 kV |  |  |  | AiVal | 134 | 137 | 9/6 | TR1BT_TENSAO_FB | 190 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Corrente Fase A |  |  |  | AiVal | 134 | 137 | 9/1 | TR1BT_CORRENTE_FA | 191 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Corrente Fase B |  |  |  | AiVal | 134 | 137 | 9/2 | TR1BT_CORRENTE_FB | 192 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Corrente Fase C |  |  |  | AiVal | 134 | 137 | 9/3 | TR1BT_CORRENTE_FC | 193 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Potência Ativa |  |  |  | AiVal | 134 | 137 | 9/11 | TR1BT_POT_ATIVA | 194 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Potência Reativa |  |  |  | AiVal | 134 | 137 | 9/12 | TR1BT_POT_REATIVA | 195 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Disj.52-01 - Abrir/Fechar |  | 1/2 |  | DiSOEx2 | 240 | 160 | 20 | TR1BT_COMANDOS_DJ | 155 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Disj. 52-01 – Aberto | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | TR1BT_DJ_ABERTO | 670 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Disj. 52-01 – Fechado | 2 |  |  | DiSOEx2 | 240 | 160 | 1 | TR1BT_DJ_FECHADO | 671 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Disj. 52-01 - Superv.Circuito TRIP - Alarme | 3 |  |  | DiVal | 240 | 190 | 1 | TR1BT_CIRC_TRIP_FALHADO | 672 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Disj. 52-01 - Mola Descarregada | 4 |  |  | DiVal | 240 | 191 | 1 | TR1BT_DJ_MOLA_DESC | 673 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Disj. 52-01 - BP SF6 (1o/2o.Estágio) - ALARME | 5 |  |  | DiVal | 240 | 192 | 1 | TR1BT_DJ_SF6_BLOQUEIO | 674 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Operação Indevida da Secc.29-120 (S329D) | 6 |  |  | DiVal | 240 | 193 | 1 | TR1BT_OPER_INDEV_SECC | 675 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | B69 | 86FD da 69kV ou 86T1 Atuado - Abertura e Bloqueio Disj.52-01 | 7 |  |  | - | - | - | - | (Somente p/Intertravamento!) | - | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Disj.52-01 – 43LR em posição LOCAL | 8 |  |  | DI Val | 240 | 195 | 1 | TR1BT_DJ_43LR_LOCAL | 676 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Disj.52-01 – 43TC Excluída | - |  |  | DI Val | 101 | 85 | 1 | TR1BT_43TC_EXCLUIDA | 677 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 62BF - Atuado |  | 3/4 |  | Auto Fault | 160 | 85 | 2 | TR1BT_62BF_ATUADO | 678 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 50 ABC - Estágio 1 - Atuado |  | 1 |  | AF | 160 | 90 | 2 | TR1BT_50ABC_E1_ATUADO | 679 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 50 ABC - Estágio 2 - Atuado |  | 1 |  | AF | 160 | 91 | 2 | TR1BT_50ABC_E2_ATUADO | 680 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 50 N - Estágio 1 - Atuado |  | 1 |  | AF | 160 | 92 | 2 | TR1BT_50N_E1_ATUADO | 681 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 50 N - Estágio 2 - Atuado |  | 1 |  | AF | 160 | 93 | 2 | TR1BT_50N_E2_ATUADO | 682 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 50/51 Fase A - Atuado |  |  |  | FDI | 60 | 54 | 2 | TR1BT_50FA_51FA_ATUADO | 683 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 50/51 Fase B - Atuado |  |  |  | FDI | 60 | 55 | 2 | TR1BT_50FB_51FB_ATUADO | 684 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 50/51 Fase C - Atuado |  |  |  | FDI | 60 | 56 | 2 | TR1BT_50FC_51FC_ATUADO | 685 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 51 ABC - Atuado |  | 1 |  | FDI | 60 | 58 | 2 | TR1BT_51ABC_ATUADO | 686 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 51 N - Atuado |  | 1 |  | FDI | 60 | 66 | 2 | TR1BT_51N_ATUADO | 687 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 60FF - falha Fusível |  |  |  | DI Val | 135 | 149 | 1 | TR1BT_60FF_ALARME | 688 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Saude Comunicação | [7 empty] | TR1BT_SAUDE_COMUNIC | 689 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## TR1AT-TM1
TREETECH |  | Descrição do ponto: | RELE |  |  | MODBUS | SLAVE |  |  | MASTER |  | LOCAL |  | COS |  | S6
EQUIPAMENTO | MÓDULO |  | FUNÇÃO MODBUS | REGISTRADOR | BIT | TIPO | VARIAVEIS | Identificação do ponto: | Lógica | Identificação do ponto: | DNP3 | SUL | RGE | SUL | RGE | NIVEL2
Medição
TREETECH TM (End: 02) | TR1 | Temperatura do óleo | 3 (Read Holding Reg) | 40020 |  | 16 Bits |  | TR1_TM11_TEMP_OLEO | IDF | TR1_TEMP_OLEO | 197
TREETECH TM (End: 02) | TR1AT | Temperatura do enrolamento 1 | 3 (Read Holding Reg) | 40021 |  | 16 Bits |  | TR1_TM11_TEMP_ENROL_AT | IDF | TR1_TEMP_ENROL_AT | 198
Sinalização
TREETECH TM (End: 02) | TR1 | Temp.Óleo - Alarme | 3 (Read Holding Reg) | 40024 | 0 |  |  | TR1_TM11_26T_ALARME | OR | TR1_26T_ALARME | 708
TREETECH TM (End: 02) | TR1 | Temp.Óleo - Desligamento | 3 (Read Holding Reg) | 40024 | 1 |  |  | TR1_TM11_26T_ATUADO | OR | TR1_26T_ATUADO | 709
TREETECH TM (End: 02) | TR1AT | Temp.Enrolamento AT- Alarme | 3 (Read Holding Reg) | 40024 | 4 |  |  | TR1_TM11_49_ALARME |  | TR1AT_49AT_ALARME | 710
TREETECH TM (End: 02) | TR1AT | Temp.Enrolamento AT- Desligamento | 3 (Read Holding Reg) | 40024 | 5 |  |  | TR1_TM11_49_ATUADO |  | TR1AT_49AT_ATUADO | 711
TREETECH TM (End: 02) | TR1 | SAÚDE COMUNICAÇÃO | [7 empty] | TR1_TM11_SAUDE_COMUNIC | 712

## TR1BT-TM2
TREETECH |  | Descrição do ponto: | RELE |  |  | MODBUS | SLAVE |  |  | MASTER |  | LOCAL |  | COS |  | S6
EQUIPAMENTO | MÓDULO |  | FUNÇÃO MODBUS | REGISTRADOR | BIT | TIPO | VARIAVEIS | Identificação do ponto: | Lógica | Identificação do ponto: | DNP3 | SUL | RGE | SUL | RGE | NIVEL2
Medição
TREETECH TM (End: 03) | TR1 | Temperatura do óleo | 3 (Read Holding Reg) | 40020 |  | 16 Bits |  | TR1_TM12_TEMP_OLEO | IDF | TR1_TEMP_OLEO | -
TREETECH TM (End: 03) | TR1BT | Temperatura do enrolamento 1 | 3 (Read Holding Reg) | 40021 |  | 16 Bits |  | TR1_TM12_TEMP_ENROL_BT |  | TR1_TEMP_ENROL_BT | 199
Sinalização
TREETECH TM (End: 03) | TR1 | Temp.Óleo - Alarme | 3 (Read Holding Reg) | 40024 | 0 |  |  | TR1_TM12_26T_ALARME | OR | TR1_26T_ALARME | -
TREETECH TM (End: 03) | TR1 | Temp.Óleo - Desligamento | 3 (Read Holding Reg) | 40024 | 1 |  |  | TR1_TM12_26T_ATUADO | OR | TR1_26T_ATUADO | -
TREETECH TM (End: 03) | TR1BT | Temp.Enrolamento AT- Alarme | 3 (Read Holding Reg) | 40024 | 4 |  |  | TR1_TM12_49_ALARME |  | TR1BT_49BT_ALARME | 713
TREETECH TM (End: 03) | TR1BT | Temp.Enrolamento AT- Desligamento | 3 (Read Holding Reg) | 40024 | 5 |  |  | TR1_TM12_49_ATUADO |  | TR1BT_49BT_ATUADO | 714
TREETECH TM (End: 03) | TR1 | SAÚDE COMUNICAÇÃO | [7 empty] | TR1_TM12_SAUDE_COMUNIC | 715

## LTPCH67
SE GUAPORÉ - LT PCH 138kV
RELÉ xxF1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
| Medição | [27 empty] | IDF | [6 empty] | CALC
7SJ64 (End.: 08) | LT PCH | Tensão fase B da LT |  |  |  | AI Val | 134 | 137 | 9/6 | LT67PCH_TENSAO_FB | 210 | LTPCH_TENSAO_FB | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Corrente fase A |  |  |  | AI Val | 134 | 137 | 9/1 | LT67PCH_CORRENTE_FA | 211 | LTPCH_CORRENTE_FA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Corrente fase B |  |  |  | AI Val | 134 | 137 | 9/2 | LT67PCH_CORRENTE_FB | 212 | LTPCH_CORRENTE_FB | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Corrente fase C |  |  |  | AI Val | 134 | 137 | 9/3 | LT67PCH_CORRENTE_FC | 213 | LTPCH_CORRENTE_FC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Potência Ativa |  |  |  | AI Val | 134 | 137 | 9/11 | LT67PCH_POT_ATIVA | 214 | LTPCH_POT_ATIVA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Potência Reativa |  |  |  | AI Val | 134 | 137 | 9/12 | LT67PCH_POT_REATIVA | 215 | LTPCH_POT_REATIVA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Defeito na Linha (km) |  |  |  | FPAI | 151 | 19 | 4 | LT67PCH_DIST_DEFEITO | 216 | LT67PCH_DIST_DEFEITO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Disjuntor 52-16 - Abrir/Fechar |  |  |  | Command | 240 | 160 | 20 | LT67PCH_COMANDOS_DJ | 170 | LTPCH_COMANDOS_DJ | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Secc.89-102 (D) - Abrir/Fechar |  |  |  | Command | 240 | 162 | 20 | LT67PCH_COMANDOS_S89D | 171 | LT67PCH_COMANDOS_S89D | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Secc.89-100 (E) - Abrir/Fechar |  |  |  | Command | 240 | 161 | 20 | LT67PCH_COMANDOS_S89E | 172 | LT67PCH_COMANDOS_S89E | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Secc.89-104 (C) - Abrir/Fechar |  |  |  | Command | 240 | 163 | 20 | LT67PCH_COMANDOS_S89C | 173 | LT67PCH_COMANDOS_S89C | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | 79 - Incluir/Excluir |  |  |  | Command | 240 | 169 | 20 | LT67PCH_COMANDOS_79 | 174 | LTPCH_COMANDOS_79 | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Troca Grupo de Ajuste |  |  |  | Command | 240 | 188 | 20 | LT67PCH_COMANDOS_GRUPO | 175 | LT67PCH_COMANDOS_GRUPO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Disjuntor 52-16 – Aberto | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | LT67PCH_DJ_ABERTO | 720 | LTPCH_DJ_ABERTO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Disjuntor 52-16 – Fechado | 2 |  |  | DiSOEx2 | 240 | 160 | 1 | LT67PCH_DJ_FECHADO | 721 | LTPCH_DJ_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Secc.89-100 (S89E) - Aberto | 8 |  |  | DiSOEx2 | 240 | 161 | 1 | LT67PCH_S89E_ABERTA | 722 | LTPCH_S89E_ABERTA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Secc.89-100 (S89E) - Fechado | 9 |  |  | DiSOEx2 | 240 | 161 | 1 | LT67PCH_S89E_FECHADO | 723 | LTPCH_S89E_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Secc.89-102 (S89D) - Aberto | 10 |  |  | DiSOEx2 | 240 | 162 | 1 | LT67PCH_S89D_ABERTA | 724 | LTPCH_S89D_ABERTA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Secc.89-102 (S89D) - Fechado | 11 |  |  | DiSOEx2 | 240 | 162 | 1 | LT67PCH_S89D_FECHADO | 725 | LTPCH_S89D_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Secc.89-104 (S89C) - Aberto | 12 |  |  | DiSOEx2 | 240 | 163 | 1 | LT67PCH_S89C_ABERTA | 726 | LTPCH_S89C_ABERTA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Secc.89-104 (S89C) - Fechado | 13 |  |  | DiSOEx2 | 240 | 163 | 1 | LT67PCH_S89C_FECHADO | 727 | LTPCH_S89C_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Seccion. 29-05 (S29T) - Aberto | 14 |  |  | DiSOEx2 | 240 | 165 | 1 | LT67PCH_S29T_ABERTA | 728 | LTPCH_S29T_ABERTA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Seccion. 29-05 (S29T) - Fechado | 15 |  |  | DiSOEx2 | 240 | 165 | 1 | LT67PCH_S29T_FECHADO | 729 | LTPCH_S29T_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | S89E - 43LR - Posição LOCAL | 6 |  |  | DiVal | 240 | 154 | 1 | LT67PCH_S89E_43LR_LOCAL | 730 | LT67PCH_S89E_43LR_LOCAL | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | S89D - 43LR - Posição LOCAL | 6 |  |  | DiVal | 240 | 158 | 1 | LT67PCH_S89D_43LR_LOCAL | 731 | LT67PCH_S89D_43LR_LOCAL | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | S89C- 43LR - Posição LOCAL | 6 |  |  | DiVal | 240 | 156 | 1 | LT67PCH_S89C_43LR_LOCAL | 732 | LT67PCH_S89C_43LR_LOCAL | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | S89E - Falta VCC/VCA - Alarme | 7 |  |  | DiVal | 240 | 159 | 1 | LT67PCH_S89E_F_CC_CA | 733 | LT67PCH_S89E_F_CC_CA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | S89D - Falta VCC/VCA - Alarme | 7 |  |  | DiVal | 240 | 157 | 1 | LT67PCH_S89D_F_CC_CA | 734 | LT67PCH_S89D_F_CC_CA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | S89C - Falta VCC/VCA - Alarme | 7 |  |  | DiVal | 240 | 155 | 1 | LT67PCH_S89C_F_CC_CA | 735 | LT67PCH_S89C_F_CC_CA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | DJ - Chave 43TC - Incluir/Excluir |  |  |  | DiVal | 101 | 85 | 1 | LT67PCH_43TC_EXCLUIDA | 736 | LTPCH_43TC_EXCLUIDA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | DJ - SF6 - Alarme | 3 |  |  | DiVal | 240 | 192 | 1 | LT67PCH_SF6_ALARME | 737 | LTPCH_SF6_ALARME | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | DJ - SF6 - Bloqueio | 4 |  |  | DiVal | 240 | 191 | 1 | LT67PCH_SF6_BLOQUEIO | 738 | LTPCH_SF6_BLOQUEIO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | DJ - Mola Descarregada | 5 |  |  | DiVal | 240 | 190 | 1 | LT67PCH_MOLA_DESC | 739 | LTPCH_MOLA_DESC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | DJ - 43LR - Posição LOCAL | 6 |  |  | DiVal | 240 | 193 | 1 | LT67PCH_43LR_POS_LOCAL | 740 | LTPCH_43LR_POS_LOCAL | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | DJ - Falta VCC/VCA de COM/MOTOR - Alarme | 7 |  |  | DiVal | 240 | 198 | 1 | LT67PCH_F_CC_COM_MOT | 741 | LTPCH_F_CC_COM_MOT | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Sinal Rele 24F02(F67) - Excluir 43TC | 16 |  |  | - | - | - | - | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Sinal Rele 24F02(F67) - Excluir 79 | 17 |  |  | - | - | - | - | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | B138 | 86FD/AT - Atuado | 18 |  |  | Di Val | 240 | 195 | 1 | B138_86FD_ATUADO | 742 | B138_86FD_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Operação Indevida de SECCIONADORAS | 19 |  |  | DiVal | 240 | 194 | 1 | LT67PCH_OP_INDEV_SECC | 743 | LTPCH_OP_INDEV_SECC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | DJ - Supervisão Circuito TRIP - Alarme | 20 |  |  | DiVal | 170 | 55 | 1 | LT67PCH_CIRC_TRIP_FALHADO | 744 | LTPCH_CIRC_TRIP_FALHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Grupo de Ajustes B - Ativado |  |  |  | DiVal | 160 | 24 | 1 | LT67PCH_GRUPOB_ATIVADO | 745 | LT67PCH_GRUPOB_ATIVADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | 79 - Excluído |  |  |  | DiVal | 40 | 81 | 1 | LT67PCH_79_EXCLUIDO | 746 | LTPCH_79_EXCLUIDO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | 79 - Disparo |  |  |  | AutoDi | 160 | 128 | 1 | LT67PCH_79_DISPARO | 747 | LT67PCH_79_DISPARO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | 79 - Religamento Sucedido |  |  |  | DiVal | 40 | 162 | 1 | LT67PCH_79_SUCEDIDO | 748 | LT67PCH_79_SUCEDIDO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | 79 - Bloqueado |  |  |  | Fault Di | 40 | 163 | 2 | LT67PCH_79_BLOQUEADO | 749 | LT67PCH_79_BLOQUEADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | 25 - Falha Operação Sincronismo |  |  |  | AutoDi | 41 | 35 | 1 | LT67PCH_25_FALHA_SINCRO | 750 | LTPCH_25_FALHA_SINCRO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuado 50 BF |  |  |  | Auto Fault | 160 | 85 | 2 | LT67PCH_50BF_ATUADO | 751 | LT67PCH_50BF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Supervisão Medição: Falha Fusível TPs (10s) |  |  |  | DiVal | 135 | 189 | 1 | LT67PCH_60FF_ALARME | 752 | LT67PCH_60FF_ALARME | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Prot.67 - Bloqueada |  |  |  | DiVal | 63 | 11 | 1 | LT67PCH_67_BLOQUEADA | 753 | LT67PCH_67_BLOQUEADA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuado 67-1 |  |  |  | Fault Di | 63 | 25 | 2 | LT67PCH_67_1_ATUADO | 754 | LT67PCH_67_1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuado 67-2 |  |  |  | Fault Di | 63 | 72 | 2 | LT67PCH_67_2_ATUADO | 755 | LT67PCH_67_2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuado 67 - TOC |  |  |  | Fault Di | 63 | 35 | 2 | LT67PCH_67TOC_ATUADO | 756 | LT67PCH_67TOC_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuado 67N-1 |  |  |  | Fault Di | 63 | 43 | 2 | LT67PCH_67N_1_ATUADO | 757 | LT67PCH_67N_1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuado 67N-2 |  |  |  | Fault Di | 63 | 64 | 2 | LT67PCH_67N_2_ATUADO | 758 | LT67PCH_67N_2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuado 67N - TOC |  |  |  | Fault Di | 63 | 46 | 2 | LT67PCH_67N_TOC_ATUADO | 759 | LT67PCH_67N_TOC_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuado 67 - Fase A |  |  |  | Fault Di | 63 | 75 | 2 | LT67PCH_67_FA_ATUADO | 760 | LT67PCH_67_FA_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuado 67 - Fase B |  |  |  | Fault Di | 63 | 76 | 2 | LT67PCH_67_FB_ATUADO | 761 | LT67PCH_67_FB_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuado 67 - Fase C |  |  |  | Fault Di | 63 | 77 | 2 | LT67PCH_67_FC_ATUADO | 762 | LT67PCH_67_FC_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Falta Tensão LT - Alarme |  |  |  | DiVal | 240 | 204 | 1 | LT67PCH_FALTA_TENSAO_LT | 763 | LTPCH_FALTA_TENSAO_LT | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Localiz.Defeito - Disparo |  |  |  | DiVal | 151 | 7 | 1 | LT67PCH_LDF_ATUADO | 764 | LT67PCH_LDF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuada Proteção Sub-Frequencia - E1 |  |  |  | Fdi | 70 | 234 | 2 | LT67PCH_81U_E1_ATUADO | 765 | LT67PCH_81U_E1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuada Proteção Sub-Frequencia - E2 |  |  |  | Fdi | 70 | 235 | 2 | LT67PCH_81U_E2_ATUADO | 766 | LT67PCH_81U_E2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuada Proteção Sobre-Frequencia - E1 |  |  |  | Fdi | 70 | 236 | 2 | LT67PCH_81O_E1_ATUADO | 767 | LT67PCH_81O_E1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuada Proteção Sobre-Frequencia - E2 |  |  |  | Fdi | 70 | 237 | 2 | LT67PCH_81O_E2_ATUADO | 768 | LT67PCH_81O_E2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuada Proteção 27 E1 |  |  |  | FDi | 74 | 81 | 2 | LT67PCH_27_E1_ATUADO | 769 | LT67PCH_27_E1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuada Proteção 27 E2 |  |  |  | FDi | 74 | 40 | 2 | LT67PCH_27_E2_ATUADO | 770 | LT67PCH_27_E2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuada Proteção 59 E1 |  |  |  | FDi | 74 | 83 | 2 | LT67PCH_59_E1_ATUADO | 771 | LT67PCH_59_E1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuada Proteção 59 E2 |  |  |  | FDi | 74 | 41 | 2 | LT67PCH_59_E2_ATUADO | 772 | LT67PCH_59_E2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Saúde Comunicação | [8 empty] | 773 | LT67PCH_SAUDE_COMUNIC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## LTPCH21
SE GUAPORÉ - LT PCH 138kV
RELÉ xxF1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
| Medição | [27 empty] | IDF | [6 empty] | CALC
7SA631 (End.: 07) | LT PCH | Tensão fase B da LT |  |  |  | AI Val | 134 | 124 | 9/5 | LT21PCH_TENSAO_FB | IDF | LTPCH_TENSAO_FB | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Corrente fase A |  |  |  | AI Val | 134 | 124 | 9/1 | LT21PCH_CORRENTE_FA | IDF | LTPCH_CORRENTE_FA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Corrente fase B |  |  |  | AI Val | 134 | 124 | 9/2 | LT21PCH_CORRENTE_FB | IDF | LTPCH_CORRENTE_FB | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Corrente fase C |  |  |  | AI Val | 134 | 124 | 9/3 | LT21PCH_CORRENTE_FC | IDF | LTPCH_CORRENTE_FC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Potência Ativa |  |  |  | AI Val | 134 | 124 | 9/7 | LT21PCH_POT_ATIVA | IDF | LTPCH_POT_ATIVA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Potência Reativa |  |  |  | AI Val | 134 | 124 | 9/8 | LT21PCH_POT_REATIVA | IDF | LTPCH_POT_REATIVA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Defeito na Linha (km) |  |  |  | FPAI | 151 | 19 | 4 | LT21PCH_DIST_DEFEITO | 217 | LT21PCH_DIST_DEFEITO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Disjuntor 52-16 - Abrir/Fechar |  |  |  | Command | 240 | 160 | 20 | LT21PCH_COMANDOS_DJ | IDF | LTPCH_COMANDOS_DJ | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | 79 - Incluir/Excluir |  |  |  | Command | 240 | 169 | 20 | LT21PCH_COMANDOS_79 | IDF | LTPCH_COMANDOS_79 | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Disjuntor 52-16 – Aberto | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | LT21PCH_DJ_ABERTO | IDF | LTPCH_DJ_ABERTO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Disjuntor 52-16 – Fechado | 2 |  |  | DiSOEx2 | 240 | 160 | 1 | LT21PCH_DJ_FECHADO | IDF | LTPCH_DJ_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Secc.89-100 (S89E) - Aberto | 8 |  |  | DiSOEx2 | 240 | 161 | 1 | LT21PCH_S89E_ABERTA | IDF | LTPCH_S89E_ABERTA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Secc.89-100 (S89E) - Fechado | 9 |  |  | DiSOEx2 | 240 | 161 | 1 | LT21PCH_S89E_FECHADO | IDF | LTPCH_S89E_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Secc.89-102 (S89D) - Aberto | 10 |  |  | DiSOEx2 | 240 | 162 | 1 | LT21PCH_S89D_ABERTA | IDF | LTPCH_S89D_ABERTA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Secc.89-102 (S89D) - Fechado | 11 |  |  | DiSOEx2 | 240 | 162 | 1 | LT21PCH_S89D_FECHADO | IDF | LTPCH_S89D_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Secc.89-104 (S89C) - Aberto | 12 |  |  | DiSOEx2 | 240 | 163 | 1 | LT21PCH_S89C_ABERTA | IDF | LTPCH_S89C_ABERTA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Secc.89-104 (S89C) - Fechado | 13 |  |  | DiSOEx2 | 240 | 163 | 1 | LT21PCH_S89C_FECHADO | IDF | LTPCH_S89C_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Seccion. 29-05 (S29T) - Aberto | 14 |  |  | DiSOEx2 | 240 | 165 | 1 | LT21PCH_S29T_ABERTA | IDF | LTPCH_S29T_ABERTA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Seccion. 29-05 (S29T) - Fechado | 15 |  |  | DiSOEx2 | 240 | 165 | 1 | LT21PCH_S29T_FECHADO | IDF | LTPCH_S29T_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | DJ - Chave 43TC - Incluir/Excluir |  |  |  | DiVal | 101 | 85 | 1 | LT21PCH_43TC_EXCLUIDA | OR | LTPCH_43TC_EXCLUIDA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | DJ - SF6 - Alarme | 3 |  |  | DiVal | 240 | 192 | 1 | LT21PCH_SF6_ALARME | IDF | LTPCH_SF6_ALARME | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | DJ - SF6 - Bloqueio | 4 |  |  | DiVal | 240 | 191 | 1 | LT21PCH_SF6_BLOQUEIO | IDF | LTPCH_SF6_BLOQUEIO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | DJ - Mola Descarregada | 5 |  |  | DiVal | 240 | 190 | 1 | LT21PCH_MOLA_DESC | IDF | LTPCH_MOLA_DESC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | DJ - 43LR - Posição LOCAL | 6 |  |  | DiVal | 240 | 193 | 1 | LT21PCH_43LR_POS_LOCAL | IDF | LTPCH_43LR_POS_LOCAL | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | DJ - Falta VCC de COM/MOTOR - Alarme | 7 |  |  | DiVal | 240 | 198 | 1 | LT21PCH_F_CC_COM_MOT | IDF | LTPCH_F_CC_COM_MOT | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Sinal Rele 24F02(F67) - Excluir 43TC | 16 |  |  | - | - | - | - | (Só para lógica interna de intertravamento!) |  | (Só para lógica interna de intertravamento!) | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Sinal Rele 24F02(F67) - Excluir 79 | 17 |  |  | - | - | - | - | (Só para lógica interna de intertravamento!) |  | (Só para lógica interna de intertravamento!) | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | B138 | 86FD/AT - Atuado | 18 |  |  | Di Val | 240 | 195 | 1 | B138_86FD_ATUADO | OR | B138_86FD_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Operação Indevida de SECCIONADORAS | 19 |  |  | DiVal | 240 | 194 | 1 | LT21PCH_OP_INDEV_SECC | OR | LTPCH_OP_INDEV_SECC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | DJ - Supervisão Circuito TRIP - Alarme | 20 |  |  | DiVal | 170 | 56 | 1 | LT21PCH_CIRC_TRIP_FALHADO | OR | LTPCH_CIRC_TRIP_FALHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | 79 - Excluído |  |  |  | DiVal | 40 | 81 | 1 | LT21PCH_79_EXCLUIDO | OR | LTPCH_79_EXCLUIDO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | 79 - Disparo |  |  |  | AutoDi | 160 | 128 | 1 | LT21PCH_79_DISPARO | 775 | LT21PCH_79_DISPARO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | 79 - Religamento Sucedido |  |  |  | AutoDi | 40 | 162 | 1 | LT21PCH_79_SUCEDIDO | 776 | LT21PCH_79_SUCEDIDO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | 79 - Bloqueado (Lockout) |  |  |  | FDI | 40 | 83 | 2 | LT21PCH_79_BLOQUEADO | 777 | LT21PCH_79_BLOQUEADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | 25 - Falha Operação Sincronismo |  |  |  | AutoDi | 41 | 35 | 1 | LT21PCH_25_FALHA_SINCRO | OR | LTPCH_25_FALHA_SINCRO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 50 BF |  |  |  | Auto Fault | 160 | 85 | 2 | LT21PCH_50BF_ATUADO | 778 | LT21PCH_50BF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Supervisão Medição: Falha Fusível TPs |  |  |  | DiVal | 135 | 149 | 1 | LT21PCH_60FF_ALARME | 779 | LT21PCH_60FF_ALARME | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Prot.21 - Bloqueada |  |  |  | DiVal | 28 | 52 | 1 | LT21PCH_21_BLOQUEADA | 780 | LT21PCH_21_BLOQUEADA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 21 Trip Fase A |  |  |  | Fault Di | 28 | 206 | 2 | LT21PCH_21FA_ATUADO | 781 | LT21PCH_21FA_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 21 Trip Fase B |  |  |  | Fault Di | 28 | 207 | 2 | LT21PCH_21FB_ATUADO | 782 | LT21PCH_21FB_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 21 Trip Fase C |  |  |  | Fault Di | 28 | 208 | 2 | LT21PCH_21FC_ATUADO | 783 | LT21PCH_21FC_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 21 N Trip |  |  |  | Fault Di | 28 | 212 | 2 | LT21PCH_21N_ATUADO | 784 | LT21PCH_21N_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 21 Trip3p.Z1sf |  |  |  | Auto Fault | 28 | 224 | 2 | LT21PCH_21Z1SF_ATUADO | 785 | LT21PCH_21Z1SF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 21 Trip3p.Z1mf |  |  |  | Auto Fault | 28 | 225 | 2 | LT21PCH_21Z1MF_ATUADO | 786 | LT21PCH_21Z1MF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 21 Trip3p.Z2 |  |  |  | Auto Fault | 28 | 217 | 2 | LT21PCH_21Z2_ATUADO | 787 | LT21PCH_21Z2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 21 Trip3p.Z3 |  |  |  | Auto Fault | 28 | 218 | 2 | LT21PCH_21Z3_ATUADO | 788 | LT21PCH_21Z3_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 21 Trip3p.Z4 |  |  |  | Auto Fault | 28 | 209 | 2 | LT21PCH_21Z4_ATUADO | 789 | LT21PCH_21Z4_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 21 Trip3p.Z5 |  |  |  | Auto Fault | 28 | 210 | 2 | LT21PCH_21Z5_ATUADO | 790 | LT21PCH_21Z5_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Falta Tensão LT - Alarme |  |  |  | DiVal | 240 | 204 | 1 | LT21PCH_FALTA_TENSAO_LT | OR | LTPCH_FALTA_TENSAO_LT | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Localiz.Defeito - Disparo |  |  |  | DiVal | 151 | 7 | 1 | LT21PCH_LDF_ATUADO | 791 | LT21PCH_LDF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuada Proteção Backup: 5XB TRIP |  |  |  | Auto Fault | 128 | 72 | 2 | LT21PCH_5XB_ATUADO | 792 | LT21PCH_5XB_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuada Proteção 50HS - Trip ABC (SOTF) |  |  |  | Auto Fault | 25 | 95 | 2 | LT21PCH_50HS_ABC_ATUADO | 793 | LT21PCH_50HS_ABC_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 67N TRIP |  |  |  | Auto Fault | 166 | 69 | 2 | LT21PCH_67N_ATUADO | 794 | LT21PCH_67N_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Saúde Comunicação | [8 empty] | 795 | LT21PCH_SAUDE_COMUNIC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## LTKNP67
SE GUAPORÉ - LT KNP 69kV
RELÉ xxF1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
| Medição | [27 empty] | IDF | [6 empty] | CALC
7SJ64 (End.: 12d/0Ch) | LT KNP | Tensão Barra A-B |  |  |  | AI Val | 134 | 137 | 9_6 | LT67KNP_TENSAO_AB | 220 | LTKNP_TENSAO_AB | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Corrente Fase A |  |  |  | AI Val | 134 | 137 | 9/1 | LT67KNP_CORRENTE_FA | 221 | LTKNP_CORRENTE_FA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Corrente Fase B |  |  |  | AI Val | 134 | 137 | 9/2 | LT67KNP_CORRENTE_FB | 222 | LTKNP_CORRENTE_FB | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Corrente Fase C |  |  |  | AI Val | 134 | 137 | 9/3 | LT67KNP_CORRENTE_FC | 223 | LTKNP_CORRENTE_FC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Potência Ativa |  |  |  | AI Val | 134 | 137 | 9_11 | LT67KNP_POT_ATIVA | 224 | LTKNP_POT_ATIVA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Potência Reativa |  |  |  | AI Val | 134 | 137 | 9_12 | LT67KNP_POT_REATIVA | 225 | LTKNP_POT_REATIVA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Defeito na Linha (km) |  |  |  | FPAI | 151 | 19 | 4 | LT67KNP_DIST_DEFEITO | 226 | LT67KNP_DIST_DEFEITO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Disjuntor 52-04 - Abrir/Fechar |  | 6/7 |  | Command | 240 | 160 | 20 | LT67KNP_COMANDOS_DJ | 180 | LTKNP_COMANDOS_DJ | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | 79 - Incluir/Excluir |  | 11 |  | Command | 240 | 169 | 20 | LT67KNP_COMANDOS_79 | 181 | LTKNP_COMANDOS_79 | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Dj.52-04 – Aberto | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | LT67KNP_DJ_ABERTO | 810 | LTKNP_DJ_ABERTO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Dj.52-04 – Fechado | 2 |  |  | DiSOEx2 | 240 | 160 | 1 | LT67KNP_DJ_FECHADO | 811 | LTKNP_DJ_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Seccion. 29-12 (329E) - Aberto | 8 |  |  | DiSOEx2 | 240 | 161 | 1 | LT67KNP_S329E_ABERTO | 812 | LTKNP_S329E_ABERTO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Seccion. 29-12 (329E) - Fechado | 9 |  |  | DiSOEx2 | 240 | 161 | 1 | LT67KNP_S329E_FECHADO | 813 | LTKNP_S329E_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Seccion. 29-10 (329D) - Aberto | 10 |  |  | DiSOEx2 | 240 | 162 | 1 | LT67KNP_S329D_ABERTO | 814 | LTKNP_S329D_ABERTO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Seccion. 29-10 (329D) - Fechado | 11 |  |  | DiSOEx2 | 240 | 162 | 1 | LT67KNP_S329D_FECHADO | 815 | LTKNP_S329D_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Seccion. 29-14 (329C) - Aberto | 12 |  |  | DiSOEx2 | 240 | 163 | 1 | LT67KNP_S329C_ABERTO | 816 | LTKNP_S329C_ABERTO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Seccion. 29-14 (329C) - Fechado | 13 |  |  | DiSOEx2 | 240 | 163 | 1 | LT67KNP_S329C_FECHADO | 817 | LTKNP_S329C_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Seccion. 29-01 (229T) - Aberto | 14 |  |  | DiSOEx2 | 240 | 165 | 1 | LT67KNP_S229T_ABERTO | 818 | LTKNP_S229T_ABERTO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Seccion. 29-01 (229T) - Fechado | 15 |  |  | DiSOEx2 | 240 | 165 | 1 | LT67KNP_S229T_FECHADO | 819 | LTKNP_S229T_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | DJ - SF6 - Alarme |  |  |  | DiVal | 240 | 191 | 1 | LT67KNP_DJ_SF6_ALARME | 820 | LTKNP_DJ_SF6_ALARME | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | DJ - SF6 - Bloqueio |  |  |  | DiVal | 240 | 192 | 1 | LT67KNP_DJ_SF6_BLOQUEIO | 821 | LTKNP_DJ_SF6_BLOQUEIO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | DJ - 43LR - Posição LOCAL | 3 |  |  | DiVal | 240 | 193 | 1 | LT67KNP_43LR_POS_LOCAL | 822 | LTKNP_43LR_POS_LOCAL | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | DJ - Mola Descarregada | 4 |  |  | DiVal | 240 | 190 | 1 | LT67KNP_MOLA_DESC | 823 | LTKNP_MOLA_DESC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | DJ - Falta VCC Motor | 5 |  |  | DiVal | 240 | 198 | 1 | LT67KNP_FVCC_MOTOR | 824 | LTKNP_FVCC_MOTOR | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | DJ - Supervisão Circuito TRIP - Alarme | 6 |  |  | DiVal | 170 | 55 | 1 | LT67KNP_CIRC_TRIP_FALHA | 825 | LTKNP_CIRC_TRIP_FALHA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Reserva | 7 |  |  | - | - | - | - | Reserva | - | Reserva | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Sinal Relé 02F1 (F21) - Excluir Telecomando COS | 16 |  |  | - | - | - | - | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Sinal Rele 02F1 (F21) - Excluir 79 | 17 |  |  | - | - | - | - | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | B69 | 86FD /AT - Atuado | 18 |  |  | DiVal | 240 | 195 | 1 | B69_86FD_ATUADO | 826 | B69_86FD_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Operação Indevida da Seccionadoras Isoladoras | 19 |  |  | DiVal | 240 | 194 | 1 | LT67KNP_OP_INDEV_SECC | 827 | LTKNP_OP_INDEV_SECC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Reserva | 20 - 33 |  |  | - | - | - | - | - | - | - | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | DJ - Chave 43TC Excluida |  |  |  | DiVal | 101 | 85 | 1 | LT67KNP_43TC_EXCLUIDA | 828 | LTKNP_43TC_EXCLUIDA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | 79 - Disparo |  |  |  | DiVal | 160 | 128 | 1 | LT67KNP_79_DISPARO | 829 | LT67KNP_79_DISPARO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | 79 - Excluído |  |  |  | DiVal | 40 | 81 | 1 | LT67KNP_79_EXCLUIDO | 830 | LTKNP_79_EXCLUIDO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | 79 - Religamento Sucedido |  |  |  | DiVal | 40 | 162 | 1 | LT67KNP_79_SUCEDIDO | 831 | LT67KNP_79_SUCEDIDO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | 79 - Bloqueado (Lockout) |  |  |  | FaltDi | 40 | 163 | 2 | LT67KNP_79_BLOQUEADO | 832 | LT67KNP_79_BLOQUEADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Reserva |  |  |  | - | - | - | - | Reserva | - | Reserva | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuado 50 BF |  |  |  | Auto Fault | 160 | 85 | 2 | LT67KNP_50BF_ATUADO | 833 | LT67KNP_50BF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Prot.67 - Bloqueada |  |  |  | DiVal | 63 | 11 | 1 | LT67KNP_67_BLOQUEADA | 834 | LT67KNP_67_BLOQUEADA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuado 67-1 |  |  |  | Fault Di | 63 | 25 | 2 | LT67KNP_67_1_ATUADO | 835 | LT67KNP_67_1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuado 67-2 |  |  |  | Fault Di | 63 | 72 | 2 | LT67KNP_67_2_ATUADO | 836 | LT67KNP_67_2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuado 67 - TOC |  |  |  | Fault Di | 63 | 35 | 2 | LT67KNP_67TOC_ATUADO | 837 | LT67KNP_67TOC_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuado 67N-1 |  |  |  | Fault Di | 63 | 43 | 2 | LT67KNP_67N_1_ATUADO | 838 | LT67KNP_67N_1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuado 67N-2 |  |  |  | Fault Di | 63 | 64 | 2 | LT67KNP_67N_2_ATUADO | 839 | LT67KNP_67N_2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuado 67N - TOC |  |  |  | Fault Di | 63 | 46 | 2 | LT67KNP_67N_TOC_ATUADO | 840 | LT67KNP_67N_TOC_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuado 67 - Fase A |  |  |  | Fault Di | 63 | 75 | 2 | LT67KNP_67_FA_ATUADO | 841 | LT67KNP_67_FA_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuado 67 - Fase B |  |  |  | Fault Di | 63 | 76 | 2 | LT67KNP_67_FB_ATUADO | 842 | LT67KNP_67_FB_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuado 67 - Fase C |  |  |  | Fault Di | 63 | 77 | 2 | LT67KNP_67_FC_ATUADO | 843 | LT67KNP_67_FC_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Supervisão Medição: Falha Fusível TPs |  |  |  | DiVal | 135 | 149 | 1 | LT67KNP_60FF_ALARME | 844 | LT67KNP_60FF_ALARME | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Localiz.Defeito - Disparo |  |  |  | DiVal | 151 | 7 | 1 | LT67KNP_LDF_ATUADO | 845 | LT67KNP_LDF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuada Proteção Sub-Frequencia - E1 |  |  |  | Fdi | 70 | 234 | 2 | LT67KNP_81U_E1_ATUADO | 846 | LT67KNP_81U_E1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuada Proteção Sub-Frequencia - E2 |  |  |  | Fdi | 70 | 235 | 2 | LT67KNP_81U_E2_ATUADO | 847 | LT67KNP_81U_E2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuada Proteção Sobre-Frequencia - E1 |  |  |  | Fdi | 70 | 236 | 2 | LT67KNP_81O_E1_ATUADO | 848 | LT67KNP_81O_E1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuada Proteção Sobre-Frequencia - E2 |  |  |  | Fdi | 70 | 237 | 2 | LT67KNP_81O_E2_ATUADO | 849 | LT67KNP_81O_E2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuada Proteção 27 |  |  |  | FDi | 74 | 81 | 2 | LT67KNP_27_ATUADO | 850 | LT67KNP_27_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuada Proteção 59 |  |  |  | FDi | 74 | 83 | 2 | LT67KNP_59_ATUADO | 851 | LT67KNP_59_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | 25 diferença de Tensão |  |  |  | DiVal | 254 | 130 | 1 | LT67KNP_25_V_DIFF | 852 | LTKNP_25_V_DIFF | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | 25 diferença de Frequência |  |  |  | DiVal | 254 | 129 | 1 | LT67KNP_25_HZ_DIFF | 853 | LTKNP_25_HZ_DIFF | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | 25 diferença de Ângulo |  |  |  | DiVal | 254 | 128 | 1 | LT67KNP_25_ANG_DIFF | 854 | LTKNP_25_ANG_DIFF | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | 25 Supervisiona 79 |  |  |  | DiVal | 254 | 127 | 1 | LT67KNP_25_SUP_79 | 855 | LT67KNP_25_SUP_79 | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Saúde Comunicação | [8 empty] | 856 | LT67KNP_SAUDE_COMUNIC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## LTKNP21
SE GUAPORÉ - LT KNP 69kV
RELÉ xxF1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
| Medição | [27 empty] | IDF | [6 empty] | CALC
7SA63 (End.: 11d/0Bh) | LT KNP | Tensão Barra A-B |  |  |  | AI Val | 134 | 124 | 9/5 | LT21KNP_TENSAO_FB | IDF | LTKNP_TENSAO_FB | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Corrente Fase A |  |  |  | AI Val | 134 | 124 | 9/1 | LT21KNP_CORRENTE_FA | IDF | LTKNP_CORRENTE_FA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Corrente Fase B |  |  |  | AI Val | 134 | 124 | 9/2 | LT21KNP_CORRENTE_FB | IDF | LTKNP_CORRENTE_FB | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Corrente Fase C |  |  |  | AI Val | 134 | 124 | 9/3 | LT21KNP_CORRENTE_FC | IDF | LTKNP_CORRENTE_FC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Potencia Ativa |  |  |  | AI Val | 134 | 124 | 9/7 | LT21KNP_POT_ATIVA | IDF | LTKNP_POT_ATIVA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Potencia Reativa |  |  |  | AI Val | 134 | 124 | 9/8 | LT21KNP_POT_REATIVA | IDF | LTKNP_POT_REATIVA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Defeito na Linha (km) |  |  |  | FPAI | 151 | 19 | 4 | LT21KNP_DIST_DEFEITO | 227 | LT21KNP_DIST_DEFEITO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Disjuntor 52-04 - Abrir/Fechar |  |  |  | Command | 240 | 160 | 20 | LT21KNP_COMANDOS_DJ | IDF | LTKNP_COMANDOS_DJ | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | 79 - Incluir/Excluir |  |  |  | Command | 240 | 169 | 20 | LT21KNP_COMANDOS_79 | IDF | LTKNP_COMANDOS_79 | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Dj.52-04 – Aberto | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | LT21KNP_DJ_ABERTO | IDF | LTKNP_DJ_ABERTO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Dj.52-04 – Fechado | 2 |  |  | DiSOEx2 | 240 | 160 | 1 | LT21KNP_DJ_FECHADO | IDF | LTKNP_DJ_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Seccion. 29-12 (329E) - Aberto | 8 |  |  | DiSOEx2 | 240 | 161 | 1 | LT21KNP_S89E_ABERTA | IDF | LTKNP_S89E_ABERTA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Seccion. 29-12 (329E) - Fechado | 9 |  |  | DiSOEx2 | 240 | 161 | 1 | LT21KNP_S89E_FECHADO | IDF | LTKNP_S89E_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Seccion. 29-10 (329D) - Aberto | 10 |  |  | DiSOEx2 | 240 | 162 | 1 | LT21KNP_S89D_ABERTA | IDF | LTKNP_S89D_ABERTA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Seccion. 29-10 (329D) - Fechado | 11 |  |  | DiSOEx2 | 240 | 162 | 1 | LT21KNP_S89D_FECHADO | IDF | LTKNP_S89D_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Seccion. 29-14 (329C) - Aberto | 12 |  |  | DiSOEx2 | 240 | 163 | 1 | LT21KNP_S89C_ABERTA | IDF | LTKNP_S89C_ABERTA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Seccion. 29-14 (329C) - Fechado | 13 |  |  | DiSOEx2 | 240 | 163 | 1 | LT21KNP_S89C_FECHADO | IDF | LTKNP_S89C_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Seccion. 29-01 (229T) - Aberto | 14 |  |  | DiSOEx2 | 240 | 165 | 1 | LT21KNP_S29T_ABERTA | IDF | LTKNP_S29T_ABERTA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Seccion. 29-01 (229T) - Fechado | 15 |  |  | DiSOEx2 | 240 | 165 | 1 | LT21KNP_S29T_FECHADO | IDF | LTKNP_S29T_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | DJ - SF6 - Alarme |  |  |  | DiVal | 240 | 191 | 1 | LT21KNP_DJ_SF6_ALARME | IDF | LTKNP_DJ_SF6_ALARME | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | DJ - SF6 - Bloqueio |  |  |  | DiVal | 240 | 190 | 1 | LT21KNP_DJ_SF6_BLOQUEIO | IDF | LTKNP_DJ_SF6_BLOQUEIO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | DJ - 43LR - Posição LOCAL | 3 |  |  | DiVal | 240 | 193 | 1 | LT21KNP_43LR_POS_LOCAL | IDF | LTKNP_43LR_POS_LOCAL | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | DJ - Mola Descarregada | 4 |  |  | DiVal | 240 | 192 | 1 | LT21KNP_MOLA_DESC | IDF | LTKNP_MOLA_DESC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | DJ - Falta VCC Motor | 5 |  |  | DiVal | 240 | 198 | 1 | LT21KNP_FVCC_MOTOR | IDF | LTKNP_FVCC_MOTOR | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | DJ - Supervisão Circuito TRIP - Alarme | 6 |  |  | DiVal | 170 | 55 | 1 | LT21KNP_CIRC_TRIP_FALHADO | OR | LTKNP_CIRC_TRIP_FALHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Reserva | 7 |  |  | - | - | - | - | Reserva | - | Reserva | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Sinal Relé 25F2 (F67) - Excluir Telecomando COS | 16 |  |  | - | - | - | - | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Sinal Rele 25F2(F67) - Excluir 79 | 17 |  |  | - | - | - | - | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | B69 | 86FD /AT - Atuado | 18 |  |  | DiVal | 240 | 195 | 1 | B69_86FD_ATUADO | OR | B69_86FD_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Operação Indevida da Seccionadoras Isoladoras | 19 |  |  | DiVal | 240 | 196 | 1 | LT21KNP_OP_INDEV_SECC | OR | LTKNP_OP_INDEV_SECC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Reserva | 20 |  |  | - | - | - | - | Reserva | - | Reserva | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | DJ - Chave 43TC Excluida |  | 10 |  | DiVal | 101 | 85 | 1 | LT21KNP_43TC_EXCLUIDA | OR | LTKNP_43TC_EXCLUIDA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | 79 - Disparo |  |  |  | AutoDi | 160 | 128 | 1 | LT21KNP_79_DISPARO | 860 | LT21KNP_79_DISPARO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | 79 - Excluído |  |  |  | DiVal | 40 | 81 | 1 | LT21KNP_79_EXCLUIDO | OR | LTKNP_79_EXCLUIDO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | 79 - Religamento Sucedido |  |  |  | AutoDi | 40 | 162 | 1 | LT21KNP_79_SUCEDIDO | 861 | LT21KNP_79_SUCEDIDO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | 79 - Definitive TRIP (Lockout) |  |  |  | Fault Di | 150 | 180 | 2 | LT21KNP_79_BLOQUEADO | 862 | LT21KNP_79_BLOQUEADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Reserva |  |  |  | - | - | - | - | Reserva | - | Reserva | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 50 BF |  | 4 |  | Auto Fault | 160 | 85 | 2 | LT21KNP_50BF_ATUADO | 863 | LT21KNP_50BF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Prot.21 - Bloqueada |  |  |  | DiVal | 28 | 52 | 1 | LT21KNP_21_BLOQUEADA | 864 | LT21KNP_21_BLOQUEADA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 21 Trip Fase A |  | 6 |  | Fault Di | 28 | 206 | 2 | LT21KNP_21FA_ATUADO | 865 | LT21KNP_21FA_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 21 Trip Fase B |  | 6 |  | Fault Di | 28 | 207 | 2 | LT21KNP_21FB_ATUADO | 866 | LT21KNP_21FB_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 21 Trip Fase C |  | 6 |  | Fault Di | 28 | 208 | 2 | LT21KNP_21FC_ATUADO | 867 | LT21KNP_21FC_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 21 N Trip |  | 6 |  | Fault Di | 28 | 212 | 2 | LT21KNP_21N_ATUADO | 868 | LT21KNP_21N_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 21 Trip3p.Z1sf |  | 6 |  | Auto Fault | 28 | 224 | 2 | LT21KNP_21Z1SF_ATUADO | 869 | LT21KNP_21Z1SF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 21 Trip3p.Z1mf |  | 6 |  | Auto Fault | 28 | 225 | 2 | LT21KNP_21Z1MF_ATUADO | 870 | LT21KNP_21Z1MF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 21 Trip3p.Z2 |  | 6 |  | Auto Fault | 28 | 217 | 2 | LT21KNP_21Z2_ATUADO | 871 | LT21KNP_21Z2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 21 Trip3p.Z3 |  | 6 |  | Auto Fault | 28 | 218 | 2 | LT21KNP_21Z3_ATUADO | 872 | LT21KNP_21Z3_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 21 Trip3p.Z4 |  | 6 |  | Auto Fault | 28 | 209 | 2 | LT21KNP_21Z4_ATUADO | 873 | LT21KNP_21Z4_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Ligar DJ Sobre Falha |  |  |  | Auto Fault | 25 | 95 | 2 | LT21KNP_50HS_ATUADO | 874 | LT21KNP_50HS_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 67N TRIP |  | 6 |  | Auto Fault | 166 | 69 | 2 | LT21KNP_67N_ATUADO | 875 | LT21KNP_67N_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuada Proteção Backup: 5XB TRIP |  | 6 |  | Auto Fault | 128 | 72 | 2 | LT21KNP_5XB_ATUADO | 876 | LT21KNP_5XB_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Supervisão Medição: Falha Fusível TPs |  |  |  | DiVal | 135 | 149 | 1 | LT21KNP_60FF_ALARME | 877 | LT21KNP_60FF_ALARME | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Localiz.Defeito - Disparo |  |  |  | DiVal | 151 | 7 | 1 | LT21KNP_LDF_ATUADO | 878 | LT21KNP_LDF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | 25 diferença de Tensão |  |  |  | DiVal | 254 | 130 | 1 | LT21KNP_25_V_DIFF | OR | LTKNP_25_V_DIFF | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | 25 diferença de Frequência |  |  |  | DiVal | 254 | 129 | 1 | LT21KNP_25_HZ_DIFF | OR | LTKNP_25_HZ_DIFF | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | 25 diferença de Ângulo |  |  |  | DiVal | 254 | 128 | 1 | LT21KNP_25_ANG_DIFF | OR | LTKNP_25_ANG_DIFF | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Saúde Comunicação |  |  |  | - | - | - | - |  | 879 | LT21KNP_SAUDE_COMUNIC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## LTCAS67
SE GUAPORÉ - LT CAS 138kV
RELÉ xxF1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
| Medição | [27 empty] | IDF | [6 empty] | CALC
7SJ64 (End.: 10/0Ah) | LT CAS | Tensão Barra A-B |  |  |  | AI Val | 134 | 137 | 9/6 | LT67CAS_TENSAO_FB | 230 | LTCAS_TENSAO_FB | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Corrente Fase A |  |  |  | AI Val | 134 | 137 | 9/1 | LT67CAS_CORRENTE_FA | 231 | LTCAS_CORRENTE_FA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Corrente Fase B |  |  |  | AI Val | 134 | 137 | 9/2 | LT67CAS_CORRENTE_FB | 232 | LTCAS_CORRENTE_FB | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Corrente Fase C |  |  |  | AI Val | 134 | 137 | 9/3 | LT67CAS_CORRENTE_FC | 233 | LTCAS_CORRENTE_FC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Potência Ativa |  |  |  | AI Val | 134 | 137 | 9/11 | LT67CAS_POT_ATIVA | 234 | LTCAS_POT_ATIVA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Potência Reativa |  |  |  | AI Val | 134 | 137 | 9/12 | LT67CAS_POT_REATIVA | 235 | LTCAS_POT_REATIVA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Defeito na Linha (km) |  |  |  | FPAI | 151 | 19 | 4 | LT67CAS_DIST_DEFEITO | 236 | LT67CAS_DIST_DEFEITO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Disjuntor 52-18 - Abrir/Fechar |  |  |  | Command | 240 | 160 | 20 | LT67CAS_COMANDOS_DJ | 185 | LTCAS_COMANDOS_DJ | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Seccion. 89-108 (289E) - Abrir/Fechar |  |  |  | Command | 240 | 161 | 20 | LT67CAS_COMANDOS_S89D | 186 | LT67CAS_COMANDOS_S89D | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Seccion. 89-106 (289D) - Abrir/Fechar |  |  |  | Command | 240 | 162 | 20 | LT67CAS_COMANDOS_S89E | 187 | LT67CAS_COMANDOS_S89E | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Seccion. 89-110 (289C) - Abrir/Fechar |  |  |  | Command | 240 | 163 | 20 | LT67CAS_COMANDOS_S89C | 188 | LT67CAS_COMANDOS_S89C | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | 79 - Incluir/Excluir |  |  |  | Command | 240 | 169 | 20 | LT67CAS_COMANDOS_79 | 189 | LTCAS_COMANDOS_79 | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Disjuntor 52-18 – Aberto | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | LT67CAS_DJ_ABERTO | 890 | LTCAS_DJ_ABERTO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Disjuntor 52-18 – Fechado | 2 |  |  | DiSOEx2 | 240 | 160 | 1 | LT67CAS_DJ_FECHADO | 891 | LTCAS_DJ_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.89-108 (S89E) - Aberto | 8 |  |  | DiSOEx2 | 240 | 161 | 1 | LT67CAS_S329E_ABERTO | 892 | LTCAS_S329E_ABERTO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.89-108 (S89E) - Fechado | 9 |  |  | DiSOEx2 | 240 | 161 | 1 | LT67CAS_S329E_FECHADO | 893 | LTCAS_S329E_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.89-106 (S89D) - Aberto | 10 |  |  | DiSOEx2 | 240 | 162 | 1 | LT67CAS_S329D_ABERTO | 894 | LTCAS_S329D_ABERTO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.89-106 (S89D) - Fechado | 11 |  |  | DiSOEx2 | 240 | 162 | 1 | LT67CAS_S329D_FECHADO | 895 | LTCAS_S329D_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.89-110 (S89C) - Aberto | 12 |  |  | DiSOEx2 | 240 | 163 | 1 | LT67CAS_S329C_ABERTO | 896 | LTCAS_S329C_ABERTO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.89-110 (S89C) - Fechado | 13 |  |  | DiSOEx2 | 240 | 163 | 1 | LT67CAS_S329C_FECHADO | 897 | LTCAS_S329C_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc. 29-03 (S29T) - Aberto | 14 |  |  | DiSOEx2 | 240 | 165 | 1 | LT67CAS_S229T_ABERTO | 898 | LTCAS_S229T_ABERTO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc. 29-03 (S29T) - Fechado | 15 |  |  | DiSOEx2 | 240 | 165 | 1 | LT67CAS_S229T_FECHADO | 899 | LTCAS_S229T_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | DJ - SF6 Alarme | 3 |  |  | DiVal | 240 | 192 | 1 | LT67CAS_SF6_ALARME | 900 | LTCAS_SF6_ALARME | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | DJ - SF6 Abertura e Bloqueio | 4 |  |  | DiVal | 240 | 191 | 1 | LT67CAS_SF6_BLOQUEIO | 901 | LTCAS_SF6_BLOQUEIO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | DJ - Mola Descarregada | 5 |  |  | DiVal | 240 | 190 | 1 | LT67CAS_MOLA_DESC | 902 | LTCAS_MOLA_DESC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | DJ - 43LR - Posição LOCAL | 6 |  |  | DiVal | 240 | 193 | 1 | LT67CAS_43LR_POS_LOCAL | 903 | LTCAS_43LR_POS_LOCAL | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | DJ - Falta VCC CMD/VCA AQUEC | 7 |  |  | DiVal | 240 | 198 | 1 | LT67CAS_FALTA_VCA_VCC | 904 | LTCAS_FALTA_VCA_VCC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Sinal Relé (F21) - Excluir Telecomando COS | 16 |  |  | - | - | - | - | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Sinal Rele (F21) - Excluir 79 | 17 |  |  | - | - | - | - | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | B138 | 86FD /AT - Atuado | 18 |  |  | DiVal | 240 | 195 | 1 | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | DJ - Supervisão Circuito TRIP - Alarme | 20 |  |  | DiVal | 170 | 55 | 1 | LT67CAS_CIRC_TRIP_FALHA | 906 | LTCAS_CIRC_TRIP_FALHA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.(89-108) - 43LR - Posição LOCAL | 21 |  |  | DiVal | 240 | 196 | 1 | LT67CAS_S289E_43LR | 907 | LT67CAS_S289E_43LR | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.(89-108)-VCC CMD/MOTOR | 22 |  |  | DiVal | 240 | 197 | 1 | LT67CAS_S289E_DEF_INTERN | 908 | LT67CAS_S289E_DEF_INTERN | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.(89-106) - 43LR - Posição LOCAL | 23 |  |  | DiVal | 240 | 199 | 1 | LT67CAS_S289D_43LR | 909 | LT67CAS_S289D_43LR | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.(89-106)-VCC CMD/MOTOR | 24 |  |  | DiVal | 240 | 200 | 1 | LT67CAS_S289D_DEF_INTERN | 910 | LT67CAS_S289D_DEF_INTERN | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.(89-110) - 43LR - Posição LOCAL | 25 |  |  | DiVal | 240 | 201 | 1 | LT67CAS_S289C_43LR | 911 | LT67CAS_S289C_43LR | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.(89-110)-VCC CMD/MOTOR | 26 |  |  | DiVal | 240 | 202 | 1 | LT67CAS_S289C_DEF_INTERN | 912 | LT67CAS_S289C_DEF_INTERN | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Operação Indevida das Secc.Isoladoras | 33 |  |  | DiVal | 240 | 194 | 1 | LT67CAS_OPER_INDEV_SECC | 913 | LTCAS_OPER_INDEV_SECC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | TRIP LT PCH Autodromo |  |  |  | DiVal | 240 | 203 | 1 | LT67CAS_TRIP_LT_AUTODROMO | 914 | LT67CAS_TRIP_LT_AUTODROMO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | DJ - Chave 43TC Excluida |  |  |  | DiVal | 101 | 85 | 1 | LT67CAS_43TC_EXCLUIDA | 915 | LTCAS_43TC_EXCLUIDA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | 79 supervisionado pelo 25 |  |  |  | DiVal | 160 | 129 | 1 | LT67CAS_25_SUPERV_79 | 916 | LT67CAS_25_SUPERV_79 | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | 79 - Excluído |  |  |  | DiVal | 40 | 81 | 1 | LT67CAS_79_EXCLUIDO | 917 | LTCAS_79_EXCLUIDO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | 79 - Religamento Sucedido |  |  |  | DiVal | 40 | 162 | 1 | LT67CAS_79_SUCEDIDO | 918 | LT67CAS_79_SUCEDIDO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | 79 - Bloqueado (Lockout) |  |  |  | FaltDi | 40 | 163 | 2 | LT67CAS_79_BLOQUEADO | 919 | LT67CAS_79_BLOQUEADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | 25 - Falha Operação Sincronismo |  |  |  | AutoDi | 41 | 35 | 1 | LT67CAS_25_FALHA_SINCRO | 920 | LTCAS_25_FALHA_SINCRO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuado 50 BF |  |  |  | Auto Fault | 160 | 85 | 2 | LT67CAS_50BF_ATUADO | 921 | LT67CAS_50BF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Prot.67 - Bloqueada |  |  |  | DiVal | 63 | 11 | 1 | LT67CAS_67_BLOQUEADA | 922 | LT67CAS_67_BLOQUEADA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuado 67-1 |  |  |  | Fault Di | 63 | 25 | 2 | LT67CAS_67_1_ATUADO | 923 | LT67CAS_67_1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuado 67-2 |  |  |  | Fault Di | 63 | 72 | 2 | LT67CAS_67_2_ATUADO | 924 | LT67CAS_67_2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuado 67 - TOC |  |  |  | Fault Di | 63 | 35 | 2 | LT67CAS_67TOC_ATUADO | 925 | LT67CAS_67TOC_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuado 67N-1 |  |  |  | Fault Di | 63 | 43 | 2 | LT67CAS_67N_1_ATUADO | 926 | LT67CAS_67N_1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuado 67N-2 |  |  |  | Fault Di | 63 | 64 | 2 | LT67CAS_67N_2_ATUADO | 927 | LT67CAS_67N_2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuado 67N - TOC |  |  |  | Fault Di | 63 | 46 | 2 | LT67CAS_67N_TOC_ATUADO | 928 | LT67CAS_67N_TOC_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuado 67 - Fase A |  |  |  | Fault Di | 63 | 75 | 2 | LT67CAS_67_FA_ATUADO | 929 | LT67CAS_67_FA_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuado 67 - Fase B |  |  |  | Fault Di | 63 | 76 | 2 | LT67CAS_67_FB_ATUADO | 930 | LT67CAS_67_FB_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuado 67 - Fase C |  |  |  | Fault Di | 63 | 77 | 2 | LT67CAS_67_FC_ATUADO | 931 | LT67CAS_67_FC_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Supervisão Medição: Falha Fusível TPs |  |  |  | DiVal | 135 | 149 | 1 | LT67CAS_60FF_ALARME | 932 | LT67CAS_60FF_ALARME | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Falta Tensão LT - Alarme |  |  |  | DiVal | 240 | 204 | 1 | LT67CAS_FALTA_TENSAO_LT | 933 | LTCAS_FALTA_TENSAO_LT | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Localiz.Defeito - Disparo |  |  |  | DiVal | 151 | 7 | 1 | LT67CAS_LDF_ATUADO | 934 | LT67CAS_LDF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuada Proteção Sub-Frequencia - E1 |  |  |  | Fdi | 70 | 234 | 2 | LT67CAS_81U_E1_ATUADO | 935 | LT67CAS_81U_E1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuada Proteção Sub-Frequencia - E2 |  |  |  | Fdi | 70 | 235 | 2 | LT67CAS_81U_E2_ATUADO | 936 | LT67CAS_81U_E2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuada Proteção Sobre-Frequencia - E1 |  |  |  | Fdi | 70 | 236 | 2 | LT67CAS_81O_E1_ATUADO | 937 | LT67CAS_81O_E1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuada Proteção Sobre-Frequencia - E2 |  |  |  | Fdi | 70 | 237 | 2 | LT67CAS_81O_E2_ATUADO | 938 | LT67CAS_81O_E2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuada Proteção 27 |  |  |  | FDi | 74 | 81 | 2 | LT67CAS_27_ATUADO | 939 | LT67CAS_27_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuada Proteção 59 |  |  |  | FDi | 74 | 83 | 2 | LT67CAS_59_ATUADO | 940 | LT67CAS_59_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Saúde Comunicação | [8 empty] | 941 | LT67CAS_SAUDE_COMUNIC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## LTCAS21
SE GUAPORÉ - LT CAS 138kV
RELÉ xxF1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
| Medição | [27 empty] | IDF | [6 empty] | CALC
7SA63 (End.: 9) | LT CAS | Tensão Barra A-B |  |  |  | AI Val | 134 | 124 | 9_5 | LT21CAS_TENSAO_AB | IDF | LTCAS_TENSAO_AB | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Corrente Fase A |  |  |  | AI Val | 134 | 124 | 9/1 | LT21CAS_CORRENTE_FA | IDF | LTCAS_CORRENTE_FA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Corrente Fase B |  |  |  | AI Val | 134 | 124 | 9/2 | LT21CAS_CORRENTE_FB | IDF | LTCAS_CORRENTE_FB | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Corrente Fase C |  |  |  | AI Val | 134 | 124 | 9/3 | LT21CAS_CORRENTE_FC | IDF | LTCAS_CORRENTE_FC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Potencia Ativa |  |  |  | AI Val | 134 | 124 | 9/7 | LT21CAS_POT_ATIVA | IDF | LTCAS_POT_ATIVA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Potencia Reativa |  |  |  | AI Val | 134 | 124 | 9/8 | LT21CAS_POT_REATIVA | IDF | LTCAS_POT_REATIVA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Defeito na Linha (km) |  |  |  | FPAI | 151 | 19 | 4 | LT21CAS_DIST_DEFEITO | 237 | LT21CAS_DIST_DEFEITO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Disjuntor 52-18 - Abrir/Fechar |  |  |  | Command | 240 | 160 | 20 | LT21CAS_COMANDOS_DJ | IDF | LTCAS_COMANDOS_DJ | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | 79 - Incluir/Excluir |  |  |  | Command | 240 | 169 | 20 | LT21CAS_COMANDOS_79 | IDF | LTCAS_COMANDOS_79 | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Disjuntor 52-18 – Aberto | 1 |  |  | DiSOEx2 | 240 | 160 | 1 | LT21CAS_DJ_ABERTO | IDF | LTCAS_DJ_ABERTO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Disjuntor 52-18 – Fechado | 2 |  |  | DiSOEx2 | 240 | 160 | 1 | LT21CAS_DJ_FECHADO | IDF | LTCAS_DJ_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Secc.89-108 (S89E) - Aberto | 8 |  |  | DiSOEx2 | 240 | 161 | 1 | LT21CAS_S329E_ABERTO | IDF | LTCAS_S329E_ABERTO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Secc.89-108 (S89E) - Fechado | 9 |  |  | DiSOEx2 | 240 | 161 | 1 | LT21CAS_S329E_FECHADO | IDF | LTCAS_S329E_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Secc.89-106 (S89D) - Aberto | 10 |  |  | DiSOEx2 | 240 | 162 | 1 | LT21CAS_S329D_ABERTO | IDF | LTCAS_S329D_ABERTO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Secc.89-106 (S89D) - Fechado | 11 |  |  | DiSOEx2 | 240 | 162 | 1 | LT21CAS_S329D_FECHADO | IDF | LTCAS_S329D_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Secc.89-110 (S89C) - Aberto | 12 |  |  | DiSOEx2 | 240 | 163 | 1 | LT21CAS_S329C_ABERTO | IDF | LTCAS_S329C_ABERTO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Secc.89-110 (S89C) - Fechado | 13 |  |  | DiSOEx2 | 240 | 163 | 1 | LT21CAS_S329C_FECHADO | IDF | LTCAS_S329C_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Secc. 29-03 (S29T) - Aberto | 14 |  |  | DiSOEx2 | 240 | 165 | 1 | LT21CAS_S229T_ABERTO | IDF | LTCAS_S229T_ABERTO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Secc. 29-03 (S29T) - Fechado | 15 |  |  | DiSOEx2 | 240 | 165 | 1 | LT21CAS_S229T_FECHADO | IDF | LTCAS_S229T_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | DJ - SF6 Alarme | 3 |  |  | DiVal | 240 | 190 | 1 | LT21CAS_SF6_ALARME | IDF | LTCAS_SF6_ALARME | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | DJ - SF6 Abertura e Bloqueio | 4 |  |  | DiVal | 240 | 191 | 1 | LT21CAS_SF6_BLOQUEIO | IDF | LTCAS_SF6_BLOQUEIO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | DJ - Mola Descarregada/Falta VCC Motor | 5 |  |  | DiVal | 240 | 192 | 1 | LT21CAS_MOLA_DESC | IDF | LTCAS_MOLA_DESC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | DJ - 43LR - Posição LOCAL | 6 |  |  | DiVal | 240 | 193 | 1 | LT21CAS_43LR_POS_LOCAL | IDF | LTCAS_43LR_POS_LOCAL | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Falta VCC CMD/VCA AQUEC | 7 |  |  | DiVal | 240 | 194 | 1 | LT21CAS_FALTA_VCA_VCC | IDF | LTCAS_FALTA_VCA_VCC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Sinal Relé (F67) - Excluir Telecomando COS | 16 |  |  | - | - | - | - | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Sinal Rele (F67) - Excluir 79 | 17 |  |  | - | - | - | - | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | B138 | 86FD /AT - Atuado | 18 |  |  | DiVal | 240 | 195 | 1 | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Operação Indevida da Seccs | 19 |  |  | DiVal | 240 | 196 | 1 | LT21CAS_OP_INDEV_SECC | OR | LTCAS_OP_INDEV_SECC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | DJ - Supervisão Circuito TRIP - Alarme | 20 |  |  | DiVal | 170 | 55 | 1 | LT21CAS_CIRC_TRIP_FALHADO | OR | LTCAS_CIRC_TRIP_FALHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | TRIP LT PCH Autodromo |  |  |  | DiVal | 240 | 203 | 1 | LT21CAS_TRIP_LT_AUTODROMO | 945 | LT21CAS_TRIP_LT_AUTODROMO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | DJ - Chave 43TC Excluida |  |  |  | DiVal | 101 | 85 | 1 | LT21CAS_43TC_EXCLUIDA | OR | LTCAS_43TC_EXCLUIDA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | 79 - Disparo |  |  |  | AutoDi | 160 | 128 | 1 | LT21CAS_79_DISPARO | 946 | LT21CAS_79_DISPARO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | 79 - Excluído |  |  |  | DiVal | 40 | 81 | 1 | LT21CAS_79_EXCLUIDO | OR | LTCAS_79_EXCLUIDO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | 79 - Religamento Sucedido |  |  |  | AutoDi | 40 | 162 | 1 | LT21CAS_79_SUCEDIDO | 947 | LT21CAS_79_SUCEDIDO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | 79 - Definiteve TRIP (Lockout) |  |  |  | Fault Di | 150 | 180 | 2 | LT21CAS_79_BLOQUEADO | 948 | LT21CAS_79_BLOQUEADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | 25 - Falha Operação Sincronismo |  |  |  | AutoDi | 41 | 83 | 1 | LT21CAS_25_FALHA_SINCRO | OR | LTCAS_25_FALHA_SINCRO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 50 BF |  |  |  | Auto Fault | 160 | 85 | 2 | LT21CAS_50BF_ATUADO | 949 | LT21CAS_50BF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Prot.21 - Bloqueada |  |  |  | DiVal | 28 | 52 | 1 | LT21CAS_21_BLOQUEADA | 950 | LT21CAS_21_BLOQUEADA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 21 Trip Fase A |  |  |  | Fault Di | 28 | 206 | 2 | LT21CAS_21FA_ATUADO | 951 | LT21CAS_21FA_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 21 Trip Fase B |  |  |  | Fault Di | 28 | 207 | 2 | LT21CAS_21FB_ATUADO | 952 | LT21CAS_21FB_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 21 Trip Fase C |  |  |  | Fault Di | 28 | 208 | 2 | LT21CAS_21FC_ATUADO | 953 | LT21CAS_21FC_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 21 N Trip |  |  |  | Fault Di | 28 | 212 | 2 | LT21CAS_21N_ATUADO | 954 | LT21CAS_21N_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 21 Trip3p.Z1sf |  |  |  | Auto Fault | 28 | 224 | 2 | LT21CAS_21Z1SF_ATUADO | 955 | LT21CAS_21Z1SF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 22 Trip3p.Z1mf |  |  |  | Auto Fault | 28 | 225 | 2 | LT21CAS_21Z1MF_ATUADO | 956 | LT21CAS_21Z1MF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 21 Trip3p.Z2 |  |  |  | Auto Fault | 28 | 217 | 2 | LT21CAS_21Z2_ATUADO | 957 | LT21CAS_21Z2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 21 Trip3p.Z3 |  |  |  | Auto Fault | 28 | 218 | 2 | LT21CAS_21Z3_ATUADO | 958 | LT21CAS_21Z3_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 21 Trip3p.Z4 |  |  |  | Auto Fault | 28 | 209 | 2 | LT21CAS_21Z4_ATUADO | 959 | LT21CAS_21Z4_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Ligar DJ Sobre Falha |  |  |  | Auto Fault | 25 | 95 | 2 | LT21CAS_50HS_ATUADO | 960 | LT21CAS_50HS_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 67N TRIP |  |  |  | Auto Fault | 166 | 69 | 2 | LT21CAS_67N_ATUADO | 961 | LT21CAS_67N_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuada Proteção Backup: 5XB TRIP |  |  |  | Auto Fault | 128 | 72 | 2 | LT21CAS_5XB_ATUADO | 962 | LT21CAS_5XB_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Supervisão Medição: Falha Fusível TPs |  |  |  | DiVal | 135 | 149 | 1 | LT21CAS_60FF_ALARME | 963 | LT21CAS_60FF_ALARME | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Falta Tensão LT - Alarme |  |  |  | DiVal | 240 | 204 | 1 | LT21CAS_FALTA_TENSAO_LT | OR | LTCAS_FALTA_TENSAO_LT | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Localiz.Defeito - Disparo |  |  |  | DiVal | 151 | 7 | 1 | LT21CAS_LDF_ATUADO | 964 | LT21CAS_LDF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Saúde Comunicação | [7 empty] | LT21CAS_SAUDE_COMUNIC | 965 | LT21CAS_SAUDE_COMUNIC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## LTARV67
SE GUAPORÉ - LT ARV 138kV
RELÉ xxF1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
| Medição | [27 empty] | IDF | [6 empty] | CALC
7SJ64 (End.: 30/1Eh) | LT ARV | Tensão Barra A-B |  |  |  | AI Val | 134 | 137 | 9/6 | LT67ARV_TENSAO_FB | 240 | LTARV_TENSAO_FB | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Corrente Fase A |  |  |  | AI Val | 134 | 137 | 9/1 | LT67ARV_CORRENTE_FA | 241 | LTARV_CORRENTE_FA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Corrente Fase B |  |  |  | AI Val | 134 | 137 | 9/2 | LT67ARV_CORRENTE_FB | 242 | LTARV_CORRENTE_FB | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Corrente Fase C |  |  |  | AI Val | 134 | 137 | 9/3 | LT67ARV_CORRENTE_FC | 243 | LTARV_CORRENTE_FC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Potência Ativa |  |  |  | AI Val | 134 | 137 | 9/11 | LT67ARV_POT_ATIVA | 244 | LTARV_POT_ATIVA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Potência Reativa |  |  |  | AI Val | 134 | 137 | 9/12 | LT67ARV_POT_REATIVA | 245 | LTARV_POT_REATIVA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Defeito na Linha (km) |  |  |  | FPAI | 151 | 19 | 4 | LT67ARV_DIST_DEFEITO | 246 | LT67ARV_DIST_DEFEITO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Disjuntor 52-20 - Abrir/Fechar |  |  |  | Command | 240 | 160 | 20 | LT67ARV_COMANDOS_DJ | 192 | LTARV_COMANDOS_DJ | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Seccion. 89-120 - Abrir/Fechar |  |  |  | Command | 240 | 161 | 20 | LT67ARV_COMANDOS_S89D | 193 | LT67ARV_COMANDOS_S89D | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Seccion. 89-118 - Abrir/Fechar |  |  |  | Command | 240 | 163 | 20 | LT67ARV_COMANDOS_S89B | 194 | LT67ARV_COMANDOS_S89B | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Seccion. 89-122 - Abrir/Fechar |  |  |  | Command | 240 | 162 | 20 | LT67ARV_COMANDOS_S89C | 195 | LT67ARV_COMANDOS_S89C | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | 79 - Incluir/Excluir |  |  |  | Command | 240 | 169 | 20 | LT67ARV_COMANDOS_79 | 196 | LTARV_COMANDOS_79 | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Troca Grupo de Ajuste |  |  |  | Command | 240 | 170 | 20 | LT67ARV_COMANDOS_GRUPO | 197 | LT67ARV_COMANDOS_GRUPO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Disjuntor 52-20 – Aberto |  |  |  | DiSOEx2 | 240 | 160 | 1 | LT67ARV_DJ_ABERTO | 980 | LTARV_DJ_ABERTO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Disjuntor 52-20 – Fechado |  |  |  | DiSOEx2 | 240 | 160 | 1 | LT67ARV_DJ_FECHADO | 981 | LTARV_DJ_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.89-120 - Aberto |  |  |  | DiSOEx2 | 240 | 161 | 1 | LT67ARV_S26QB_ABERTA | 982 | LTARV_S26QB_ABERTA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.89-120 - Fechado |  |  |  | DiSOEx2 | 240 | 161 | 1 | LT67ARV_S26QB_FECHADA | 983 | LTARV_S26QB_FECHADA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.89-118 - Aberto |  |  |  | DiSOEx2 | 240 | 162 | 1 | LT67ARV_S26QC_ABERTA | 984 | LTARV_S26QC_ABERTA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.89-118 - Fechado |  |  |  | DiSOEx2 | 240 | 162 | 1 | LT67ARV_S26QC_FECHADA | 985 | LTARV_S26QC_FECHADA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.89-122 - Aberto |  |  |  | DiSOEx2 | 240 | 163 | 1 | LT67ARV_S26QD_ABERTA | 986 | LTARV_S26QD_ABERTA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.89-122 - Fechado |  |  |  | DiSOEx2 | 240 | 163 | 1 | LT67ARV_S26QD_FECHADA | 987 | LTARV_S26QD_FECHADA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Seccion. 29-07 - Aberto |  |  |  | DiSOEx2 | 240 | 164 | 1 | LT67ARV_S29T_ABERTA | 988 | LTARV_S29T_ABERTA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Seccion. 29-07 - Fechado |  |  |  | DiSOEx2 | 240 | 164 | 1 | LT67ARV_S29T_FECHADA | 989 | LTARV_S29T_FECHADA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | DJ - SF6 Alarme |  |  |  | DiVal | 240 | 192 | 1 | LT67ARV_SF6_ALARME | 990 | LTARV_SF6_ALARME | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | DJ - SF6 Abertura e Bloqueio |  |  |  | DiVal | 240 | 191 | 1 | LT67ARV_SF6_BLOQUEIO | 991 | LTARV_SF6_BLOQUEIO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | DJ - Mola Descarregada |  |  |  | DiVal | 240 | 190 | 1 | LT67ARV_MOLA_DESC | 992 | LTARV_MOLA_DESC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | DJ - 43LR - Posição LOCAL |  |  |  | DiVal | 240 | 193 | 1 | LT67ARV_43LR_POS_LOCAL | 993 | LTARV_43LR_POS_LOCAL | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | DJ - Falta VCC CMD/VCA AQUEC |  |  |  | DiVal | 240 | 194 | 1 | LT67ARV_FALTA_VCA_VCC | 994 | LTARV_FALTA_VCA_VCC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Sinal Relé (F21) - Excluir Telecomando COS |  |  |  | - |  |  | 1 | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Sinal Rele (F21) - Excluir 79 |  |  |  | - |  |  | 1 | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | DJ - Supervisão Circuito TRIP - Alarme |  |  |  | DiVal | 170 | 55 | 1 | LT67ARV_CIRC_TRIP_FALHA | 995 | LTARV_CIRC_TRIP_FALHA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.(89-120) - 43LR - Posição LOCAL |  |  |  | DiVal | 240 | 196 | 1 | LT67ARV_S289B_43LR | 996 | LT67ARV_S289B_43LR | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.(89-120)-VCC CMD/MOTOR |  |  |  | DiVal | 240 | 197 | 1 | LT67ARV_S289B_DEF_INTERN | 997 | LT67ARV_S289B_DEF_INTERN | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.(89-118) - 43LR - Posição LOCAL |  |  |  | DiVal | 240 | 200 | 1 | LT67ARV_S289D_43LR | 998 | LT67ARV_S289D_43LR | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.(89-118)-VCC CMD/MOTOR |  |  |  | DiVal | 240 | 201 | 1 | LT67ARV_S289D_DEF_INTERN | 999 | LT67ARV_S289D_DEF_INTERN | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.(89-122) - 43LR - Posição LOCAL |  |  |  | DiVal | 240 | 198 | 1 | LT67ARV_S289C_43LR | 1000 | LT67ARV_S289C_43LR | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.(89-122)-VCC CMD/MOTOR |  |  |  | DiVal | 240 | 199 | 1 | LT67ARV_S289C_DEF_INTERN | 1001 | LT67ARV_S289C_DEF_INTERN | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Operação Indevida das Secc.Isoladoras |  |  |  | DiVal | 240 | 195 | 1 | LT67ARV_OPER_INDEV_SECC | 1002 | LTARV_OPER_INDEV_SECC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | DJ - Chave 43TC Excluida |  |  |  | DiVal | 101 | 85 | 1 | LT67ARV_43TC_EXCLUIDA | 1003 | LTARV_43TC_EXCLUIDA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Grupo de Ajustes B - Ativado |  |  |  | DiVal | 160 | 24 | 1 | LT67ARV_GRUPOB_ATIVADO | 1004 | LT67ARV_GRUPOB_ATIVADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | 79 supervisionado pelo 25 |  |  |  | Auto DI | 160 | 129 | 1 | LT67ARV_25_SUPERV_79 | 1005 | LT67ARV_25_SUPERV_79 | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | 79 - Excluído |  |  |  | DiVal | 40 | 81 | 1 | LT67ARV_79_EXCLUIDO | 1006 | LTARV_79_EXCLUIDO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | 79 - Religamento Sucedido |  |  |  | DiVal | 40 | 162 | 1 | LT67ARV_79_SUCEDIDO | 1007 | LT67ARV_79_SUCEDIDO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | 79 - Bloqueado (Lockout) |  |  |  | FaultDI | 40 | 163 | 2 | LT67ARV_79_BLOQUEADO | 1008 | LT67ARV_79_BLOQUEADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | 25 - Bloqueado |  |  |  | DiVal | 41 | 204 | 1 | LT67ARV_25_BLOQUEADO | 1009 | LT67ARV_25_BLOQUEADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | 25 - Falha Operação Sincronismo |  |  |  | Auto DI | 41 | 35 | 1 | LT67ARV_25_FALHA_SINCRO | 1010 | LTARV_25_FALHA_SINCRO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 50 BF |  |  |  | AutoFault | 160 | 85 | 2 | LT67ARV_50BF_ATUADO | 1011 | LT67ARV_50BF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Prot.67 - Bloqueada |  |  |  | DiVal | 63 | 11 | 1 | LT67ARV_67_BLOQUEADA | 1012 | LT67ARV_67_BLOQUEADA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 67-1 |  |  |  | FaultDI | 63 | 25 | 2 | LT67ARV_67_1_ATUADO | 1013 | LT67ARV_67_1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 67-2 |  |  |  | FaultDI | 63 | 72 | 2 | LT67ARV_67_2_ATUADO | 1014 | LT67ARV_67_2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 67 - TOC |  |  |  | FaultDI | 63 | 35 | 2 | LT67ARV_67TOC_ATUADO | 1015 | LT67ARV_67TOC_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 67N-1 |  |  |  | FaultDI | 63 | 43 | 2 | LT67ARV_67N_1_ATUADO | 1016 | LT67ARV_67N_1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 67N-2 |  |  |  | FaultDI | 63 | 64 | 2 | LT67ARV_67N_2_ATUADO | 1017 | LT67ARV_67N_2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 67N - TOC |  |  |  | FaultDI | 63 | 46 | 2 | LT67ARV_67N_TOC_ATUADO | 1018 | LT67ARV_67N_TOC_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 67 - Fase A |  |  |  | FaultDI | 63 | 75 | 2 | LT67ARV_67_FA_ATUADO | 1019 | LT67ARV_67_FA_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 67 - Fase B |  |  |  | FaultDI | 63 | 76 | 2 | LT67ARV_67_FB_ATUADO | 1020 | LT67ARV_67_FB_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 67 - Fase C |  |  |  | FaultDI | 63 | 77 | 2 | LT67ARV_67_FC_ATUADO | 1021 | LT67ARV_67_FC_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Supervisão Medição: Falha Fusível TPs |  |  |  | DiVal | 135 | 149 | 1 | LT67ARV_60FF_ALARME | 1022 | LT67ARV_60FF_ALARME | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Falta Tensão LT - Alarme |  |  |  | DiVal | 240 | 217 | 1 | LT67ARV_FALTA_TENSAO_LT | 1023 | LTARV_FALTA_TENSAO_LT | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Localiz.Defeito - Disparo |  |  |  | DiVal | 151 | 7 | 1 | LT67ARV_LDF_ATUADO | 1024 | LT67ARV_LDF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuada Proteção Sub-Frequencia - E1 |  |  |  | FaultDI | 70 | 234 | 2 | LT67ARV_81U_E1_ATUADO | 1025 | LT67ARV_81U_E1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuada Proteção Sobre-Frequencia - E1 |  |  |  | FaultDI | 70 | 236 | 2 | LT67ARV_81O_E1_ATUADO | 1026 | LT67ARV_81O_E1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 50-1 |  |  |  | AutoFault | 160 | 90 | 2 | LT50ARV_50_1_ATUADO | 1027 | LT50ARV_50_1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 50-2 |  |  |  | AutoFault | 160 | 91 | 2 | LT50ARV_50_2_ATUADO | 1028 | LT50ARV_50_2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 51 |  |  |  | FaultDI | 60 | 58 | 2 | LT50ARV_51F_ATUADO | 1029 | LT50ARV_51F_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 50N-1 |  |  |  | AutoFault | 160 | 92 | 2 | LT50ARV_50N_1_ATUADO | 1030 | LT50ARV_50N_1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 50N-2 |  |  |  | AutoFault | 160 | 93 | 2 | LT50ARV_50N_2_ATUADO | 1031 | LT50ARV_50N_2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 51N |  |  |  | FaultDI | 60 | 66 | 2 | LT50ARV_51N_ATUADO | 1032 | LT50ARV_51N_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuada Proteção 27 |  |  |  | FaultDI | 74 | 81 | 2 | LT67ARV_27_ATUADO | 1033 | LT67ARV_27_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuada Proteção 59 |  |  |  | FaultDI | 74 | 83 | 2 | LT67ARV_59_ATUADO | 1034 | LT67ARV_59_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | 25 diferença de Tensão |  |  |  | Auto DI | 41 | 207 | 1 | LT67ARV_25_TENSAO_DIF | 1035 | LTARV_25_TENSAO_DIF | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | 25 diferença de Frequência |  |  |  | Auto DI | 41 | 208 | 1 | LT67ARV_25_FREQ_DIF | 1036 | LTARV_25_FREQ_DIF | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | 25 diferença de Ângulo |  |  |  | Auto DI | 41 | 209 | 1 | LT67ARV_25_ANG_DIF | 1037 | LTARV_25_ANG_DIF | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Saúde Comunicação | [8 empty] | 1038 | LT67ARV_SAUDE_COMUNIC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## LTARV21
SE GUAPORÉ - LT ARV 138kV
RELÉ xxF1 |  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
| Medição | [27 empty] | IDF | [6 empty] | CALC
7SA631 (End.: 31/1F) | LT ARV | Tensão fase B da LT |  |  |  | AI Val | 134 | 124 | 9/5 | LT21ARV_TENSAO_FB | IDF | LTARV_TENSAO_FB | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Corrente fase A |  |  |  | AI Val | 134 | 124 | 9/1 | LT21ARV_CORRENTE_FA | IDF | LTARV_CORRENTE_FA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Corrente fase B |  |  |  | AI Val | 134 | 124 | 9/2 | LT21ARV_CORRENTE_FB | IDF | LTARV_CORRENTE_FB | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Corrente fase C |  |  |  | AI Val | 134 | 124 | 9/3 | LT21ARV_CORRENTE_FC | IDF | LTARV_CORRENTE_FC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Potência Ativa |  |  |  | AI Val | 134 | 124 | 9/7 | LT21ARV_POT_ATIVA | IDF | LTARV_POT_ATIVA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Potência Reativa |  |  |  | AI Val | 134 | 124 | 9/8 | LT21ARV_POT_REATIVA | IDF | LTARV_POT_REATIVA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Defeito na Linha (km) |  |  |  | FPAI | 151 | 19 | 4 | LT21ARV_DIST_DEFEITO | 247 | LT21ARV_DIST_DEFEITO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Controle | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Disjuntor 52-20 - Abrir/Fechar |  |  |  | Command | 240 | 160 | 20 | LT21ARV_COMANDOS_DJ | IDF | LTARV_COMANDOS_DJ | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | 79 - Incluir/Excluir |  |  |  | Command | 240 | 169 | 20 | LT21ARV_COMANDOS_79 | IDF | LTARV_COMANDOS_79 | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Troca Grupo de Ajuste |  |  |  | Command | 240 | 170 | 20 | LT21ARV_COMANDOS_GRUPO | 198 | LT21ARV_COMANDOS_GRUPO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Sinalização | [20 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Disjuntor 52-20 – Aberto |  |  |  | DiSOEx2 | 240 | 160 | 1 | LT21ARV_DJ_ABERTO | IDF | LTARV_DJ_ABERTO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Disjuntor 52-20 – Fechado |  |  |  | DiSOEx2 | 240 | 160 | 1 | LT21ARV_DJ_FECHADO | IDF | LTARV_DJ_FECHADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Secc.89-120 - Aberto |  |  |  | DiSOEx2 | 240 | 161 | 1 | LT21ARV_S26QB_ABERTA | IDF | LTARV_S26QB_ABERTA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Secc.89-120 - Fechado |  |  |  | DiSOEx2 | 240 | 161 | 1 | LT21ARV_S26QB_FECHADA | IDF | LTARV_S26QB_FECHADA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Secc.89-118 - Aberto |  |  |  | DiSOEx2 | 240 | 162 | 1 | LT21ARV_S26QC_ABERTA | IDF | LTARV_S26QC_ABERTA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Secc.89-118 - Fechado |  |  |  | DiSOEx2 | 240 | 162 | 1 | LT21ARV_S26QC_FECHADA | IDF | LTARV_S26QC_FECHADA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Secc.89-122 - Aberto |  |  |  | DiSOEx2 | 240 | 163 | 1 | LT21ARV_S26QD_ABERTA | IDF | LTARV_S26QD_ABERTA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Secc.89-122 - Fechado |  |  |  | DiSOEx2 | 240 | 163 | 1 | LT21ARV_S26QD_FECHADA | IDF | LTARV_S26QD_FECHADA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Seccion. 29-07 - Aberto |  |  |  | DiSOEx2 | 240 | 164 | 1 | LT21ARV_S29T_ABERTA | IDF | LTARV_S29T_ABERTA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Seccion. 29-07 - Fechado |  |  |  | DiSOEx2 | 240 | 164 | 1 | LT21ARV_S29T_FECHADA | IDF | LTARV_S29T_FECHADA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | DJ - Chave 43TC - Incluir/Excluir |  |  |  | DiVal | 101 | 85 | 1 | LT21ARV_43TC_EXCLUIDA | OR | LTARV_43TC_EXCLUIDA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | DJ - SF6 - Alarme |  |  |  | DiVal | 240 | 192 | 1 | LT21ARV_DJ_SF6_ALARME | IDF | LTARV_DJ_SF6_ALARME | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | DJ - SF6 - Bloqueio |  |  |  | DiVal | 240 | 191 | 1 | LT21ARV_DJ_SF6_BLOQ | IDF | LTARV_DJ_SF6_BLOQ | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | DJ - Mola Descarregada |  |  |  | DiVal | 240 | 190 | 1 | LT21ARV_DJ_MOLA_DESC | IDF | LTARV_DJ_MOLA_DESC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | DJ - 43LR - Posição LOCAL |  |  |  | DiVal | 240 | 193 | 1 | LT21ARV_DJ_43LR_LOC | IDF | LTARV_DJ_43LR_LOC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | DJ - Falta VCC de COM/MOTOR - Alarme |  |  |  | DiVal | 240 | 194 | 1 | LT21ARV_DJ_FVCC_CMD | IDF | LTARV_DJ_FVCC_CMD | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Sinal Rele (F67) - Excluir 43TC | [7 empty] | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Sinal Rele (F67) - Excluir 79 | [7 empty] | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Operação Indevida de SECCIONADORAS |  |  |  | DiVal | 240 | 195 | 1 | LT21ARV_OP_INDEV_SEC | OR | LTARV_OP_INDEV_SEC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | DJ - Supervisão Circuito TRIP - Alarme |  |  |  | DiVal | 170 | 55 | 1 | LT21ARV_DJ_SBOB_TRIP | OR | LTARV_DJ_SBOB_TRIP | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Grupo de Ajustes B - Ativado |  |  |  | DiVal | 128 | 24 | 1 | LT21ARV_GRPB_ATIVADO | 1040 | LT21ARV_GRPB_ATIVADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | 79 - Excluído |  |  |  | DiVal | 40 | 81 | 1 | LT21ARV_79_EXCLUIDO | OR | LTARV_79_EXCLUIDO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | 79 - Disparo |  |  |  | Auto DI | 160 | 128 | 1 | LT21ARV_25_SUP_79 | 1041 | LT21ARV_25_SUP_79 | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | 79 - Religamento Sucedido |  |  |  | Auto DI | 40 | 162 | 1 | LT21ARV_79_SUCEDIDO | 1042 | LT21ARV_79_SUCEDIDO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | 79 - Bloqueado (Lockout) |  |  |  | AutoFault | 150 | 180 | 2 | LT21ARV_79_BLOQUEADO | 1044 | LT21ARV_79_BLOQUEADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | 25 - Bloqueado |  |  |  | DiVal | 41 | 32 | 1 | LT21ARV_25_BLOQUEADO | 1043 | LT21ARV_25_BLOQUEADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | 25 - Falha Operação Sincronismo |  |  |  | Auto DI | 41 | 35 | 1 | LT21ARV_25_FALHA_SINC | OR | LTARV_25_FALHA_SINC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 50 BF |  |  |  | AutoFault | 160 | 85 | 2 | LT21ARV_50BF_ATUADO | 1045 | LT21ARV_50BF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Supervisão Medição: Falha Fusível TPs |  |  |  | DiVal | 135 | 149 | 1 | LT21ARV_60FF_ALARME | 1046 | LT21ARV_60FF_ALARME | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Prot.21 - Bloqueada |  |  |  | DiVal | 28 | 52 | 1 | LT21ARV_21_BLOQUEADA | 1047 | LT21ARV_21_BLOQUEADA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 21 Trip Fase A |  |  |  | FaultDI | 28 | 206 | 2 | LT21ARV_21FA_ATUADO | 1048 | LT21ARV_21FA_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 21 Trip Fase B |  |  |  | FaultDI | 28 | 207 | 2 | LT21ARV_21FB_ATUADO | 1049 | LT21ARV_21FB_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 21 Trip Fase C |  |  |  | FaultDI | 28 | 208 | 2 | LT21ARV_21FC_ATUADO | 1050 | LT21ARV_21FC_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 21 N Trip |  |  |  | FaultDI | 28 | 212 | 2 | LT21ARV_21N_ATUADO | 1051 | LT21ARV_21N_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 21 Trip3p.Z1sf |  |  |  | AutoFault | 28 | 224 | 2 | LT21ARV_21Z1SF_ATUADO | 1052 | LT21ARV_21Z1SF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 21 Trip3p.Z1mf |  |  |  | AutoFault | 28 | 225 | 2 | LT21ARV_21Z1MF_ATUADO | 1053 | LT21ARV_21Z1MF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 21 Trip3p.Z2 |  |  |  | AutoFault | 28 | 217 | 2 | LT21ARV_21Z2_ATUADO | 1054 | LT21ARV_21Z2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 21 Trip3p.Z3 |  |  |  | AutoFault | 28 | 218 | 2 | LT21ARV_21Z3_ATUADO | 1055 | LT21ARV_21Z3_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 21 Trip3p.Z4 |  |  |  | AutoFault | 28 | 209 | 2 | LT21ARV_21Z4_ATUADO | 1056 | LT21ARV_21Z4_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Falta Tensão LT - Alarme |  |  |  | DiVal | 240 | 205 | 1 | LT21ARV_LT_SEM_VCA | OR | LTARV_LT_SEM_VCA | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Localiz.Defeito - Disparo |  |  |  | DiVal | 151 | 7 | 1 | LT21ARV_LDF_ATUADO | 1057 | LT21ARV_LDF_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuada Proteção Backup: 5XB TRIP |  |  |  | AutoFault | 128 | 72 | 2 | LT21ARV_5XB_ATUADO | 1058 | LT21ARV_5XB_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuada Proteção 50HS - Trip ABC (SOTF) |  |  |  | AutoFault | 25 | 95 | 2 | LT21ARV_50HS_ATUADO | 1059 | LT21ARV_50HS_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 50N-1 |  |  |  | AutoFault | 160 | 92 | 2 | LT21ARV_50NE1_ATUADO | 1060 | LT21ARV_50NE1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 50N-2 |  |  |  | AutoFault | 160 | 93 | 2 | LT21ARV_50NE2_ATUADO | 1061 | LT21ARV_50NE2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 50/51 - Fase A |  |  |  | FaultDI | 64 | 117 | 2 | LT21ARV_5051FA_ATUADO | 1062 | LT21ARV_5051FA_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 50/51 - Fase B |  |  |  | FaultDI | 64 | 118 | 2 | LT21ARV_5051FB_ATUADO | 1063 | LT21ARV_5051FB_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 50/51 - Fase C |  |  |  | FaultDI | 64 | 119 | 2 | LT21ARV_5051FC_ATUADO | 1064 | LT21ARV_5051FC_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 51N |  |  |  | FaultDI | 60 | 66 | 2 | LT21ARV_51N_ATUADO | 1065 | LT21ARV_51N_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 50-1 |  |  |  | AutoFault | 64 | 121 | 2 | LT21ARV_50FNE1_ATUADO | 1066 | LT21ARV_50FNE1_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 50-2 |  |  |  | AutoFault | 64 | 122 | 2 | LT21ARV_50FNE2_ATUADO | 1067 | LT21ARV_50FNE2_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 51 |  |  |  | AutoFault | 64 | 123 | 2 | LT21ARV_51FN_ATUADO | 1068 | LT21ARV_51FN_ATUADO | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | 25 diferença de Tensão |  |  |  | Auto DI | 41 | 47 | 1 | LT21ARV_25_TENSAO_DIF | OR | LTARV_25_TENSAO_DIF | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | 25 diferença de Frequência |  |  |  | Auto DI | 41 | 48 | 1 | LT21ARV_25_FREQ_DIF | OR | LTARV_25_FREQ_DIF | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | 25 diferença de Ângulo |  |  |  | Auto DI | 41 | 49 | 1 | LT21ARV_25_ANG_DIF | OR | LTARV_25_ANG_DIF | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Saúde Comunicação | [8 empty] | 1069 | LT21ARV_SAUDE_COMUNIC | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## SACA - MMD
KRON |  | Descrição do ponto: | RELE |  |  | MODBUS | SLAVE |  |  | MASTER |  | LOCAL |  | COS |  | S6 | COS
EQUIPAMENTO | MÓDULO |  | FUNÇÃO MODBUS | REGISTRADOR | ENRADA | TIPO | VARIAVEIS | Identificação do ponto: | Lógica | Identificação do ponto: | DNP3 | SUL | RGE | SUL | RGE | NIVEL2 | NIVEL3
Medição
PM820 (End: 09) | SA | CORRENTE A | 3 (Read Holding Reg) | 43000 |  | 32 Bits |  | SACA_CORRENTE_FA |  | SACA_CORRENTE_FA | 270
PM820 (End: 09) | SA | CORRENTE B | 3 (Read Holding Reg) | 43002 |  | 32 Bits |  | SACA_CORRENTE_FB |  | SACA_CORRENTE_FB | 271
PM820 (End: 09) | SA | CORRENTE C | 3 (Read Holding Reg) | 43004 |  | 32 Bits |  | SACA_CORRENTE_FC |  | SACA_CORRENTE_FC | 272
PM820 (End: 09) | SA | TENSAO AB | 3 (Read Holding Reg) | 43020 |  | 32 Bits |  | SACA_TENSAO_AB |  | SACA_TENSAO_AB | 273
PM820 (End: 09) | SA | TENSAO BC | 3 (Read Holding Reg) | 43022 |  | 32 Bits |  | SACA_TENSAO_BC |  | SACA_TENSAO_BC | 274
PM820 (End: 09) | SA | TENSAO CA | 3 (Read Holding Reg) | 43024 |  | 32 Bits |  | SACA_TENSAO_CA |  | SACA_TENSAO_CA | 275
PM820 (End: 09) | SA | TENSAO A | 3 (Read Holding Reg) | 43028 |  | 32 Bits |  | SACA_TENSAO_A |  | SACA_TENSAO_A | -
PM820 (End: 09) | SA | TENSAO B | 3 (Read Holding Reg) | 43030 |  | 32 Bits |  | SACA_TENSAO_B |  | SACA_TENSAO_B | -
PM820 (End: 09) | SA | TENSAO C | 3 (Read Holding Reg) | 43032 |  | 32 Bits |  | SACA_TENSAO_C |  | SACA_TENSAO_C | -
PM820 (End: 09) | SA | POTÊNCIA ATIVA TOTAL | 3 (Read Holding Reg) | 43068 |  | 32 Bits |  | SACA_POT_ATIVA |  | SACA_POT_ATIVA | 276
PM820 (End: 09) | SA | POTÊNCIA REATIVA TOTAL | 3 (Read Holding Reg) | 43078 |  | 32 Bits |  | SACA_POT_REATIVA |  | SACA_POT_REATIVA | 277
PM820 (End: 09) | SA | SAÚDE COMUNICAÇÃO | [7 empty] | SACA_MMD_SAUDE_COMUNIC | 1093

## COMANDOS
SE GUAPORÉ
|  | PONTO | RELÉ | [8 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED |  |  |  |  | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Controle
SPS (End: 14) | TR2 | Comando TAP | 3 (Read Holding Reg) | 40788 | 0_1 | 0 | 0 | TR2_TELECOM_TAP | SPS | TR2_TELECOM_TAP | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
SPS (End: 14) | TR2 | Comandos R90 | 3 (Read Holding Reg) | 40788 | 5_6 | 0 | 0 | TR2_TELECOM_R90 | SPS | TR2_TELECOM_R90 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
SPS (End: 14) | TR3 | Comando TAP | 3 (Read Holding Reg) | 41556 | 0_1 | 0 | 0 | TR3_TELECOM_TAP | SPS | TR3_TELECOM_TAP | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
SPS (End: 14) | TR3 | Comandos R90 | 3 (Read Holding Reg) | 41556 | 5_6 | 0 | 0 | TR3_TELECOM_R90 | SPS | TR3_TELECOM_R90 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
SPS (End: 14) | TR2 | Comandos Mestre TR2 | 3 (Read Holding Reg) | 40788 | 2 | 0 | 0 | TR2_TELECOM_MESTRE | SPS | TR2_TELECOM_MESTRE | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
SPS (End: 14) | TR3 | Comandos Mestre TR3 | 3 (Read Holding Reg) | 41556 | 2 | 0 | 0 | TR3_TELECOM_MESTRE | SPS | TR3_TELECOM_MESTRE | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
SPS (End: 14) | TR2 | Comando Individual | 3 (Read Holding Reg) | 40788 | 4 | 0 | 0 | TR2_TELECOM_INDIVIDUAL | SPS | TR2_TELECOM_INDIVIDUAL | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
SPS (End: 14) | TR3 | Comando Individual | 3 (Read Holding Reg) | 41556 | 4 | 0 | 0 | TR3_TELECOM_INDIVIDUAL | SPS | TR3_TELECOM_INDIVIDUAL | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
0 | SE | CA_Comando Sirene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SE_ALARME_LIGAR | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-1 | 0 | 0 | R1SG-1/2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-2 | 0 | 0 | R1SG-3/4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-3 | 0 | 0 | R1SG-5/6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-4 | 0 | 0 | R1SG-7/8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-5 | 0 | 0 | R1SG-9/10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-6 | 0 | 0 | R1SG-11/12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-7 | 0 | 0 | R1SG-13/14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-8 | 0 | 0 | R1SG-15/16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-9 | 0 | 0 | R1SG-17/18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-10 | 0 | 0 | R1SG-19/20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-11 | 0 | 0 | R1SG-21/22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-12 | 0 | 0 | R1SG-23/24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-13 | 0 | 0 | R1SG-25/26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-14 | 0 | 0 | R1SG-27/28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-15 | 0 | 0 | R1SG-29/30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-16 | 0 | 0 | R1SG-31/32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-1 | TR1 | Comandos R90 | R1SH-1/2 | 0 | 0 | 0 | 0 | 0 | SET/RESET | TR1_COMANDOS_R90 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-2 | TR1 | Comando TAP | R1SH-3/4 | 0 | 0 | 0 | 0 | 0 | PULSO | TR1_COMANDOS_TAP | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-3 | 0 | 0 | R1SH-5/6 | 0 | 0 | 0 | 0 | 0 | PULSO | TR1_COMANDOS_TAP | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-4 | TR2 | Comando VF1 | R1SH-7/8 | 0 | 0 | 0 | 0 | 0 | SET/RESET | TR2_COMANDOS_VF1 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-5 | TR2 | Comando VF2 | R1SH-9/10 | 0 | 0 | 0 | 0 | 0 | SET/RESET | TR2_COMANDOS_VF2 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-6 | TR3 | Comando VF1 | R1SH-11/12 | 0 | 0 | 0 | 0 | 0 | PULSO | TR3_COMANDOS_VF1 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-7 | 0 | 0 | R1SH-13/14 | 0 | 0 | 0 | 0 | 0 | PULSO | TR3_COMANDOS_VF1 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-8 | B138 | Comando Rearme 86B | R1SH-15/16 | 0 | 0 | 0 | 0 | 0 | PULSO | B138_COMANDOS_86FD | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-9 | B69 | Comando Rearme 86B | R1SH-17/18 | 0 | 0 | 0 | 0 | 0 | PULSO | B69_COMANDOS_86FD | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-10 | B23P1 | Comando Rearme 86B | R1SH-19/20 | 0 | 0 | 0 | 0 | 0 | PULSO | B23P1_COMANDOS_86FD | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-11 | B23P2 | Comando Rearme 86B | R1SH-21/22 | 0 | 0 | 0 | 0 | 0 | PULSO | B23P2_COMANDOS_86FD | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-12 | GPR23 | Desligamento 26/49 - Excluir/Incluir | R1SH-23/24 | 0 | 0 | 0 | 0 | 0 | PULSO | ALGPR23_COMANDOS_RC | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-13 | 0 | 0 | R1SH-25/26 | 0 | 0 | 0 | 0 | 0 | PULSO | ALGPR23_COMANDOS_RC | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-14 | GPR24 | Desligamento 26/49 - Excluir/Incluir | R1SH-27/28 | 0 | 0 | 0 | 0 | 0 | PULSO | ALGPR24_COMANDOS_RC | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-15 | 0 | 0 | R1SH-29/30 | 0 | 0 | 0 | 0 | 0 | PULSO | ALGPR24_COMANDOS_RC | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
DO-16 | 0 | SIRENE ALARME | R1SH-31/32 | 0 | 0 | 0 | 0 | 0 | CALCULADO | SE_ALARME_DO | CALC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Disj. 52-13 (21QA) - Abrir / Fechar | 0 | 4/5 | 0 | DiSOEx2 | 240 | 160 | 1900-01-19 | GPR21_COMANDOS_DJ | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Religamento (79) - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 169 | 1900-01-19 | GPR21_COMANDOS_79 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Relé Neutro (51N) - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 170 | 1900-01-19 | GPR21_COMANDOS_PN | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Desligamento 26/49 - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 171 | 1900-01-19 | GPR21_COMANDOS_RC | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Disjuntor 52-12 Abrir/Fechar | 0 | 4/5 | 0 | Comando | 0 | 12 | 1900-01-17 | GPR22_COMANDOS_DJ | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Religador - Excluir/Incluir | 0 | 0 | 0 | Comando | 0 | 12 | 1900-01-01 | GPR22_COMANDOS_79 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | 50/51N - Excluir/Incluir | 0 | 0 | 0 | Comando | 0 | 12 | 1900-01-02 | GPR22_COMANDOS_PN | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Perfil Normal - Ativar/Desativar | 0 | 0 | 0 | Comando | 0 | 12 | 1900-01-06 | GPR22_COMANDOS_PERF0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Perfil Altenativo - Ativar/Desativar | 0 | 0 | 0 | Comando | 0 | 12 | 1900-01-07 | GPR22_COMANDOS_PERF1 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | 26/49 - Incluir | 0 | 0 | 0 | Comando | 0 | 12 | 1900-01-31 | GPR22_INCLUIR_RC | 15 | 32 incluir 33 excluir | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | 26/49 - Excluir | 0 | 0 | 0 | Comando | 0 | 12 | 1900-02-01 | GPR22_EXCLUIR_RC | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Disjuntor 52-11 Abrir/Fechar | 0 | 4/5 | 0 | Comando | 0 | 12 | 0 | GPR23_COMANDOS_DJ | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Religador - Excluir/Incluir | 0 | 0 | 0 | Comando | 0 | 12 | 1900-01-01 | GPR23_COMANDOS_79 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | 50/51N - Excluir/Incluir | 0 | 0 | 0 | Comando | 0 | 12 | 1900-01-04 | GPR23_COMANDOS_PN | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Perfil Normal - Ativar/Desativar | 0 | 0 | 0 | Comando | 0 | 12 | 1900-01-05 | GPR23_COMANDOS_PERF0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
ADVC (End:26) | GPR23 | Perfil Altenativo - Ativar/Desativar | 0 | 0 | 0 | Comando | 0 | 12 | 1900-01-06 | GPR23_COMANDOS_PERF1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Disjuntor 52-10 Abrir/Fechar | 0 | 4/5 | 0 | Comando | 0 | 12 | 0 | GPR24_COMANDOS_DJ | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Religador - Excluir/Incluir | 0 | 0 | 0 | Comando | 0 | 12 | 1900-01-01 | GPR24_COMANDOS_79 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | 50/51N - Excluir/Incluir | 0 | 0 | 0 | Comando | 0 | 12 | 1900-01-04 | GPR24_COMANDOS_PN | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Perfil Normal - Ativar/Desativar | 0 | 0 | 0 | Comando | 0 | 12 | 1900-01-05 | GPR24_COMANDOS_PERF0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
ADVC (End:27) | GPR24 | Perfil Altenativo - Ativar/Desativar | 0 | 0 | 0 | Comando | 0 | 12 | 1900-01-06 | GPR24_COMANDOS_PERF1 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Disj. 52-09 (11Q0) - Abrir / Fechar | 0 | 4/5 | 0 | DiSOEx2 | 240 | 160 | 1900-01-19 | GPR31_COMANDOS_DJ | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Religamento (79) - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 169 | 1900-01-19 | GPR31_COMANDOS_79 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Relé Neutro (51N) - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 170 | 1900-01-19 | GPR31_COMANDOS_PN | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Desligamento 26/49 - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 171 | 1900-01-19 | GPR31_COMANDOS_RC | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Disj. 24-01 (10Q0) - Abrir / Fechar | 0 | 4/5 | 0 | DiSOEx2 | 240 | 160 | 1900-01-19 | GPR32_COMANDOS_DJ | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Religamento (79) - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 169 | 1900-01-19 | GPR32_COMANDOS_79 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Relé Neutro (51N) - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 170 | 1900-01-19 | GPR32_COMANDOS_PN | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Desligamento 26/49 - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 171 | 1900-01-19 | GPR32_COMANDOS_RC | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Disj. 52-08 (09Q0) - Abrir / Fechar | 0 | 4/5 | 0 | DiSOEx2 | 240 | 160 | 1900-01-19 | GPR33_COMANDOS_DJ | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Religamento (79) - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 169 | 1900-01-19 | GPR33_COMANDOS_79 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Relé Neutro (51N) - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 170 | 1900-01-19 | GPR33_COMANDOS_PN | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Desligamento 26/49 - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 171 | 1900-01-19 | GPR33_COMANDOS_RC | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Disj. 52-07 (08Q0) - Abrir / Fechar | 0 | 4/5 | 0 | DiSOEx2 | 240 | 160 | 1900-01-19 | GPR34_COMANDOS_DJ | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Religamento (79) - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 169 | 1900-01-19 | GPR34_COMANDOS_79 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Relé Neutro (51N) - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 170 | 1900-01-19 | GPR34_COMANDOS_PN | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Desligamento 26/49 - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 171 | 1900-01-19 | GPR34_COMANDOS_RC | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Disj. 52-06 (07Q0) - Abrir / Fechar | 0 | 4/5 | 0 | DiSOEx2 | 240 | 160 | 1900-01-19 | GPR35_COMANDOS_DJ | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Religamento (79) - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 169 | 1900-01-19 | GPR35_COMANDOS_79 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Relé Neutro (51N) - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 170 | 1900-01-19 | GPR35_COMANDOS_PN | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Desligamento 26/49 - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 171 | 1900-01-19 | GPR35_COMANDOS_RC | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Disj. 52-05 (06Q0) - Abrir / Fechar | 0 | 4/5 | 0 | DiSOEx2 | 240 | 160 | 1900-01-19 | GPR36_COMANDOS_DJ | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Religamento (79) - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 169 | 1900-01-19 | GPR36_COMANDOS_79 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Relé Neutro (51N) - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 170 | 1900-01-19 | GPR36_COMANDOS_PN | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Desligamento 26/49 - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 171 | 1900-01-19 | GPR36_COMANDOS_RC | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj. 52-15 (06Q0) - Abrir / Fechar | 0 | 4/5 | 0 | DiSOEx2 | 240 | 160 | 1900-01-19 | IB23_COMANDOS_DJ | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Relé Neutro (51N) - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 170 | 1900-01-19 | IB23_COMANDOS_PN | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Disj. 52-19 (06Q0) - Abrir / Fechar | 0 | 4/5 | 0 | DiSOEx2 | 240 | 160 | 1900-01-19 | BC1_COMANDOS_DJ | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Automatismo - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 170 | 1900-01-19 | BC1_COMANDOS_AUTO | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Relé Neutro (51N) - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 171 | 1900-01-19 | BC1_COMANDOS_86BC | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Disj. 52-14 (06Q0) - Abrir / Fechar | 0 | 4/5 | 0 | DiSOEx2 | 240 | 160 | 1900-01-19 | BC2_COMANDOS_DJ | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Automatismo - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 170 | 1900-01-19 | BC2_COMANDOS_AUTO | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Relé Neutro (51N) - Excluir/Incluir | 0 | 0 | 0 | DiSOEx2 | 240 | 171 | 1900-01-19 | BC2_COMANDOS_86BC | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Disj.52-02 (XXQA) - Abrir/Fechar | 0 | 4/5 | 0 | Command | 240 | 160 | 1900-01-19 | TR3AT_COMANDOS_DJ | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Secc.89-04 (XXQD) - Abrir/Fechar | 0 | 1/2 | 0 | Command | 240 | 161 | 1900-01-19 | TR3AT_COMANDOS_S8904 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Secc.89-24 (03Q4) - Abrir / Fechar | 0 | 5/6 | 0 | Double | 240 | 161 | 1900-01-19 | TR3BT_COMANDOS_S8924 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Trocar Grupo de Ajuste A/B | 0 | 0 | 0 | Double | 240 | 188 | 1900-01-19 | TR3BT_COMANDOS_GRUPO | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 81 - Inclui / Excliu | 0 | 0 | 0 | Double | 240 | 220 | 1900-01-19 | TR3BT_81_I_E | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Disj.52-03 (15QA) - Abrir/Fechar | 0 | 4/5 | 0 | Command | 240 | 160 | 1900-01-19 | TR2AT_COMANDOS_DJ | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Secc.89-08 (15QD) - Abrir/Fechar | 0 | 1/2 | 0 | Command | 240 | 161 | 1900-01-19 | TR2AT_COMANDOS_S8908 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Secc. 89-62 (15QE) – Abrir / Fechar | 0 | 5/6 | 0 | Double | 240 | 161 | 1900-01-19 | TR2BT_COMANDOS_S8962 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Trocar Grupo de Ajuste A/B | 0 | 0 | 0 | Double | 240 | 188 | 1900-01-19 | TR2BT_COMANDOS_GRUPO | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 81 - Inclui / Excliu | 0 | 0 | 0 | Double | 240 | 220 | 1900-01-19 | TR2BT_81_I_E | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Disj.52-17 - Abrir/Fechar | 0 | 4/5 | 0 | Command | 240 | 160 | 1900-01-19 | TR1AT_COMANDOS_DJ | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-112 (S89D) - Abrir/Fechar | 0 | 1/2 | 0 | Command | 240 | 161 | 1900-01-19 | TR1AT_COMANDOS_S89D | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-114 (S89E) - Abrir/Fechar | 0 | 8/9 | 0 | Command | 240 | 162 | 1900-01-19 | TR1AT_COMANDOS_S89E | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-116 (S89C) - Abrir/Fechar | 0 | 11/12 | 0 | Command | 240 | 163 | 1900-01-19 | TR1AT_COMANDOS_S89C | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Disj.52-01 - Abrir/Fechar | 0 | 1/2 | 0 | DiSOEx2 | 240 | 160 | 1900-01-19 | TR1BT_COMANDOS_DJ | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Disjuntor 52-16 - Abrir/Fechar | 0 | 0 | 0 | Command | 240 | 160 | 1900-01-19 | LT21PCH_COMANDOS_DJ | IDF | LTPCH_COMANDOS_DJ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | 79 - Incluir/Excluir | 0 | 0 | 0 | Command | 240 | 169 | 1900-01-19 | LT21PCH_COMANDOS_79 | IDF | LTPCH_COMANDOS_79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Disjuntor 52-16 - Abrir/Fechar | 0 | 0 | 0 | Command | 240 | 160 | 1900-01-19 | LT67PCH_COMANDOS_DJ | 170 | LTPCH_COMANDOS_DJ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Secc.89-102 (D) - Abrir/Fechar | 0 | 0 | 0 | Command | 240 | 162 | 1900-01-19 | LT67PCH_COMANDOS_S89D | 171 | LT67PCH_COMANDOS_S89D | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Secc.89-100 (E) - Abrir/Fechar | 0 | 0 | 0 | Command | 240 | 161 | 1900-01-19 | LT67PCH_COMANDOS_S89E | 172 | LT67PCH_COMANDOS_S89E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Secc.89-104 (C) - Abrir/Fechar | 0 | 0 | 0 | Command | 240 | 163 | 1900-01-19 | LT67PCH_COMANDOS_S89C | 173 | LT67PCH_COMANDOS_S89C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | 79 - Incluir/Excluir | 0 | 0 | 0 | Command | 240 | 169 | 1900-01-19 | LT67PCH_COMANDOS_79 | 174 | LTPCH_COMANDOS_79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Troca Grupo de Ajuste | 0 | 0 | 0 | Command | 240 | 188 | 1900-01-19 | LT67PCH_COMANDOS_GRUPO | 175 | LT67PCH_COMANDOS_GRUPO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Disjuntor 52-04 - Abrir/Fechar | 0 | 6/7 | 0 | Command | 240 | 160 | 1900-01-19 | LT67KNP_COMANDOS_DJ | 180 | LTKNP_COMANDOS_DJ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | 79 - Incluir/Excluir | 0 | 11 | 0 | Command | 240 | 169 | 1900-01-19 | LT67KNP_COMANDOS_79 | 181 | LTKNP_COMANDOS_79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Disjuntor 52-04 - Abrir/Fechar | 0 | 0 | 0 | Command | 240 | 160 | 1900-01-19 | LT21KNP_COMANDOS_DJ | IDF | LTKNP_COMANDOS_DJ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | 79 - Incluir/Excluir | 0 | 0 | 0 | Command | 240 | 169 | 1900-01-19 | LT21KNP_COMANDOS_79 | IDF | LTKNP_COMANDOS_79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Disjuntor 52-18 - Abrir/Fechar | 0 | 0 | 0 | Command | 240 | 160 | 1900-01-19 | LT67CAS_COMANDOS_DJ | 185 | LTCAS_COMANDOS_DJ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Seccion. 89-108 (289E) - Abrir/Fechar | 0 | 0 | 0 | Command | 240 | 161 | 1900-01-19 | LT67CAS_COMANDOS_S89D | 186 | LT67CAS_COMANDOS_S89D | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Seccion. 89-106 (289D) - Abrir/Fechar | 0 | 0 | 0 | Command | 240 | 162 | 1900-01-19 | LT67CAS_COMANDOS_S89E | 187 | LT67CAS_COMANDOS_S89E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Seccion. 89-110 (289C) - Abrir/Fechar | 0 | 0 | 0 | Command | 240 | 163 | 1900-01-19 | LT67CAS_COMANDOS_S89C | 188 | LT67CAS_COMANDOS_S89C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | 79 - Incluir/Excluir | 0 | 0 | 0 | Command | 240 | 169 | 1900-01-19 | LT67CAS_COMANDOS_79 | 189 | LTCAS_COMANDOS_79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Disjuntor 52-18 - Abrir/Fechar | 0 | 0 | 0 | Command | 240 | 160 | 1900-01-19 | LT21CAS_COMANDOS_DJ | IDF | LTCAS_COMANDOS_DJ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | 79 - Incluir/Excluir | 0 | 0 | 0 | Command | 240 | 169 | 1900-01-19 | LT21CAS_COMANDOS_79 | IDF | LTCAS_COMANDOS_79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Disjuntor 52-20 - Abrir/Fechar | 0 | 0 | 0 | Command | 240 | 160 | 1900-01-19 | LT67ARV_COMANDOS_DJ | 192 | LTARV_COMANDOS_DJ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Seccion. 89-120 - Abrir/Fechar | 0 | 0 | 0 | Command | 240 | 161 | 1900-01-19 | LT67ARV_COMANDOS_S89D | 193 | LT67ARV_COMANDOS_S89D | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Seccion. 89-118 - Abrir/Fechar | 0 | 0 | 0 | Command | 240 | 163 | 1900-01-19 | LT67ARV_COMANDOS_S89B | 194 | LT67ARV_COMANDOS_S89B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Seccion. 89-122 - Abrir/Fechar | 0 | 0 | 0 | Command | 240 | 162 | 1900-01-19 | LT67ARV_COMANDOS_S89C | 195 | LT67ARV_COMANDOS_S89C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | 79 - Incluir/Excluir | 0 | 0 | 0 | Command | 240 | 169 | 1900-01-19 | LT67ARV_COMANDOS_79 | 196 | LTARV_COMANDOS_79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Troca Grupo de Ajuste | 0 | 0 | 0 | Command | 240 | 170 | 1900-01-19 | LT67ARV_COMANDOS_GRUPO | 197 | LT67ARV_COMANDOS_GRUPO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Disjuntor 52-20 - Abrir/Fechar | 0 | 0 | 0 | Command | 240 | 160 | 1900-01-19 | LT21ARV_COMANDOS_DJ | IDF | LTARV_COMANDOS_DJ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | 79 - Incluir/Excluir | 0 | 0 | 0 | Command | 240 | 169 | 1900-01-19 | LT21ARV_COMANDOS_79 | IDF | LTARV_COMANDOS_79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Troca Grupo de Ajuste | 0 | 0 | 0 | Command | 240 | 170 | 1900-01-19 | LT21ARV_COMANDOS_GRUPO | 198 | LT21ARV_COMANDOS_GRUPO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## DIGITAIS
SE GUAPORÉ
|  | PONTO | RELÉ | [8 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED |  |  |  |  | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Sinalização
PM820 (End: 09) | SA | SAÚDE COMUNICAÇÃO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SACA_MMD_SAUDE_COMUNIC | 1093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 16) | TR2 | Temp.Óleo - Alarme | 3 (Read Holding Reg) | 40024 | 0 | 0 | 0 | TR2_TM11_26T_ALARME | 0 | TR2_26T_ALARME | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 16) | TR2 | Temp.Óleo - Desligamento | 3 (Read Holding Reg) | 40024 | 1 | 0 | 0 | TR2_TM11_26T_ATUADO | 0 | TR2_26T_ATUADO | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 16) | TR2AT | Temp.Enrolamento AT- Alarme | 3 (Read Holding Reg) | 40024 | 4 | 0 | 0 | TR2_TM11_49_ALARME | 0 | TR2AT_49AT_ALARME | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 16) | TR2AT | Temp.Enrolamento AT- Desligamento | 3 (Read Holding Reg) | 40024 | 5 | 0 | 0 | TR2_TM11_49_ATUADO | 0 | TR2AT_49AT_ATUADO | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 16) | TR2 | SAÚDE COMUNICAÇÃO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TR2_TM11_SAUDE_COMUNIC | 555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 15) | TR2 | VF1 - Ligada | 3 (Read Holding Reg) | 40001 | 0 | 0 | 0 | TR2_TM1BT_VF1_LIGADA | 0 | TR2_VF1_LIGADA | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 15) | TR2 | VF2 - Ligada | 3 (Read Holding Reg) | 40001 | 1 | 0 | 0 | TR2_TM1BT_VF2_LIGADA | 0 | TR2_VF2_LIGADA | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 15) | TR2 | Temp.Óleo - Alarme | 3 (Read Holding Reg) | 40024 | 0 | 0 | 0 | TR2_TM12_26T_ALARME | 0 | TR2_26T_ALARME | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 15) | TR2 | Temp.Óleo - Desligamento | 3 (Read Holding Reg) | 40024 | 1 | 0 | 0 | TR2_TM12_26T_ATUADO | 0 | TR2_26T_ATUADO | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 15) | TR2BT | Temp.Enrolamento BT- Alarme | 3 (Read Holding Reg) | 40024 | 4 | 0 | 0 | TR2_TM12_49_ALARME | 0 | TR2BT_49BT_ALARME | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 15) | TR2BT | Temp.Enrolamento BT- Desligamento | 3 (Read Holding Reg) | 40024 | 5 | 0 | 0 | TR2_TM12_49_ATUADO | 0 | TR2BT_49BT_ATUADO | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 15) | TR2 | SAÚDE COMUNICAÇÃO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TR2_TM12_SAUDE_COMUNIC | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPS (End: 14) | TR2 | Relé 90 Excluído/Incluído | 3 (Read Holding Reg) | 40010 | 3 | 0 | 0 | TR2_R90_EXCLUIDO | SPS | TR2_R90_EXCLUIDO | 561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPS (End: 14) | TR2 | Posição MESTRE | 3 (Read Holding Reg) | 40010 | 0 | 0 | 0 | TR2_MESTRE | SPS | TR2_MESTRE | 562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPS (End: 14) | TR2 | Posição COMANDADO | 3 (Read Holding Reg) | 40010 | 1 | 0 | 0 | TR2_COMANDADO | SPS | TR2_COMANDADO | 563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPS (End: 14) | TR2 | Posição INDIVIDUAL | 0 | 0 | 0 | 0 | 0 | TR2_INDIVIDUAL | SPS | TR2_INDIVIDUAL | 564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPS (End: 14) | TR2 | Chave L/R - Pos. Local | 3 (Read Holding Reg) | 40010 | 2 | 0 | 0 | TR2_SPS_43LR_LOCAL | SPS | TR2_SPS_43LR_LOCAL | 565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPS (End: 14) | TR2 | Erro Paralelismo | 3 (Read Holding Reg) | 40011 | 1 | 0 | 0 | TR2_SPS_ERRO_PARALEL | SPS | TR2_SPS_ERRO_PARALEL | 566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPS (End: 14) | TR3 | Relé 90 Excluído/Incluído | 3 (Read Holding Reg) | 40019 | 3 | 0 | 0 | TR3_R90_EXCLUIDO | SPS | TR3_R90_EXCLUIDO | 454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPS (End: 14) | TR3 | Posição MESTRE | 3 (Read Holding Reg) | 40019 | 0 | 0 | 0 | TR3_MESTRE | SPS | TR3_MESTRE | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPS (End: 14) | TR3 | Posição COMANDADO | 3 (Read Holding Reg) | 40019 | 1 | 0 | 0 | TR3_COMANDADO | SPS | TR3_COMANDADO | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPS (End: 14) | TR3 | Posição INDIVIDUAL | 0 | 0 | 0 | 0 | 0 | TR3_INDIVIDUAL | SPS | TR3_INDIVIDUAL | 457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPS (End: 14) | TR3 | Chave L/R - Pos.Local | 3 (Read Holding Reg) | 40019 | 2 | 0 | 0 | TR3_SPS_43LR_LOCAL | SPS | TR3_SPS_43LR_LOCAL | 458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPS (End: 14) | TR3 | Erro Paralelismo | 3 (Read Holding Reg) | 40020 | 1 | 0 | 0 | TR3_SPS_ERRO_PARALEL | SPS | TR3_SPS_ERRO_PARALEL | 459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPS (End: 14) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPS (End: 14) | TR2 | Saúde Comunicação | 3 (Read Holding Reg) | 0 | 0 | 0 | 0 | 0 | SPS | SPS_SAUDE_COMUNIC | 567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 02) | TR1 | Temp.Óleo - Alarme | 3 (Read Holding Reg) | 40024 | 0 | 0 | 0 | TR1_TM11_26T_ALARME | OR | TR1_26T_ALARME | 708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 02) | TR1 | Temp.Óleo - Desligamento | 3 (Read Holding Reg) | 40024 | 1 | 0 | 0 | TR1_TM11_26T_ATUADO | OR | TR1_26T_ATUADO | 709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 02) | TR1AT | Temp.Enrolamento AT- Alarme | 3 (Read Holding Reg) | 40024 | 4 | 0 | 0 | TR1_TM11_49_ALARME | 0 | TR1AT_49AT_ALARME | 710 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 02) | TR1AT | Temp.Enrolamento AT- Desligamento | 3 (Read Holding Reg) | 40024 | 5 | 0 | 0 | TR1_TM11_49_ATUADO | 0 | TR1AT_49AT_ATUADO | 711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 02) | TR1 | SAÚDE COMUNICAÇÃO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TR1_TM11_SAUDE_COMUNIC | 712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 03) | TR1 | Temp.Óleo - Alarme | 3 (Read Holding Reg) | 40024 | 0 | 0 | 0 | TR1_TM12_26T_ALARME | OR | TR1_26T_ALARME | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 03) | TR1 | Temp.Óleo - Desligamento | 3 (Read Holding Reg) | 40024 | 1 | 0 | 0 | TR1_TM12_26T_ATUADO | OR | TR1_26T_ATUADO | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 03) | TR1BT | Temp.Enrolamento AT- Alarme | 3 (Read Holding Reg) | 40024 | 4 | 0 | 0 | TR1_TM12_49_ALARME | 0 | TR1BT_49BT_ALARME | 713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 03) | TR1BT | Temp.Enrolamento AT- Desligamento | 3 (Read Holding Reg) | 40024 | 5 | 0 | 0 | TR1_TM12_49_ATUADO | 0 | TR1BT_49BT_ATUADO | 714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 03) | TR1 | SAÚDE COMUNICAÇÃO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TR1_TM12_SAUDE_COMUNIC | 715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | SE | CA_Sensor de Fumaça | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SE_SENSOR_FUMACA | 1080 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | SE | CA_central Armada | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SE_ALARME_ATIVO | 1081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | SE | CA_Sensor Invasão Externa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SENSOR_EXTERNO | 1082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | SE | CA_Sensor Invasão Interna | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SE_SENSOR_INTERNO | 1083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | SE | CA Sirene Disparada | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SE_SIRENE_DISPARADA | 1084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | SE | CA VCC_Presente | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CA_VCC_PRESENTE | 1085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | SE | CA Sensor Defeito | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SE_SENSOR_DEFEITO | 1086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-1 | 0 | 0 | R1SC-1 | 0 | 0 | 0 | 0 | 0 | CALCULADO | TR1_TAP_BIT1 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-2 | 0 | 0 | R1SC-2 | 0 | 0 | 0 | 0 | 0 | CALCULADO | TR1_TAP_BIT2 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-3 | 0 | 0 | R1SC-3 | 0 | 0 | 0 | 0 | 0 | CALCULADO | TR1_TAP_BIT3 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-4 | 0 | 0 | R1SC-4 | 0 | 0 | 0 | 0 | 0 | CALCULADO | TR1_TAP_BIT4 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-5 | 0 | 0 | R1SC-5 | 0 | 0 | 0 | 0 | 0 | CALCULADO | TR1_TAP_BIT5 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-6 | 0 | 0 | R1SC-6 | 0 | 0 | 0 | 0 | 0 | CALCULADO | TR1_TAP_BIT6 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-7 | TR1 | TR1 CDC em marcha | R1SC-7 | 0 | 0 | 0 | 0 | 0 | 0 | TR1_CDC_EM_MARCHA | 690 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-8 | TR1 | TR1 CDC DJ - Desligado | R1SC-8 | 0 | 0 | 0 | 0 | 0 | 0 | TR1_CDC_DJ_DESLIGADO | 691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-9 | TR1BT | DJ Falta Vca Aquecimento | R1SC-9 | 0 | 0 | 0 | 0 | 0 | 0 | TR1BT_DJ_FVCA_AQUEC | 692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SC-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-10 | TR1BT | DJ Falta Vcc Circ Fechamento | R1SC-11 | 0 | 0 | 0 | 0 | 0 | 0 | TR1BT_DJ_FVCC_CIRC_CLOSE | 693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SC-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-11 | TR1AT | DJ Falta Vca Aquecimento | R1SC-13 | 0 | 0 | 0 | 0 | 0 | 0 | TR1AT_DJ_FALTA_VCA_AQUEC | 694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SC-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-12 | TR1AT | DJ Falta Vcc Circ Fechamento | R1SC-15 | 0 | 0 | 0 | 0 | 0 | 0 | TR1AT_DJ_FALTA_VCC_CLOSE | 695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SC-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-13 | TR1AT | Defeito Relé | R1SC-17 | 0 | 0 | 0 | 0 | 0 | 0 | TR1AT_DEFEITO_RELE | 696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-14 | TR1 | Defeito Relé | R1SC-18 | 0 | 0 | 0 | 0 | 0 | 0 | TR1DIF_DEFEITO_RELE | 697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-15 | TR1BT | Defeito Relé | R1SC-19 | 0 | 0 | 0 | 0 | 0 | 0 | TR1BT_DEFEITO_RELE | 698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-16 | TR1 | VF12 - Defeito | R1SC-20 | 0 | 0 | 0 | 0 | 0 | 0 | TR1_VF1_2_DEFEITO | 699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-17 | TR1 | VF1 - Ligada | R1SC-21 | 0 | 0 | 0 | 0 | 0 | 0 | TR1_VF1_LIGADA | 700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-18 | TR1 | VF2 - Ligada | R1SC-22 | 0 | 0 | 0 | 0 | 0 | 0 | TR1_VF2_LIGADA | 701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-19 | TR1 | 71T Max Min - Alarme | R1SC-23 | 0 | 0 | 0 | 0 | 0 | 0 | TR1_OLEO_TR_MAX_MIN_AL | 702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-20 | TR1 | 71C Max Min - Alarme | R1SC-24 | 0 | 0 | 0 | 0 | 0 | 0 | TR1_OLEO_CDC_MAX_MIN_AL | 703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-21 | TR1 | Relé 90 - Excluído | R1SC-25 | 0 | 0 | 0 | 0 | 0 | 0 | TR1_90_EXCLUIDO | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SC-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-22 | TR1 | TM11 - Defeito relé | R1SC-27 | 0 | 0 | 0 | 0 | 0 | 0 | TR1_DEFEITO_TM1_1 | 705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SC-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-23 | TR1 | TM12 - Defeito relé | R1SC-29 | 0 | 0 | 0 | 0 | 0 | 0 | TR1_DEFEITO_TM1_2 | 706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SC-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-24 | TR1 | 86T Falta Vcc Circuito | R1SC-31 | 0 | 0 | 0 | 0 | 0 | 0 | TR1_FVCC_86T1 | 707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SC-32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-1 | TR2AT | Defeito Relé | R1SD-1 | 0 | 0 | 0 | 0 | 0 | 0 | TR2AT_DEFEITO_RELE_15F1 | 541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-2 | TR2 | Defeito Relé | R1SD-2 | 0 | 0 | 0 | 0 | 0 | 0 | TR2DIF_DEFEITO_RELE_15F2 | 542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-3 | TR2BT | Defeito Relé | R1SD-3 | 0 | 0 | 0 | 0 | 0 | 0 | TR2BT_DEFEITO_RELE_15F3 | 543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-4 | TR2 | 71T Max Min - Alarme | R1SD-4 | 0 | 0 | 0 | 0 | 0 | 0 | TR2_NIVOLEO_TR_MAXMIN | 544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-5 | TR2 | 71C Max Min - Alarme | R1SD-5 | 0 | 0 | 0 | 0 | 0 | 0 | TR2_NIVOLEO_CDC_MAXMIN | 545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-6 | TR2 | VF1 - Defeito | R1SD-6 | 0 | 0 | 0 | 0 | 0 | 0 | TR2_VF1_DEFEITO | 546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-7 | TR2 | VF2 - Defeito | R1SD-7 | 0 | 0 | 0 | 0 | 0 | 0 | TR2_VF2_DEFEITO | 547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-8 | TR2 | VF1 - Ligada | R1SD-8 | 0 | 0 | 0 | 0 | 0 | 0 | TR2_VF1_LIGADO | 548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-9 | TR2 | VF2 - Ligada | R1SD-9 | 0 | 0 | 0 | 0 | 0 | 0 | TR2_VF2_LIGADO | 549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SD-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-10 | TR2 | TM - Defeito relé | R1SD-11 | 0 | 0 | 0 | 0 | 0 | 0 | TR2_TM12_DEFEITO_RELE | 550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SD-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-11 | TR3 | 71T Max Min - Alarme | R1SD-13 | 0 | 0 | 0 | 0 | 0 | 0 | TR3_OLEO_TR_MAX_MIN_AL | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SD-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-12 | TR3 | 71C Max Min - Alarme | R1SD-15 | 0 | 0 | 0 | 0 | 0 | 0 | TR3_OLEO_CDC_MAX_MIN_AL | 445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SD-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-13 | 0 | SENSORES EXTERNOS | R1SD-17 | 0 | 0 | 0 | 0 | 0 | 0 | SE_SENSOR_EXTERNO | CALC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-14 | 0 | SENSORES INTERNOS | R1SD-18 | 0 | 0 | 0 | 0 | 0 | 0 | SE_SENSOR_INTERNO | CALC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-15 | 0 | SENSORES FUMAÇA | R1SD-19 | 0 | 0 | 0 | 0 | 0 | 0 | SE_SENSOR_FUMACA | CALC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-16 | 0 | CHAVE LIGAR/DESLIGAR | R1SD-20 | 0 | 0 | 0 | 0 | 0 | 0 | CA_COMANDO_LOCAL | CALC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-17 | 0 | SUPERVISAO 125Vcc | R1SD-21 | 0 | 0 | 0 | 0 | 0 | 0 | CA_VCC_PRESENTE | CALC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-18 | TR3AT | Defeito Relé | R1SD-22 | 0 | 0 | 0 | 0 | 0 | 0 | TR3AT_DEFEITO_RELE_04F1 | 446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-19 | TR3 | Defeito Relé | R1SD-23 | 0 | 0 | 0 | 0 | 0 | 0 | TR3DIF_DEFEITO_RELE_04F2 | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-20 | TR3BT | Defeito Relé | R1SD-24 | 0 | 0 | 0 | 0 | 0 | 0 | TR3BT_DEFEITO_RELE_04F3 | 448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-21 | TR3 | VF1 - Defeito | R1SD-25 | 0 | 0 | 0 | 0 | 0 | 0 | TR3_VF1_DEFEITO | 449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SD-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-22 | TR3 | VF2 - Defeito | R1SD-27 | 0 | 0 | 0 | 0 | 0 | 0 | TR3_VF2_DEFEITO | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SD-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-23 | TR3 | VF1 - Ligada | R1SD-29 | 0 | 0 | 0 | 0 | 0 | 0 | TR3_VF1_LIGADA | 451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SD-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-24 | TR3 | VF2 - Ligada | R1SD-31 | 0 | 0 | 0 | 0 | 0 | 0 | TR3_VF2_LIGADA | 452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SD-32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-1 | TR3 | CDC - Falta Vca Painel | R1SE-1 | 0 | 0 | 0 | 0 | 0 | 0 | TR3_CDC_FALTA_VCA_PAINEL | 453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-2 | LT CAS | Defeito Relé | R1SE-2 | 0 | 0 | 0 | 0 | 0 | 0 | LT21CAS_DEFEITO_RELE_25F1 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-3 | LT CAS | Defeito Relé | R1SE-3 | 0 | 0 | 0 | 0 | 0 | 0 | LT67CAS_DEFEITO_RELE_25F2 | 967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-4 | LT CAS | DJ Falta Vca Aquecimento | R1SE-4 | 0 | 0 | 0 | 0 | 0 | 0 | LTCAS_DJ_FALTA_VCA_AQUEC | 968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-5 | LT CAS | DJ Falta Vcc Circ Fechamento | R1SE-5 | 0 | 0 | 0 | 0 | 0 | 0 | LTCAS_DJ_FALTA_VCC_CLOSE | 969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-6 | LT KNP | Defeito Relé | R1SE-6 | 0 | 0 | 0 | 0 | 0 | 0 | LT21KNP_DEFEITO_RELE_02F1 | 880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-7 | LT KNP | Defeito Relé | R1SE-7 | 0 | 0 | 0 | 0 | 0 | 0 | LT67KNP_DEFEITO_RELE_02F2 | 881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-8 | LT ARV | Defeito Relé | R1SE-8 | 0 | 0 | 0 | 0 | 0 | 0 | LT21ARV_FALHA_RELE_26F1 | 1070 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-9 | LT ARV | Defeito Relé | R1SE-9 | 0 | 0 | 0 | 0 | 0 | 0 | LT67ARV_FALHA_RELE_26F2 | 1071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SE-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-10 | GPR23 | Defeito Relé | R1SE-11 | 0 | 0 | 0 | 0 | 0 | 0 | ALGPR23_DEFEITO_RELE | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SE-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-11 | GPR23 | Telecomando (43TC) - Excluído | R1SE-13 | 0 | 0 | 0 | 0 | 0 | 0 | ALGPR23_43TC_EXCLUIDA | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SE-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-12 | GPR23 | Proteção 26/49 - Incluida | R1SE-15 | 0 | 0 | 0 | 0 | 0 | 0 | ALGPR23_26_49_INCLUIDA | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SE-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-13 | B138 | 86BF Falta Vcc Circuito | R1SE-17 | 0 | 0 | 0 | 0 | 0 | 0 | B138_FALTA_VCC_86FD | 796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-14 | LT PCH | Defeito Relé | R1SE-18 | 0 | 0 | 0 | 0 | 0 | 0 | LT21PCH_DEFEITO_RELE_24F1 | 797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-15 | LT PCH | Defeito Relé | R1SE-19 | 0 | 0 | 0 | 0 | 0 | 0 | LT67PCH_DEFEITO_RELE_24F2 | 798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-16 | LT PCH | MDJ TP Barra - Desligado | R1SE-20 | 0 | 0 | 0 | 0 | 0 | 0 | LTPCH_MDJ_TP_PROT_ABERTO | 799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-17 | LT PCH | MDJ TP Linha - Desligado | R1SE-21 | 0 | 0 | 0 | 0 | 0 | 0 | LTPCH_MINIDJ_TP_69_ABERTO | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-18 | 0 | Reserva | R1SE-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-19 | 0 | Reserva | R1SE-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-20 | 0 | Reserva | R1SE-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-21 | 0 | Reserva | R1SE-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SE-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-22 | GPR24 | Defeito Relé | R1SE-27 | 0 | 0 | 0 | 0 | 0 | 0 | ALGPR24_DEFEITO_RELE | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SE-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-23 | GPR24 | Telecomando (43TC) - Excluído | R1SE-29 | 0 | 0 | 0 | 0 | 0 | 0 | ALGPR24_43TC_EXCLUIDA | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SE-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-24 | GPR24 | Proteção 26/49 - Incluida | R1SE-31 | 0 | 0 | 0 | 0 | 0 | 0 | ALGPR24_26_49_INCLUIDA | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SE-32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-1 | BC1 | Defeito Relé | R1SF-1 | 0 | 0 | 0 | 0 | 0 | 0 | BC1_DEFEITO_RELE_19F1 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-2 | BC2 | Defeito Relé | R1SF-2 | 0 | 0 | 0 | 0 | 0 | 0 | BC2_DEFEITO_RELE_22F1 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-3 | GPR21 | Defeito Relé | R1SF-3 | 0 | 0 | 0 | 0 | 0 | 0 | ALGPR21_DEFEITO_RELE | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-4 | GPR22 | Defeito Relé | R1SF-4 | 0 | 0 | 0 | 0 | 0 | 0 | ALGPR22_DEFEITO_RELE | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-5 | GPR31 | Defeito Relé | R1SF-5 | 0 | 0 | 0 | 0 | 0 | 0 | ALGPR31_DEFEITO_RELE_11F1 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-6 | GPR32 | Defeito Relé | R1SF-6 | 0 | 0 | 0 | 0 | 0 | 0 | ALGPR32_DEFEITO_RELE_10F1 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-7 | GPR33 | Defeito Relé | R1SF-7 | 0 | 0 | 0 | 0 | 0 | 0 | ALGPR33_DEFEITO_RELE_09F1 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-8 | GPR34 | Defeito Relé | R1SF-8 | 0 | 0 | 0 | 0 | 0 | 0 | ALGPR34_DEFEITO_RELE_08F1 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-9 | GPR35 | Defeito Relé | R1SF-9 | 0 | 0 | 0 | 0 | 0 | 0 | ALGPR35_DEFEITO_RELE_07F1 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SF-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-10 | GPR36 | Defeito Relé | R1SF-11 | 0 | 0 | 0 | 0 | 0 | 0 | ALGPR36_DEFEITO_RELE_06F1 | 283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SF-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-11 | IB23 | Defeito Relé | R1SF-13 | 0 | 0 | 0 | 0 | 0 | 0 | IB23_DEFEITO_RELE_14F1 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SF-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-12 | SE | 0 | R1SF-15 | 0 | 0 | 0 | 0 | 0 | 0 | SE_PORTA_SAL_COM_ALARME | 1090 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SF-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-13 | SA | 0 | R1SF-17 | 0 | 0 | 0 | 0 | 0 | 0 | SA_CA_RET_ALARME | 1091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-14 | SA | 0 | R1SF-18 | 0 | 0 | 0 | 0 | 0 | 0 | SACA_FALTA_FASE | 1092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-15 | 0 | Reserva | R1SF-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-16 | 0 | Reserva | R1SF-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-17 | 0 | Reserva | R1SF-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-18 | 0 | Reserva | R1SF-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-19 | 0 | Reserva | R1SF-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-20 | 0 | Reserva | R1SF-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-21 | 0 | Reserva | R1SF-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SF-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-22 | 0 | Reserva | R1SF-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SF-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-23 | 0 | Reserva | R1SF-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SF-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI-24 | 0 | Reserva | R1SF-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COMUM (-) CC CONTATOS | 0 | R1SF-32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7SJ632(End.: 1Ch) | GPR21 | Disj. 52-13 (21QA) - Aberto | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | GPR21_DJ_ABERTO | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Disj. 52-13 (21QA) - Fechado | 2 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | GPR21_DJ_FECHADO | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Disj.- Mola descarregada | 3 | 0 | 0 | DiVal | 240 | 191 | 1899-12-31 | GPR21_DJ_MOLA_DESC | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Disj.- Falta VCC Comando | 4 | 0 | 0 | DiVal | 240 | 192 | 1899-12-31 | GPR21_DJ_FVCC_COMANDO | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Disj.- Falta VCC Motor | 5 | 0 | 0 | DiVal | 240 | 193 | 1899-12-31 | GPR21_DJ_FVCC_MOTOR | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Disj.- Chave 43L/R em posição LOCAL | 6 | 0 | 0 | DiVal | 240 | 194 | 1899-12-31 | GPR21_DJ_43LR_LOCAL | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Disj.- Sup.Circuito de Abertura | 7 | 0 | 0 | DiVal | 170 | 56 | 1899-12-31 | GPR21_DJ_CIRC_TRIP_ALM | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Reserva | 8 - 15 | 0 | 0 | - | - | - | - | Reserva | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | TRIP de desligamento p/26/49 TR3 - Atuado | 16 | 4 | 0 | - | - | - | - | INTERTRAVAMENTO! | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Reserva | 17 - 20 | 0 | 0 | - | - | - | - | Reserva | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | TRIP de desligamento p/26/49 TR3 - Atuado | 21 | 4 | 0 | - | - | - | - | INTERTRAVAMENTO! | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Rele 86FD-TR2 - Atuado | 22 | 0 | 0 | - | - | - | - | INTERTRAVAMENTO! | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | TRIP de desligamento p/26/49 TR3 - Atuado | 23 | 4 | 0 | - | - | - | - | INTERTRAVAMENTO! | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Reserva | 24 | 0 | 0 | - | - | - | - | Reserva | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Telecomando (43TC) - Excluído | 0 | 0 | 0 | DiVal | 101 | 85 | 1899-12-31 | GPR21_43TC_EXCLUIDA | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 26/49 - Incluida | 0 | 0 | 0 | DiVal | 240 | 198 | 1899-12-31 | GPR21_43RC_INCLUIDA | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Grupo de Ajuste B Ativo - (51N Excluido) | 0 | 0 | 0 | DiVal | 240 | 199 | 1899-12-31 | GPR21_GRPB_ATIVADO | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Religamento - Disparo | 0 | 5 | 0 | AF | 160 | 128 | 1900-01-01 | GPR21_79_DISPARO | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Religamento - Excluído | 0 | 0 | 0 | DiVal | 40 | 81 | 1899-12-31 | GPR21_79_EXCLUIDO | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Religamento - Sucedido | 0 | 0 | 0 | DiVal | 40 | 162 | 1899-12-31 | GPR21_79_SUCEDIDO | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Religamento - Bloqueado | 0 | 0 | 0 | FDI | 40 | 163 | 1900-01-01 | GPR21_79_BLOQUEADO | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 50BF - Atuado | 0 | 15 | 0 | AF | 160 | 85 | 1900-01-01 | GPR21_50BF_ATUADO | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 50 ABC - Estágio 1 - Atuado | 0 | 4 | 0 | AF | 160 | 90 | 1900-01-01 | GPR21_50ABC_E1_ATUADO | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 50 ABC - Estágio 2 - Atuado | 0 | 4 | 0 | AF | 160 | 91 | 1900-01-01 | GPR21_50ABC_E2_ATUADO | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 50 N - Estágio 1 - Atuado | 0 | 4 | 0 | AF | 160 | 92 | 1900-01-01 | GPR21_50N_E1_ATUADO | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 50 N - Estágio 2 - Atuado | 0 | 4 | 0 | AF | 160 | 93 | 1900-01-01 | GPR21_50N_E2_ATUADO | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 50/51 Fase A - Atuado | 0 | 4 | 0 | FDI | 60 | 54 | 1900-01-01 | GPR21_50FA_51FA_ATUADO | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 50/51 Fase B - Atuado | 0 | 4 | 0 | FDI | 60 | 55 | 1900-01-01 | GPR21_50FB_51FB_ATUADO | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 50/51 Fase C - Atuado | 0 | 4 | 0 | FDI | 60 | 56 | 1900-01-01 | GPR21_50FC_51FC_ATUADO | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 51 ABC - Atuado | 0 | 4 | 0 | FDI | 60 | 58 | 1900-01-01 | GPR21_51ABC_ATUADO | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 51 N - Atuado | 0 | 4 | 0 | FDI | 60 | 66 | 1900-01-01 | GPR21_51N_ATUADO | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Sequência Negativa - Atuado | 0 | 4 | 0 | FDI | 70 | 149 | 1900-01-01 | GPR21_46_ATUADO | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Sub/Sobre Frequencia - Estágio 1 - Atuado | 0 | 4 | 0 | FDI | 70 | 234 | 1900-01-01 | GPR21_81_E1_ATUADO | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Sub/Sobre Frequencia - Estágio 2 - Atuado | 0 | 4 | 0 | FDI | 70 | 235 | 1900-01-01 | GPR21_81_E2_ATUADO | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Falta Sensitiva à Terra - Estágio 1 - Atuado | 0 | 4 | 0 | FDI | 151 | 126 | 1900-01-01 | GPR21_50Ns_E1_ATUADO | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Falta Sensitiva à Terra - Estágio 2 - Atuado | 0 | 4 | 0 | FDI | 151 | 123 | 1900-01-01 | GPR21_50Ns_E2_ATUADO | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 27 - Atuada | 0 | 4 | 0 | FDi | 74 | 81 | 1900-01-01 | GPR21_27_ATUADO | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Proteção 59 - Atuada | 0 | 4 | 0 | FDi | 74 | 83 | 1900-01-01 | GPR21_59_ATUADO | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Saude Comunicação | 0 | 0 | 0 | - | - | - | - | GPR21_SAUDE_COMUNIC | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Disjuntor 52-12 Aberto | 0 | 0 | 0 | DiSOE | 0 | 1 | 1899-12-31 | GPR22_DJ_ABERTO | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Disjuntor 52-12 Fechado | 0 | 0 | 0 | DiSOE | 0 | 1 | 0 | GPR22_DJ_FECHADO | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Disj.- Falta VCA Aux.(1) | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-20 | GPR22_FALTA_VCA | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Religador - Bloqueado (1) | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-01 | GPR22_79_BLOQUEADO | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Dis.- Falta VCC/Anormal Baterias(1) | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-21 | GPR22_FALTA_VCC | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | 43TC - Excluida | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-03-04 | GPR22_43TC_EXCLUIDA | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | 26/49 Rejeição de Carga - Incluída | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-03-05 | GPR22_43TE_INCLUIDA | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Supervisão - Bloqueada (1) | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-04 | GPR22_43LR_POS_LOCAL | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Religador -Excluído (1) | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-05 | GPR22_79_EXCLUIDO | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | 50N/51N - Excluído (1) | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-06 | GPR22_PN_EXCLUIDA | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | 50BF Atuado | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-03-03 | GPR22_50BF_ATUADO | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Atuado SGF | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-02-13 | GPR22_SGF_ATUADA | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Atuado 50N/51 N | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-02-12 | GPR22_50N_51N_ATUADA | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Atuado 50/51-C | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-02-11 | GPR22_50FC_51FC_ATUADA | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Atuado 50/51-B | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-02-10 | GPR22_50FB_51FB_ATUADA | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Atuado 50/51-A | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-02-09 | GPR22_50FA_51FA_ATUADA | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Atuado 81-1 | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-03-06 | GPR22_81_1_ATUADO | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Atuado 81-2 | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-03-07 | GPR22_81_2_ATUADO | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Perfil Normal - Ativado | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-10 | GPR22_PERF0_ATIVADO | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Perfil Alternativo 1 - Ativado | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-11 | GPR22_PERF1_ATIVADO | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Saude Comunicação | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GPR22_SAUDE_COMUNIC | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | Disjuntor 52-11 ABERTO | 0 | 0 | 0 | DiSOE | 0 | 1 | 0 | GPR23_DJ_ABERTO | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | Disjuntor 52-11 FECHADO | 0 | 0 | 0 | DiSOE | 0 | 1 | 1899-12-31 | GPR23_DJ_FECHADO | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | Chave 43LR LOCAL | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-01 | GPR23_43LR_POS_LOCAL | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | 79 Bloqueado | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-07 | GPR23_79_BLOQUEADO | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | Falta CA do Motor do DJ 52-11 | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-08 | GPR23_FALTA_VCA | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | Falta CC Disjuntor 52-11 | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-11 | GPR23_FALTA_VCC | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | 51N - Excluído | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-22 | GPR23_PN_EXCLUIDA | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | 79 - Excluido | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-24 | GPR23_79_EXCLUIDO | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | 50/51 Fase A Atuado | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-26 | GPR23_50FA_51FA_ATUADA | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | 50/51 Fase B Atuado | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-27 | GPR23_50FB_51FB_ATUADA | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | 50/51 Fase C Atuado | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-28 | GPR23_50FC_51FC_ATUADA | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | 50N/51N Atuado | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-29 | GPR23_50N_51N_ATUADA | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | Falta Sensitiva a Terra Estágio 1 | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-30 | GPR23_SGF_ATUADA | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | GPR AL23 Modo Normal | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-31 | GPR23_PERF0_ATIVADO | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | GPR AL23 Modo Perfil Alternativo 1 | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-02-02 | GPR23_PERF1_ATIVADO | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | 81 Estágio 1 Atuado | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-02-13 | GPR23_81_E1_ATUADA | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | 81 Estágio 2 Atuado | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-02-14 | GPR23_81_E2_ATUADA | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | Saude Comunicação | 0 | 0 | 0 | DiSOE | 0 | 0 | - | GPR23_SAUDE_COMUNIC | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | Disjuntor 52-10 ABERTO | 0 | 0 | 0 | DiSOE | 0 | 1 | 0 | GPR24_DJ_ABERTO | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | Disjuntor 52-10 FECHADO | 0 | 0 | 0 | DiSOE | 0 | 1 | 1899-12-31 | GPR24_DJ_FECHADO | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | Chave 43LR LOCAL | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-01 | GPR24_43LR_POS_LOCAL | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | 79 Bloqueado | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-07 | GPR24_79_BLOQUEADO | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | Falta CA do Motor do DJ 52-10 | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-08 | GPR24_FALTA_VCA | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | Falta CC Disjuntor 52-10 | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-11 | GPR24_FALTA_VCC | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | 51N - Excluído | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-22 | GPR24_PN_EXCLUIDA | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | 79 - Excluido | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-24 | GPR24_79_EXCLUIDO | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | 50/51 Fase A Atuado | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-26 | GPR24_50FA_51FA_ATUADA | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | 50/51 Fase B Atuado | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-27 | GPR24_50FB_51FB_ATUADA | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | 50/51 Fase C Atuado | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-28 | GPR24_50FC_51FC_ATUADA | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | 50N/51N Atuado | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-29 | GPR24_50N_51N_ATUADA | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | Falta Sensitiva a Terra Estágio 1 | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-30 | GPR24_SGF_ATUADA | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | GPR AL23 Modo Normal | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-01-31 | GPR24_PERF0_ATIVADO | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | GPR AL23 Modo Perfil Alternativo 1 | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-02-02 | GPR24_PERF1_ATIVADO | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | 81 Estágio 1 Atuado | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-02-13 | GPR24_81_E1_ATUADA | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | 81 Estágio 2 Atuado | 0 | 0 | 0 | DiSOE | 0 | 1 | 1900-02-14 | GPR24_81_E2_ATUADA | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | Saude Comunicação | 0 | 0 | 0 | DiSOE | 0 | 0 | - | GPR24_SAUDE_COMUNIC | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7SJ63 (End: 18d/12h) | GPR31 | Disj. 52-09 (11Q0) - Aberto | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | GPR31_DJ_ABERTO | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Disj. 52-09 (11Q0) - Fechado | 2 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | GPR31_DJ_FECHADO | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Disj.- Mola Descarregada | 3 | 0 | 0 | DiVal | 240 | 192 | 1899-12-31 | GPR31_MOLA_DESC | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Disj.- Chave 43LR em posição LOCAL | 4 | 0 | 0 | DiVal | 240 | 193 | 1899-12-31 | GPR31_43LR_LOCAL | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Disj.- Sup.Circuito de Abertura | 7 | 0 | 0 | DiVal | 170 | 56 | 1899-12-31 | GPR31_CIRC_TRIP_FALHADO | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 26/49 TR3 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 22 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 86FD/Barra P1 - Atuado (TRIP e Bloqueio DJ) | 8 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 26/49 TR2 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 16 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 86T3 - Atuado (TRIP e Bloqueio DJ) | 21 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Reserva | 0 | 0 | 0 | - | - | - | - | Reserva | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Telecomando (43TC) - Excluído | 0 | 0 | 0 | DiVal | 101 | 85 | 1899-12-31 | GPR31_43TC_EXCLUIDA | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Grupo de Ajustes B - Ativado (51N Excluido) | 0 | 0 | 0 | DiVal | 160 | 24 | 1899-12-31 | GPR31_GRPB_ATIVADO | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Chave 26/49 (Rejeição de Carga) - Incluida | 0 | 0 | 0 | DiVal | 240 | 196 | 1899-12-31 | GPR31_43RC_INCLUIDA | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 79 - Disparo | 0 | 0 | 0 | AF | 160 | 128 | 1900-01-01 | GPR31_79_DISPARO | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 79 - Excluído | 0 | 0 | 0 | DiVal | 40 | 81 | 1899-12-31 | GPR31_79_EXCLUIDO | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 79 - Sucedido | 0 | 0 | 0 | DiVal | 40 | 162 | 1899-12-31 | GPR31_RELIGAM_SUCEDIDO | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 79 - Bloqueado | 0 | 0 | 0 | FDI | 40 | 163 | 1900-01-01 | GPR31_79_BLOQUEADO | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 50BF - Atuado | 0 | 3 | 0 | AF | 160 | 85 | 1900-01-01 | GPR31_50BF_ATUADO | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 50 ABC - Estágio 1 - Atuado | 0 | 4 | 0 | AF | 160 | 90 | 1900-01-01 | GPR31_50_E1_ATUADO | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 50 ABC - Estágio 2 - Atuado | 0 | 4 | 0 | AF | 160 | 91 | 1900-01-01 | GPR31_50_E2_ATUADO | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 50 N - Estágio 1 - Atuado | 0 | 4 | 0 | AF | 160 | 92 | 1900-01-01 | GPR31_50N_E1_ATUADO | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 50 N - Estágio 2 - Atuado | 0 | 4 | 0 | AF | 160 | 93 | 1900-01-01 | GPR31_50N_E2_ATUADO | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 50/51 Fase A - Atuado | 0 | 0 | 0 | FDI | 60 | 54 | 1900-01-01 | GPR31_50FA_51FA_ATUADO | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 50/51 Fase B - Atuado | 0 | 0 | 0 | FDI | 60 | 55 | 1900-01-01 | GPR31_50FB_51FB_ATUADO | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 50/51 Fase C - Atuado | 0 | 0 | 0 | FDI | 60 | 56 | 1900-01-01 | GPR31_50FC_51FC_ATUADO | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 51 ABC - Atuado | 0 | 4 | 0 | FDI | 60 | 58 | 1900-01-01 | GPR31_51ABC_ATUADO | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 51 N - Atuado | 0 | 4 | 0 | FDI | 60 | 66 | 1900-01-01 | GPR31_51N_ATUADO | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 46 (Sequência Negativa) - Atuado | 0 | 4 | 0 | FDI | 70 | 149 | 1900-01-01 | GPR31_46_ATUADO | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 81 (Sub/Sobre Frequencia) - Estágio 1 - Atuado | 0 | 4 | 0 | FDI | 70 | 234 | 1900-01-01 | GPR31_81_E1_ATUADO | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 81 (Sub/Sobre Frequencia) - Estágio 2 - Atuado | 0 | 4 | 0 | FDI | 70 | 235 | 1900-01-01 | GPR31_81_E2_ATUADO | 124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 50Ns (Falta Sensitiva à Terra) - Estágio 1 - Atuado | 0 | 4 | 0 | FDI | 151 | 126 | 1900-01-01 | GPR31_50Ns_E1_ATUADO | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | 50Ns (Falta Sensitiva à Terra) - Estágio 2 - Atuado | 0 | 4 | 0 | FDI | 151 | 123 | 1900-01-01 | GPR31_50Ns_E2_ATUADO | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Saude Comunicação | 0 | 0 | 0 | - | - | - | - | GPR31_SAUDE_COMUNIC | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Disj. 24-01 (11Q0) - Aberto | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | GPR32_DJ_ABERTO | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Disj. 24-01 (11Q0) - Fechado | 2 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | GPR32_DJ_FECHADO | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Disj.- Mola Descarregada | 3 | 0 | 0 | DiVal | 240 | 192 | 1899-12-31 | GPR32_MOLA_DESC | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Disj.- Chave 43LR em posição LOCAL | 4 | 0 | 0 | DiVal | 240 | 193 | 1899-12-31 | GPR32_43LR_LOCAL | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Disj.- Sup.Circuito de Abertura | 7 | 0 | 0 | DiVal | 170 | 56 | 1899-12-31 | GPR32_CIRC_TRIP_FALHADO | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 26/49 TR3 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 22 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 86FD/Barra P1 - Atuado (TRIP e Bloqueio DJ) | 8 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 26/49 TR2 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 16 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 86T3 - Atuado (TRIP e Bloqueio DJ) | 21 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Reserva | 0 | 0 | 0 | - | - | - | - | Reserva | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Disj.- Falta Vcc Comando | ? | 0 | 0 | DiVal | 240 | 194 | 1899-12-31 | ALGPR32_FVCC_COMANDO | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Disj.- Falta Vca Aquecimento | ? | 0 | 0 | DiVal | 240 | 195 | 1899-12-31 | ALGPR32_FVCA_AQUECIMENT | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Telecomando (43TC) - Excluído | 0 | 0 | 0 | DiVal | 101 | 85 | 1899-12-31 | GPR32_43TC_EXCLUIDA | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Grupo de Ajustes B - Ativado (51N Excluido) | 0 | 0 | 0 | DiVal | 160 | 24 | 1899-12-31 | GPR32_GRPB_ATIVADO | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Chave 26/49 (Rejeição de Carga) - Incluida | 0 | 0 | 0 | DiVal | 240 | 196 | 1899-12-31 | GPR32_43RC_INCLUIDA | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 79 - Disparo | 0 | 0 | 0 | AF | 160 | 128 | 1900-01-01 | GPR32_79_DISPARO | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 79 - Excluído | 0 | 0 | 0 | DiVal | 40 | 81 | 1899-12-31 | GPR32_79_EXCLUIDO | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 79 - Sucedido | 0 | 0 | 0 | DiVal | 40 | 162 | 1899-12-31 | GPR32_RELIGAM_SUCEDIDO | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 79 - Bloqueado | 0 | 0 | 0 | FDI | 40 | 163 | 1900-01-01 | GPR32_79_BLOQUEADO | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 50BF - Atuado | 0 | 3 | 0 | AF | 160 | 85 | 1900-01-01 | GPR32_50BF_ATUADO | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 50 ABC - Estágio 1 - Atuado | 0 | 4 | 0 | AF | 160 | 90 | 1900-01-01 | GPR32_50_E1_ATUADO | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 50 ABC - Estágio 2 - Atuado | 0 | 4 | 0 | AF | 160 | 91 | 1900-01-01 | GPR32_50_E2_ATUADO | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 50 N - Estágio 1 - Atuado | 0 | 4 | 0 | AF | 160 | 92 | 1900-01-01 | GPR32_50N_E1_ATUADO | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 50 N - Estágio 2 - Atuado | 0 | 4 | 0 | AF | 160 | 93 | 1900-01-01 | GPR32_50N_E2_ATUADO | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 50/51 Fase A - Atuado | 0 | 0 | 0 | FDI | 60 | 54 | 1900-01-01 | GPR32_50FA_51FA_ATUADO | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 50/51 Fase B - Atuado | 0 | 0 | 0 | FDI | 60 | 55 | 1900-01-01 | GPR32_50FB_51FB_ATUADO | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 50/51 Fase C - Atuado | 0 | 0 | 0 | FDI | 60 | 56 | 1900-01-01 | GPR32_50FC_51FC_ATUADO | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 51 ABC - Atuado | 0 | 4 | 0 | FDI | 60 | 58 | 1900-01-01 | GPR32_51ABC_ATUADO | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 51 N - Atuado | 0 | 4 | 0 | FDI | 60 | 66 | 1900-01-01 | GPR32_51N_ATUADO | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 46 (Sequência Negativa) - Atuado | 0 | 4 | 0 | FDI | 70 | 149 | 1900-01-01 | GPR32_46_ATUADO | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 81 (Sub/Sobre Frequencia) - Estágio 1 - Atuado | 0 | 4 | 0 | FDI | 70 | 234 | 1900-01-01 | GPR32_81_E1_ATUADO | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 81 (Sub/Sobre Frequencia) - Estágio 2 - Atuado | 0 | 4 | 0 | FDI | 70 | 235 | 1900-01-01 | GPR32_81_E2_ATUADO | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 50Ns (Falta Sensitiva à Terra) - Estágio 1 - Atuado | 0 | 4 | 0 | FDI | 151 | 126 | 1900-01-01 | GPR32_50Ns_E1_ATUADO | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | 50Ns (Falta Sensitiva à Terra) - Estágio 2 - Atuado | 0 | 4 | 0 | FDI | 151 | 123 | 1900-01-01 | GPR32_50Ns_E2_ATUADO | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Saude Comunicação | 0 | 0 | 0 | - | - | - | - | GPR32_SAUDE_COMUNIC | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Disj. 52-08 (09Q0) - Aberto | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | GPR33_DJ_ABERTO | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Disj. 52-08 (09Q0) - Fechado | 2 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | GPR33_DJ_FECHADO | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Disj.- Mola Descarregada | 3 | 0 | 0 | DiVal | 240 | 192 | 1899-12-31 | GPR33_MOLA_DESC | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Disj.- Chave 43LR em posição LOCAL | 4 | 0 | 0 | DiVal | 240 | 193 | 1899-12-31 | GPR33_43LR_LOCAL | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Disj.- Sup.Circuito de Abertura | 7 | 0 | 0 | DiVal | 170 | 56 | 1899-12-31 | GPR33_CIRC_TRIP_FALHADO | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 26/49 TR3 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 22 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 86FD/Barra P1 - Atuado (TRIP e Bloqueio DJ) | 8 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 26/49 TR2 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 16 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 86T3 - Atuado (TRIP e Bloqueio DJ) | 21 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Reserva | 0 | 0 | 0 | - | - | - | - | Reserva | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Telecomando (43TC) - Excluído | 0 | 0 | 0 | DiVal | 101 | 85 | 1899-12-31 | GPR33_43TC_EXCLUIDA | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Grupo de Ajustes B - Ativado (51N Excluido) | 0 | 0 | 0 | DiVal | 160 | 24 | 1899-12-31 | GPR33_GRPB_ATIVADO | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Chave 26/49 (Rejeição de Carga) - Incluida | 0 | 0 | 0 | DiVal | 240 | 196 | 1899-12-31 | GPR33_43RC_INCLUIDA | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 79 - Disparo | 0 | 0 | 0 | AF | 160 | 128 | 1900-01-01 | GPR33_79_DISPARO | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 79 - Excluído | 0 | 0 | 0 | DiVal | 40 | 81 | 1899-12-31 | GPR33_79_EXCLUIDO | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 79 - Sucedido | 0 | 0 | 0 | DiVal | 40 | 162 | 1899-12-31 | GPR33_RELIGAM_SUCEDIDO | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 79 - Bloqueado | 0 | 0 | 0 | FDI | 40 | 163 | 1900-01-01 | GPR33_79_BLOQUEADO | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 50BF - Atuado | 0 | 3 | 0 | AF | 160 | 85 | 1900-01-01 | GPR33_50BF_ATUADO | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 50 ABC - Estágio 1 - Atuado | 0 | 4 | 0 | AF | 160 | 90 | 1900-01-01 | GPR33_50_E1_ATUADO | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 50 ABC - Estágio 2 - Atuado | 0 | 4 | 0 | AF | 160 | 91 | 1900-01-01 | GPR33_50_E2_ATUADO | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 50 N - Estágio 1 - Atuado | 0 | 4 | 0 | AF | 160 | 92 | 1900-01-01 | GPR33_50N_E1_ATUADO | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 50 N - Estágio 2 - Atuado | 0 | 4 | 0 | AF | 160 | 93 | 1900-01-01 | GPR33_50N_E2_ATUADO | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 50/51 Fase A - Atuado | 0 | 0 | 0 | FDI | 60 | 54 | 1900-01-01 | GPR33_50FA_51FA_ATUADO | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 50/51 Fase B - Atuado | 0 | 0 | 0 | FDI | 60 | 55 | 1900-01-01 | GPR33_50FB_51FB_ATUADO | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 50/51 Fase C - Atuado | 0 | 0 | 0 | FDI | 60 | 56 | 1900-01-01 | GPR33_50FC_51FC_ATUADO | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 51 ABC - Atuado | 0 | 4 | 0 | FDI | 60 | 58 | 1900-01-01 | GPR33_51ABC_ATUADO | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 51 N - Atuado | 0 | 4 | 0 | FDI | 60 | 66 | 1900-01-01 | GPR33_51N_ATUADO | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 46 (Sequência Negativa) - Atuado | 0 | 4 | 0 | FDI | 70 | 149 | 1900-01-01 | GPR33_46_ATUADO | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 81 (Sub/Sobre Frequencia) - Estágio 1 - Atuado | 0 | 4 | 0 | FDI | 70 | 234 | 1900-01-01 | GPR33_81_E1_ATUADO | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 81 (Sub/Sobre Frequencia) - Estágio 2 - Atuado | 0 | 4 | 0 | FDI | 70 | 235 | 1900-01-01 | GPR33_81_E2_ATUADO | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 50Ns (Falta Sensitiva à Terra) - Estágio 1 - Atuado | 0 | 4 | 0 | FDI | 151 | 126 | 1900-01-01 | GPR33_50Ns_E1_ATUADO | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | 50Ns (Falta Sensitiva à Terra) - Estágio 2 - Atuado | 0 | 4 | 0 | FDI | 151 | 123 | 1900-01-01 | GPR33_50Ns_E2_ATUADO | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Saude Comunicação | 0 | 0 | 0 | - | - | - | - | GPR33_SAUDE_COMUNIC | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Disj. 52-07(08Q0) - Aberto | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | GPR34_DJ_ABERTO | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Disj. 52-07(08Q0) - Fechado | 2 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | GPR34_DJ_FECHADO | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Disj.- Mola Descarregada | 3 | 0 | 0 | DiVal | 240 | 192 | 1899-12-31 | GPR34_MOLA_DESC | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Disj.- Chave 43LR em posição LOCAL | 4 | 0 | 0 | DiVal | 240 | 193 | 1899-12-31 | GPR34_43LR_LOCAL | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Disj.- Sup.Circuito de Abertura | 7 | 0 | 0 | DiVal | 170 | 56 | 1899-12-31 | GPR34_CIRC_TRIP_FALHADO | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 26/49 TR3 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 22 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 86FD/Barra P1 - Atuado (TRIP e Bloqueio DJ) | 8 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 26/49 TR2 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 16 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 86T3 - Atuado (TRIP e Bloqueio DJ) | 21 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Reserva | 0 | 0 | 0 | - | - | - | - | Reserva | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Telecomando (43TC) - Excluído | 0 | 0 | 0 | DiVal | 101 | 85 | 1899-12-31 | GPR34_43TC_EXCLUIDA | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Grupo de Ajustes B - Ativado (51N Excluido) | 0 | 0 | 0 | DiVal | 160 | 24 | 1899-12-31 | GPR34_GRPB_ATIVADO | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Chave 26/49 (Rejeição de Carga) - Incluida | 0 | 0 | 0 | DiVal | 240 | 196 | 1899-12-31 | GPR34_43RC_INCLUIDA | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 79 - Disparo | 0 | 0 | 0 | AF | 160 | 128 | 1900-01-01 | GPR34_79_DISPARO | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 79 - Excluído | 0 | 0 | 0 | DiVal | 40 | 81 | 1899-12-31 | GPR34_79_EXCLUIDO | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 79 - Sucedido | 0 | 0 | 0 | DiVal | 40 | 162 | 1899-12-31 | GPR34_RELIGAM_SUCEDIDO | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 79 - Bloqueado | 0 | 0 | 0 | FDI | 40 | 163 | 1900-01-01 | GPR34_79_BLOQUEADO | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 50BF - Atuado | 0 | 3 | 0 | AF | 160 | 85 | 1900-01-01 | GPR34_50BF_ATUADO | 207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 50 ABC - Estágio 1 - Atuado | 0 | 4 | 0 | AF | 160 | 90 | 1900-01-01 | GPR34_50_E1_ATUADO | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 50 ABC - Estágio 2 - Atuado | 0 | 4 | 0 | AF | 160 | 91 | 1900-01-01 | GPR34_50_E2_ATUADO | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 50 N - Estágio 1 - Atuado | 0 | 4 | 0 | AF | 160 | 92 | 1900-01-01 | GPR34_50N_E1_ATUADO | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 50 N - Estágio 2 - Atuado | 0 | 4 | 0 | AF | 160 | 93 | 1900-01-01 | GPR34_50N_E2_ATUADO | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 50/51 Fase A - Atuado | 0 | 0 | 0 | FDI | 60 | 54 | 1900-01-01 | GPR34_50FA_51FA_ATUADO | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 50/51 Fase B - Atuado | 0 | 0 | 0 | FDI | 60 | 55 | 1900-01-01 | GPR34_50FB_51FB_ATUADO | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 50/51 Fase C - Atuado | 0 | 0 | 0 | FDI | 60 | 56 | 1900-01-01 | GPR34_50FC_51FC_ATUADO | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 51 ABC - Atuado | 0 | 4 | 0 | FDI | 60 | 58 | 1900-01-01 | GPR34_51ABC_ATUADO | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 51 N - Atuado | 0 | 4 | 0 | FDI | 60 | 66 | 1900-01-01 | GPR34_51N_ATUADO | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 46 (Sequência Negativa) - Atuado | 0 | 4 | 0 | FDI | 70 | 149 | 1900-01-01 | GPR34_46_ATUADO | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 81 (Sub/Sobre Frequencia) - Estágio 1 - Atuado | 0 | 4 | 0 | FDI | 70 | 234 | 1900-01-01 | GPR34_81_E1_ATUADO | 218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 81 (Sub/Sobre Frequencia) - Estágio 2 - Atuado | 0 | 4 | 0 | FDI | 70 | 235 | 1900-01-01 | GPR34_81_E2_ATUADO | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 50Ns (Falta Sensitiva à Terra) - Estágio 1 - Atuado | 0 | 4 | 0 | FDI | 151 | 126 | 1900-01-01 | GPR34_50Ns_E1_ATUADO | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | 50Ns (Falta Sensitiva à Terra) - Estágio 2 - Atuado | 0 | 4 | 0 | FDI | 151 | 123 | 1900-01-01 | GPR34_50Ns_E2_ATUADO | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Saude Comunicação | 0 | 0 | 0 | - | - | - | - | GPR34_SAUDE_COMUNIC | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Disj. 52-06 (07Q0) - Aberto | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | GPR35_DJ_ABERTO | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Disj. 52-06 (07Q0) - Fechado | 2 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | GPR35_DJ_FECHADO | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Disj.- Mola Descarregada | 3 | 0 | 0 | DiVal | 240 | 192 | 1899-12-31 | GPR35_MOLA_DESC | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Disj.- Chave 43LR em posição LOCAL | 4 | 0 | 0 | DiVal | 240 | 193 | 1899-12-31 | GPR35_43LR_LOCAL | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Disj.- Sup.Circuito de Abertura | 7 | 0 | 0 | DiVal | 170 | 56 | 1899-12-31 | GPR35_CIRC_TRIP_FALHADO | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 26/49 TR3 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 22 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 86FD/Barra P1 - Atuado (TRIP e Bloqueio DJ) | 8 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 26/49 TR2 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 16 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 86T3 - Atuado (TRIP e Bloqueio DJ) | 21 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Reserva | 0 | 0 | 0 | - | - | - | - | Reserva | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Telecomando (43TC) - Excluído | 0 | 0 | 0 | DiVal | 101 | 85 | 1899-12-31 | GPR35_43TC_EXCLUIDA | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Grupo de Ajustes B - Ativado (51N Excluido) | 0 | 0 | 0 | DiVal | 160 | 24 | 1899-12-31 | GPR35_GRPB_ATIVADO | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Chave 26/49 (Rejeição de Carga) - Incluida | 0 | 0 | 0 | DiVal | 240 | 196 | 1899-12-31 | GPR35_43RC_INCLUIDA | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 79 - Disparo | 0 | 0 | 0 | AF | 160 | 128 | 1900-01-01 | GPR35_79_DISPARO | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 79 - Excluído | 0 | 0 | 0 | DiVal | 40 | 81 | 1899-12-31 | GPR35_79_EXCLUIDO | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 79 - Sucedido | 0 | 0 | 0 | DiVal | 40 | 162 | 1899-12-31 | GPR35_RELIGAM_SUCEDIDO | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 79 - Bloqueado | 0 | 0 | 0 | FDI | 40 | 163 | 1900-01-01 | GPR35_79_BLOQUEADO | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 50BF - Atuado | 0 | 3 | 0 | AF | 160 | 85 | 1900-01-01 | GPR35_50BF_ATUADO | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 50 ABC - Estágio 1 - Atuado | 0 | 4 | 0 | AF | 160 | 90 | 1900-01-01 | GPR35_50_E1_ATUADO | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 50 ABC - Estágio 2 - Atuado | 0 | 4 | 0 | AF | 160 | 91 | 1900-01-01 | GPR35_50_E2_ATUADO | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 50 N - Estágio 1 - Atuado | 0 | 4 | 0 | AF | 160 | 92 | 1900-01-01 | GPR35_50N_E1_ATUADO | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 50 N - Estágio 2 - Atuado | 0 | 4 | 0 | AF | 160 | 93 | 1900-01-01 | GPR35_50N_E2_ATUADO | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 50/51 Fase A - Atuado | 0 | 0 | 0 | FDI | 60 | 54 | 1900-01-01 | GPR35_50FA_51FA_ATUADO | 242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 50/51 Fase B - Atuado | 0 | 0 | 0 | FDI | 60 | 55 | 1900-01-01 | GPR35_50FB_51FB_ATUADO | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 50/51 Fase C - Atuado | 0 | 0 | 0 | FDI | 60 | 56 | 1900-01-01 | GPR35_50FC_51FC_ATUADO | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 51 ABC - Atuado | 0 | 4 | 0 | FDI | 60 | 58 | 1900-01-01 | GPR35_51ABC_ATUADO | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 51 N - Atuado | 0 | 4 | 0 | FDI | 60 | 66 | 1900-01-01 | GPR35_51N_ATUADO | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 46 (Sequência Negativa) - Atuado | 0 | 4 | 0 | FDI | 70 | 149 | 1900-01-01 | GPR35_46_ATUADO | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 81 (Sub/Sobre Frequencia) - Estágio 1 - Atuado | 0 | 4 | 0 | FDI | 70 | 234 | 1900-01-01 | GPR35_81_E1_ATUADO | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 81 (Sub/Sobre Frequencia) - Estágio 2 - Atuado | 0 | 4 | 0 | FDI | 70 | 235 | 1900-01-01 | GPR35_81_E2_ATUADO | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 50Ns (Falta Sensitiva à Terra) - Estágio 1 - Atuado | 0 | 4 | 0 | FDI | 151 | 126 | 1900-01-01 | GPR35_50Ns_E1_ATUADO | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | 50Ns (Falta Sensitiva à Terra) - Estágio 2 - Atuado | 0 | 4 | 0 | FDI | 151 | 123 | 1900-01-01 | GPR35_50Ns_E2_ATUADO | 251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Saude Comunicação | 0 | 0 | 0 | - | - | - | - | GPR35_SAUDE_COMUNIC | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Disj. 52-05 (06Q0) - Aberto | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | GPR36_DJ_ABERTO | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Disj. 52-05 (06Q0) - Fechado | 2 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | GPR36_DJ_FECHADO | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Disj.- Mola Descarregada | 3 | 0 | 0 | DiVal | 240 | 192 | 1899-12-31 | GPR36_MOLA_DESC | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Disj.- Chave 43LR em posição LOCAL | 4 | 0 | 0 | DiVal | 240 | 193 | 1899-12-31 | GPR36_43LR_LOCAL | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Disj.- Sup.Circuito de Abertura | 7 | 0 | 0 | DiVal | 170 | 56 | 1899-12-31 | GPR36_CIRC_TRIP_FALHADO | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 26/49 TR3 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 22 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 86FD/Barra P1 - Atuado (TRIP e Bloqueio DJ) | 8 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 26/49 TR2 (Rejeição de Carga) - Atuado (TRIP e Bloqueio DJ) | 16 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 86T3 - Atuado (TRIP e Bloqueio DJ) | 21 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Reserva | 0 | 0 | 0 | - | - | - | - | Reserva | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Telecomando (43TC) - Excluído | 0 | 0 | 0 | DiVal | 101 | 85 | 1899-12-31 | GPR36_43TC_EXCLUIDA | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Grupo de Ajustes B - Ativado (51N Excluido) | 0 | 0 | 0 | DiVal | 160 | 24 | 1899-12-31 | GPR36_GRPB_ATIVADO | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Chave 26/49 (Rejeição de Carga) - Incluida | 0 | 0 | 0 | DiVal | 240 | 196 | 1899-12-31 | GPR36_43RC_INCLUIDA | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 79 - Disparo | 0 | 0 | 0 | AF | 160 | 128 | 1900-01-01 | GPR36_79_DISPARO | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 79 - Excluído | 0 | 0 | 0 | DiVal | 40 | 81 | 1899-12-31 | GPR36_79_EXCLUIDO | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 79 - Sucedido | 0 | 0 | 0 | DiVal | 40 | 162 | 1899-12-31 | GPR36_RELIGAM_SUCEDIDO | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 79 - Bloqueado | 0 | 0 | 0 | FDI | 40 | 163 | 1900-01-01 | GPR36_79_BLOQUEADO | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 50BF - Atuado | 0 | 3 | 0 | AF | 160 | 85 | 1900-01-01 | GPR36_50BF_ATUADO | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 50 ABC - Estágio 1 - Atuado | 0 | 4 | 0 | AF | 160 | 90 | 1900-01-01 | GPR36_50_E1_ATUADO | 268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 50 ABC - Estágio 2 - Atuado | 0 | 4 | 0 | AF | 160 | 91 | 1900-01-01 | GPR36_50_E2_ATUADO | 269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 50 N - Estágio 1 - Atuado | 0 | 4 | 0 | AF | 160 | 92 | 1900-01-01 | GPR36_50N_E1_ATUADO | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 50 N - Estágio 2 - Atuado | 0 | 4 | 0 | AF | 160 | 93 | 1900-01-01 | GPR36_50N_E2_ATUADO | 271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 50/51 Fase A - Atuado | 0 | 0 | 0 | FDI | 60 | 54 | 1900-01-01 | GPR36_50FA_51FA_ATUADO | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 50/51 Fase B - Atuado | 0 | 0 | 0 | FDI | 60 | 55 | 1900-01-01 | GPR36_50FB_51FB_ATUADO | 273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 50/51 Fase C - Atuado | 0 | 0 | 0 | FDI | 60 | 56 | 1900-01-01 | GPR36_50FC_51FC_ATUADO | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 51 ABC - Atuado | 0 | 4 | 0 | FDI | 60 | 58 | 1900-01-01 | GPR36_51ABC_ATUADO | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 51 N - Atuado | 0 | 4 | 0 | FDI | 60 | 66 | 1900-01-01 | GPR36_51N_ATUADO | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 46 (Sequência Negativa) - Atuado | 0 | 4 | 0 | FDI | 70 | 149 | 1900-01-01 | GPR36_46_ATUADO | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 81 (Sub/Sobre Frequencia) - Estágio 1 - Atuado | 0 | 4 | 0 | FDI | 70 | 234 | 1900-01-01 | GPR36_81_E1_ATUADO | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 81 (Sub/Sobre Frequencia) - Estágio 2 - Atuado | 0 | 4 | 0 | FDI | 70 | 235 | 1900-01-01 | GPR36_81_E2_ATUADO | 279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 50Ns (Falta Sensitiva à Terra) - Estágio 1 - Atuado | 0 | 4 | 0 | FDI | 151 | 126 | 1900-01-01 | GPR36_50Ns_E1_ATUADO | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | 50Ns (Falta Sensitiva à Terra) - Estágio 2 - Atuado | 0 | 4 | 0 | FDI | 151 | 123 | 1900-01-01 | GPR36_50Ns_E2_ATUADO | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Saude Comunicação | 0 | 0 | 0 | - | - | - | - | GPR36_SAUDE_COMUNIC | 282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj. 52-15 (06Q0) - Aberto/Fechado | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | IB23_DJ_ABERTO | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj. 52-15 (06Q0) - Aberto/Fechado | 2 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | IB23_DJ_FECHADO | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj.- Mola Descarregada | 3 | 0 | 0 | DiVal | 240 | 192 | 1899-12-31 | IB23_MOLA_DESC | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj.- Falta VCC de Comando | 4 | 0 | 0 | DiVal | 240 | 195 | 1899-12-31 | IB23_FCC_COMANDO | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj.- Falta VCC Motor | 5 | 0 | 0 | DiVal | 240 | 196 | 1899-12-31 | IB23_FCC_MOTOR | 289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj.- Baixa Pressão SF6 - Estágio 1 - Alarme | 6 | 0 | 0 | DiVal | 240 | 190 | 1899-12-31 | IB23_BP_SF6_ALARME | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj.- Sup.Circuito de Abertura | 7 | 0 | 0 | DiVal | 170 | 56 | 1899-12-31 | IB23_CIRC_TRIP_FALHADO | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Reserva | 8 | 0 | 0 | - | - | - | - | Reserva | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 86FD/TR3 - Atuado (TRIP e Bloqueio DJ) | 9 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 86T3 - Atuado (TRIP e Bloqueio DJ) | 10 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Reserva | 11 | 0 | 0 | - | - | - | - | Reserva | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 86FD/TR2 - Atuado (TRIP e Bloqueio DJ) | 12 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 86T2 - Atuado (TRIP e Bloqueio DJ) | 13 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Reserva | 14-15 | 0 | 0 | - | - | - | - | Reserva | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj.- Baixa Pressão SF6 - Estágio 2 - Desligamento e Bloqueio | 16 | 0 | 0 | DiVal | 240 | 191 | 1899-12-31 | IB23_BP_SF6_BLOQUEIO | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj.- Chave 43LR em posição LOCAL | 17 | 0 | 0 | DiVal | 240 | 193 | 1899-12-31 | IB23_43LR_LOCAL | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj.- Permissão p/FECHAMENTO PARALELISMO TR3 (SPS) | 18 | 0 | 0 | DiVal | 240 | 194 | 1899-12-31 | IB23_PARALEL_TR3_OK | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Secc.89-24 (689D) do TR3/BT - Aberta/Fechada (*) | 19/20 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Disj.- Permissão p/FECHAMENTO PARALELISMO TR2 (SPS) | 22 | 0 | 0 | DiVal | 240 | 197 | 1899-12-31 | IB23_PARALEL_TR2_OK | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Secc.89-62 (689D) do TR2/BT - Aberta/Fechada | 23/24 | 0 | 0 | - | - | - | - | (Só para INTERTRAVAMENTO!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Telecomando (43TC) - Excluído | 0 | 0 | 0 | DiVal | 101 | 85 | 1899-12-31 | IB23_43TC_EXCLUIDA | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Grupo de Ajustes B - Ativado (51N Excluido) | 0 | 0 | 0 | DiVal | 160 | 24 | 1899-12-31 | IB23_GRPB_ATIVADO | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 50BF - Atuado | 0 | 3/10 | 0 | AF | 160 | 85 | 1900-01-01 | IB23_50BF_ATUADO | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 50 ABC - Estágio 1 - Atuado | 0 | 4 | 0 | AF | 160 | 90 | 1900-01-01 | IB23_50_E1_ATUADO | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 50 ABC - Estágio 2 - Atuado | 0 | 4 | 0 | AF | 160 | 91 | 1900-01-01 | IB23_50_E2_ATUADO | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 50 N - Estágio 1 - Atuado | 0 | 4 | 0 | AF | 160 | 92 | 1900-01-01 | IB23_50N_E1_ATUADO | 299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 50 N - Estágio 2 - Atuado | 0 | 4 | 0 | AF | 160 | 93 | 1900-01-01 | IB23_50N_E2_ATUADO | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 50/51 Fase A - Atuado | 0 | 0 | 0 | FDI | 60 | 54 | 1900-01-01 | IB23_50FA_51FA_ATUADO | 301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 50/51 Fase B - Atuado | 0 | 0 | 0 | FDI | 60 | 55 | 1900-01-01 | IB23_50FB_51FB_ATUADO | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 50/51 Fase C - Atuado | 0 | 0 | 0 | FDI | 60 | 56 | 1900-01-01 | IB23_50FC_51FC_ATUADO | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 51 ABC - Atuado | 0 | 4 | 0 | FDI | 60 | 58 | 1900-01-01 | IB23_51ABC_ATUADO | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | 51 N - Atuado | 0 | 4 | 0 | FDI | 60 | 66 | 1900-01-01 | IB23_51N_ATUADO | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Saude Comunicação | 0 | 0 | 0 | - | - | - | - | IB23_SAUDE_COMUNIC | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Disj. 52-19 (06Q0) - Aberto/Fechado | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | BC1_DJ_ABERTO | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Disj. 52-19 (06Q0) - Aberto/Fechado | 2 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | BC1_DJ_FECHADO | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Disj. 52-19 (06Q0) - Mola Descarregada | ? | 0 | 0 | DiVal | 240 | 192 | 1899-12-31 | BC1_DJ_MOLA_DESC | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Disj. 52-19 (06Q0) - Falta Vcc Motor/Comando | ? | 0 | 0 | DiVal | 240 | 195 | 1899-12-31 | BC1_FVCC_COM_MOT | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Disj.- Sup.Circuito de Abertura | 7 | 0 | 0 | DiVal | 170 | 56 | 1899-12-31 | BC1_CIRC_TRIP_FALHADO | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Telecomando (43TC) - Excluído | 0 | 0 | 0 | DiVal | 101 | 85 | 1899-12-31 | BC1_43TC_EXCLUIDA | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | AUTOMATISMO - Incluído | 0 | 0 | 0 | DiVal | 240 | 197 | 1899-12-31 | BC1_AUTOMAT_INCLUIDO | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | AUTOMATISMO - Atuado | 0 | 0 | 0 | DiVal | 240 | 198 | 1899-12-31 | BC1_AUTOMAT_ATUADO | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Disj.52-04 - Fechamento Bloqueado 5 minutos | 0 | 0 | 0 | DiVal | 240 | 199 | 1899-12-31 | BC1_DJ_FECH_BLOQ_5M | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | 86BC - Atuado | 0 | 0 | 0 | DiVal | 240 | 200 | 1899-12-31 | BC1_86BC_ATUADO | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | 50BF - Atuado | 0 | 3 | 0 | AF | 160 | 85 | 1900-01-01 | BC1_50BF_ATUADO | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | 50 N - Estágio 1 - Atuado | 0 | 4 | 0 | AF | 160 | 92 | 1900-01-01 | BC1_50N_E1_ATUADO | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | 50 N - Estágio 2 - Atuado | 0 | 4 | 0 | AF | 160 | 93 | 1900-01-01 | BC1_50N_E2_ATUADO | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | 51 N - Atuado | 0 | 4 | 0 | FDI | 60 | 66 | 1900-01-01 | BC1_51N_ATUADO | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | 27 Estágio 1 - Atuado | 0 | 4 | 0 | FDI | 74 | 39 | 1900-01-01 | BC1_27_E1_ATUADO | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | 27 Estágio 2 - Atuado | 0 | 4 | 0 | FDI | 74 | 40 | 1900-01-01 | BC1_27_E2_ATUADO | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | 59 Estágio 1 - Atuado | 0 | 4 | 0 | FDI | 74 | 70 | 1900-01-01 | BC1_59_E1_ATUADO | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | 59 Estágio 2 - Atuado | 0 | 4 | 0 | FDI | 74 | 71 | 1900-01-01 | BC1_59_E2_ATUADO | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Saude Comunicação | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BC1_SAUDE_COMUNIC | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Disj. 52-14 (06Q0) - Aberto/Fechado | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | BC2_DJ_ABERTO | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Disj. 52-14 (06Q0) - Aberto/Fechado | 2 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | BC2_DJ_FECHADO | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Telecomando (43TC) - Excluído | 4 | 0 | 0 | DiVal | 101 | 85 | 1899-12-31 | BC2_43TC_EXCLUIDA | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | AUTOMATISMO - Excluído | 3 | 0 | 0 | DiVal | 240 | 187 | 1899-12-31 | BC2_AUTOMAT_INCLUIDO | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | AUTOMATISMO - Atuado | 5 | 0 | 0 | DiVal | 240 | 188 | 1899-12-31 | BC2_AUTOMAT_ATUADO | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Disj. 52-14 (06Q0) - Mola Descarregada | 0 | 0 | 0 | DiVal | 240 | 195 | 1899-12-31 | BC2_MOLA_DESCARREGADA | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Disj. 52-14 (06Q0) - Falta Vcc Motor/Cmd | 0 | 0 | 0 | DiVal | 240 | 194 | 1899-12-31 | BC2_FALTA_VCC_DJ | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Disj. 52-14 (06Q0) - 43LR em Local | 0 | 0 | 0 | DiVal | 240 | 193 | 1899-12-31 | BC2_43_LR_LOCAL | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Disj.- Sup.Circuito de Abertura | 0 | 0 | 0 | DiVal | 240 | 196 | 1899-12-31 | BC2_BI_SUP_TRIP | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Disj. - Fechamento Bloqueado 5 minutos | 0 | 0 | 0 | DiVal | 240 | 200 | 1899-12-31 | BC2_DJ_FECH_BLOQ_5M | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 86BC - Atuado | 0 | 0 | 0 | DiVal | 240 | 199 | 1899-12-31 | BC2_86BC_ATUADO | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 50BF - Atuado | 0 | 0 | 0 | AF | 160 | 85 | 1900-01-01 | BC2_50BF_ATUADO | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 50F - Estágio 1 - Atuado | 0 | 0 | 0 | AF | 160 | 94 | 1900-01-01 | BC2_50_1_ATUADO | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 50F - Estágio 2 - Atuado | 0 | 0 | 0 | AF | 160 | 95 | 1900-01-01 | BC2_50_2_ATUADO | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 51F - Atuado | 0 | 0 | 0 | FDI | 60 | 67 | 1900-01-01 | BC2_51_ATUADO | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 50 N - Estágio 1 - Atuado | 0 | 0 | 0 | AF | 160 | 92 | 1900-01-01 | BC2_50N_E1_ATUADO | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 50 N - Estágio 2 - Atuado | 0 | 0 | 0 | AF | 160 | 93 | 1900-01-01 | BC2_50N_E2_ATUADO | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 51 N - Atuado | 0 | 0 | 0 | FDI | 60 | 66 | 1900-01-01 | BC2_51N_ATUADO | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 27 Estágio 1 - Atuado | 0 | 0 | 0 | FDI | 74 | 39 | 1900-01-01 | BC2_27_E1_ATUADO | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 27 Estágio 2 - Atuado | 0 | 0 | 0 | FDI | 74 | 40 | 1900-01-01 | BC2_27_E2_ATUADO | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 59 Estágio 1 - Atuado | 0 | 0 | 0 | FDI | 74 | 70 | 1900-01-01 | BC2_59_E1_ATUADO | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | 59 Estágio 2 - Atuado | 0 | 0 | 0 | FDI | 74 | 71 | 1900-01-01 | BC2_59_E2_ATUADO | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Saude Comunicação | 0 | 0 | 0 | - | - | - | - | BC2_SAUDE_COMUNIC | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Disj.52-02 – Aberto | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | TR3AT_DJ_ABERTO | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Disj.52-02 – Fechado | 2 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | TR3AT_DJ_FECHADO | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Secc.89-04 (XXQD) - Aberto | 8 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | TR3AT_S8904_ABERTO | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Secc.89-04 (XXQD) - Fechado | 9 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | TR3AT_S8904_FECHADO | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Disj. 52-02 - 43LR em posição LOCAL | 3 | 0 | 0 | DI Val | 240 | 190 | 1899-12-31 | TR3AT_DJ_43LR_LOCAL | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Disj. 52-02 - Mola Descarregada | 4 | 0 | 0 | DI Val | 240 | 191 | 1899-12-31 | TR3AT_DJ_MOLA_DESC | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Oper.Indevida Seccionadora 89-04/24 (XXSD/E) | 5 | 0 | 0 | DI Val | 240 | 192 | 1899-12-31 | TR3AT_OP_IND_SECC | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 86T3 - Atuado | 6 | 0 | 0 | DI Val | 240 | 193 | 1899-12-31 | TR3_86T3_ATUADO | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Disj. 52-02 - SF6 - Alarme | ? | 0 | 0 | DI Val | 240 | 194 | 1899-12-31 | TR3AT_SF6_ALARME | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Disj. 52-02 - SF6 - Bloqueio | ? | 0 | 0 | DI Val | 240 | 195 | 1899-12-31 | TR3AT_SF6_BLOQUEIO | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Disj. 52-02 - Falta Vcc Motor/Comando | ? | 0 | 0 | DI Val | 240 | 196 | 1899-12-31 | TR3AT_FVCC_CMD_MOT | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Disj.52-02 - Superv.Circuito TRIP - Alarme | 7 | 0 | 0 | DI Val | 170 | 57 | 1899-12-31 | TR3AT_CIRC_TRIP_FALHADO | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 63T - Alarme | 10 | 0 | 0 | DI Val | 101 | 10 | 1899-12-31 | TR3_63T_ALARME | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 63T - Desligamento | 11 | 0 | 0 | DI Val | 101 | 11 | 1899-12-31 | TR3_63T_ATUADO | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 63C - Desligamento | 12 | 0 | 0 | DI Val | 101 | 12 | 1899-12-31 | TR3_63C_ATUADO | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 63C - Alarme - FUTURO | 13 | 0 | 0 | DI Val | 101 | 13 | 1899-12-31 | Reserva | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Reserva | 14 | 0 | 0 | - | - | - | - | Reserva | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Reserva | 15 | 0 | 0 | - | - | - | - | Reserva | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 26T - Alarme | 16 | 0 | 0 | DI Val | 101 | 13 | 1899-12-31 | TR3_26T_ALARME | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 26T - Desligamento | 17 | 0 | 0 | DI Val | 101 | 14 | 1899-12-31 | TR3_26T_ATUADO | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 49BT - Alarme | 18 | 0 | 0 | DI Val | 101 | 15 | 1899-12-31 | TR3_49BT_ALARME | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 49BT - Desligamento | 19 | 0 | 0 | DI Val | 101 | 16 | 1899-12-31 | TR3_49BT_ATUADO | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 49AT - Alarme | 20 | 0 | 0 | DI Val | 101 | 17 | 1899-12-31 | TR3_49_ALARME | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | 49AT - Desligamento | 21 | 0 | 0 | DI Val | 101 | 18 | 1899-12-31 | TR3_49_ATUADO | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Partida Externa do 62BF | 22 | 0 | 0 | - | - | - | - | (Uso Interno) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | B23P1 | 86FD/BT (23kV) - Abertura e Bloqueio Disj.52-02 | 23 | 0 | 0 | DI Val | 240 | 199 | 1899-12-31 | (Somente p/Intertravamento!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | B69 | 86FD/AT (69 kV) - Abertura e Bloqueio Disj.52-02 | 24 | 0 | 0 | - | - | - | - | (Somente p/Intertravamento!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 43TC - Excluída | - | 0 | 0 | DI Val | 101 | 85 | 1899-12-31 | TR3AT_43TC_EXCLUIDA | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | TRIP da Prot.26/49 - Atuado | - | 0 | 15 | DI Val | 240 | 200 | 1899-12-31 | TR3_26_49_TRIP_ATUADO | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3 | TRIP da Prot.50/63T/63C - Atuado | - | 0 | 14 | - | - | - | - | (Somente p/Intertravamento!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 62BF - Atuado | - | 0 | 3 | Auto Fault | 160 | 85 | 1900-01-01 | TR3AT_62BF_ATUADO | 379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 50 ABC - Estágio 1 - Atuado | - | 0 | 4/10 | Auto Fault | 160 | 90 | 1900-01-01 | TR3AT_50ABC_E1_ATUADO | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 50 ABC - Estágio 2 - Atuado | - | 0 | 4/10 | Auto Fault | 160 | 91 | 1900-01-01 | TR3AT_50ABC_E2_ATUADO | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 50 N - Estágio 1 - Atuado | - | 0 | 4 | Auto Fault | 160 | 92 | 1900-01-01 | TR3AT_50N_E1_ATUADO | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 50 N - Estágio 2 - Atuado | - | 0 | 4 | Auto Fault | 160 | 93 | 1900-01-01 | TR3AT_50N_E2_ATUADO | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 50/51 Fase A - Atuado | - | 0 | - | Fault DI | 60 | 54 | 1900-01-01 | TR3AT_50FA_51FA_ATUADO | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 50/51 Fase B - Atuado | - | 0 | - | Fault DI | 60 | 55 | 1900-01-01 | TR3AT_50FB_51FB_ATUADO | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 50/51 Fase C - Atuado | - | 0 | - | Fault DI | 60 | 56 | 1900-01-01 | TR3AT_50FC_51FC_ATUADO | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 51 ABC - Atuado | - | 0 | 4/10 | Fault DI | 60 | 58 | 1900-01-01 | TR3AT_51ABC_ATUADO | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | 51 N - Atuado | - | 0 | 4/10 | Fault DI | 60 | 66 | 1900-01-01 | TR3AT_51N_ATUADO | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Prot.67 - Bloqueada | - | 0 | - | DiVal | 63 | 11 | 1899-12-31 | TR3AT_67_BLOQUEADA | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Atuado 67 - Estágio 1 | - | 0 | 4 | Fault Di | 63 | 25 | 1900-01-01 | TR3AT_67_E1_ATUADO | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Atuado 67 - Estágio 2 | - | 0 | 4 | Fault Di | 63 | 72 | 1900-01-01 | TR3AT_67_E2_ATUADO | 391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Atuado 67 - TOC | - | 0 | 4 | Fault Di | 63 | 35 | 1900-01-01 | TR3AT_67TOC_ATUADO | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Atuado 67N - Estágio 1 | - | 0 | 4 | Fault Di | 63 | 43 | 1900-01-01 | TR3AT_67N_E1_ATUADO | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Atuado 67N - Estágio 2 | - | 0 | 4 | Fault Di | 63 | 64 | 1900-01-01 | TR3AT_67N_E2_ATUADO | 394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Atuado 67N - TOC | - | 0 | 4 | Fault Di | 63 | 46 | 1900-01-01 | TR3AT_67N_TOC_ATUADO | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Atuado 67 - Fase A | - | 0 | - | Fault Di | 63 | 75 | 1900-01-01 | TR3AT_67_FA_ATUADO | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Atuado 67 - Fase B | - | 0 | - | Fault Di | 63 | 76 | 1900-01-01 | TR3AT_67_FB_ATUADO | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Atuado 67 - Fase C | - | 0 | - | Fault Di | 63 | 77 | 1900-01-01 | TR3AT_67_FC_ATUADO | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Supervisão Medição: Falha Fusível TPs | - | 0 | - | DiVal | 135 | 149 | 1899-12-31 | TR3AT_60FF_ALARME | 399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Saúde Comunicação | - | 0 | - | 0 | 0 | 0 | 0 | TR3AT_SAUDE_COMUNIC | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 03) | TR3 | 87 Trip Geral - Atuado | 0 | 0 | 0 | AF | 176 | 68 | 1900-01-01 | TR3DIF_87_ATUADO | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 03) | TR3 | 87 Fase A - Atuado | 0 | 1 | X | AF | 176 | 86 | 1900-01-01 | TR3DIF_87_FA_ATUADO | 411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 03) | TR3 | 87 Fase B - Atuado | 0 | 2 | X | AF | 176 | 87 | 1900-01-01 | TR3DIF_87_FB_ATUADO | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 03) | TR3 | 87 Fase C - Atuado | 0 | 3 | X | AF | 176 | 88 | 1900-01-01 | TR3DIF_87_FC_ATUADO | 413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 03) | TR3 | 87 - Excluído | 0 | 4 | X | DiVal | 75 | 15 | 1899-12-31 | TR3DIF_87_EXCLUIDO | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 03) | TR3 | 20 ALarme | 1 | 0 | X | DiVal | 101 | 10 | 1899-12-31 | TR3DIF_20_ALARME | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 03) | TR3 | 20 Desligamento | 2 | 0 | X | DiVal | 101 | 11 | 1899-12-31 | TR3DIF_20_DESLIGAMENTO | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 03) | TR3 | Saúde Comunicação | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TR3DIF_SAUDE_COMUNIC | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Secc.89-24 – Aberta | 1 | 0 | 3 | DiSOEx2 | 240 | 161 | 1899-12-31 | TR3BT_SECC89D_ABERTA | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Secc.89-24 – Fechada | 2 | 0 | 3 | DiSOEx2 | 240 | 161 | 1899-12-31 | TR3BT_SECC89D_FECHADA | 421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 02) | TR3BT | Secc.89-24 – Falta VCC Comando | 8 | 0 | 0 | DI Val | 240 | 191 | 1899-12-31 | TR3BT_FALTA_VCC_COMANDO | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 04) | TR3BT | Secc.89-24 – 43TC - Excluída | 0 | 0 | 0 | DI Val | 101 | 85 | 1899-12-31 | TR3BT_43TC_EXCLUIDA | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Secc.89-24 – Chave Local/Remoto - Pos. Local | 5 | 0 | 0 | DiVal | 240 | 189 | 1899-12-31 | TR3BT_43LR_POS_LOCAL | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Secc.89-24 – Falta VCC Motor | 4 | 0 | 0 | DiVal | 240 | 190 | 1899-12-31 | TR3BT_FALTA_VCC_MOTOR | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 04) | B23P1 | 86FD P1 23kV Atuado | 6 | 0 | 0 | DI Val | 240 | 199 | 1899-12-31 | B23P1_86FD_P1_ATUADO | 426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Grupo A Ativo | 0 | 0 | 0 | DI Val | 160 | 23 | 1899-12-31 | TR3BT_GRUPO_A_ATIVO | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Grupo B Ativo | 0 | 0 | 0 | DI Val | 160 | 24 | 1899-12-31 | TR3BT_GRUPO_B_ATIVO | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 51 ABC - Atuado | 0 | 0 | 1/4 | FDI | 60 | 58 | 1900-01-01 | TR3BT_51ABC_ATUADO | 429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 50 ABC - Estágio 1 - Atuado | 0 | 0 | 1/4 | AF | 160 | 90 | 1900-01-01 | TR3BT_50ABC_1_ATUADO | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 50 ABC - Estágio 2 - Atuado | 0 | 0 | 1/4 | AF | 160 | 91 | 1900-01-01 | TR3BT_50ABC_2_ATUADO | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 50 N - Estágio 1 - Atuado | 0 | 0 | 1/4 | AF | 160 | 92 | 1900-01-01 | TR3BT_50N_1_ATUADO | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 50 N - Estágio 2 - Atuado | 0 | 0 | 1/4 | AF | 160 | 93 | 1900-01-01 | TR3BT_50N_2_ATUADO | 433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 50/51 Fase A - Atuado | 0 | 0 | 1/4 | FDI | 60 | 54 | 1900-01-01 | TR3BT_50FA_51FA_ATUADO | 434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 50/51 Fase B - Atuado | 0 | 0 | 1/4 | FDI | 60 | 55 | 1900-01-01 | TR3BT_50FB_51FB_ATUADO | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 50/51 Fase C - Atuado | 0 | 0 | 1/4 | FDI | 60 | 56 | 1900-01-01 | TR3BT_50FC_51FC_ATUADO | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 51 N - Atuado | 0 | 0 | 1/4 | FDI | 60 | 66 | 1900-01-01 | TR3BT_51N_ATUADO | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 62BF - Atuado | 0 | 0 | 0 | Auto Fault | 160 | 85 | 1900-01-01 | TR3BT_50BF_ATUADO | 438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 81 Estagio 1 Atuado | 0 | 0 | 1/4 | FDI | 70 | 234 | 1900-01-01 | TR3BT_81_E1 | 439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 81 Estagio 2 Atuado | 0 | 0 | 1/4 | FDI | 70 | 235 | 1900-01-01 | TR3BT_81_E2 | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | 81 - Excluido | 0 | 0 | 0 | 0 | 240 | 221 | 1899-12-31 | TR3BT_81_Excluido | 441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Saude Comunicação | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TR3BT_SAUDE_COMUNIC | 442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Disj.52-03 – Aberto | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | TR2AT_DJ_ABERTO | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Disj.52-03 – Fechado | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | TR2AT_DJ_FECHADO | 461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Secc.89-08 (15QD) - Aberto | 8 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | TR2AT_S8908_ABERTA | 462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Secc.89-08 (15QD) - Fechado | 9 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | TR2AT_S8908_FECHADA | 463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Disj. 52-03 - 43LR em posição LOCAL | 3 | 0 | 0 | DI Val | 240 | 190 | 1899-12-31 | TR2AT_DJ_43LR_LOCAL | 464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Disj. 52-03 - Mola Descarregada | 4 | 0 | 0 | DI Val | 240 | 191 | 1899-12-31 | TR2AT_DJ_MOLA_DESC | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Disj. 52-03 - SF6 Alarme | ? | 0 | 0 | DI Val | 240 | 194 | 1899-12-31 | TR2AT_SF6_Alarme | 466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Disj. 52-03 - SF6 Bloqueio | ? | 0 | 0 | DI Val | 240 | 195 | 1899-12-31 | TR2AT_SF6_BLOQUEIO | 467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Oper.Indevida Seccionadora 89-08 (S89D) | 5 | 0 | 0 | DI Val | 240 | 192 | 1899-12-31 | TR2AT_OP_IND_SECC | 468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 86T2 - Atuado | 6 | 0 | 0 | DI Val | 240 | 193 | 1899-12-31 | TR2_86T2_ATUADO | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Disj.52-03 - Superv.Circuito TRIP - Alarme | 7 | 0 | 0 | DI Val | 170 | 57 | 1899-12-31 | TR2AT_CIRC_TRIP_FALHADO | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 63T - Alarme | 10 | 0 | 0 | DI Val | 101 | 10 | 1899-12-31 | TR2_63T_ALARME | 471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 63T - Desligamento | 11 | 0 | 0 | DI Val | 101 | 11 | 1899-12-31 | TR2_63T_ATUADO | 472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Reserva | 12 | 0 | 0 | - | - | - | - | Reserva | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Reserva | 13 | 0 | 0 | - | - | - | - | Reserva | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 63C - Alarme | 14 | 0 | 0 | DI Val | 101 | 12 | 1899-12-31 | TR2_63C_ALARME | 473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 63C - Desligamento | 15 | 0 | 0 | DI Val | 101 | 13 | 1899-12-31 | TR2_63C_ATUADO | 474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 26T - Alarme | 16 | 0 | 0 | DI Val | 101 | 14 | 1899-12-31 | TR2_26T_ALARME | 475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 26T - Desligamento | 17 | 0 | 0 | DI Val | 101 | 15 | 1899-12-31 | TR2_26T_ATUADO | 476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 49BT - Alarme | 18 | 0 | 0 | DI Val | 101 | 16 | 1899-12-31 | TR2_49BT_ALARME | 477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 49BT - Desligamento | 19 | 0 | 0 | DI Val | 101 | 17 | 1899-12-31 | TR2_49BT_ATUADO | 478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 49AT - Alarme | 20 | 0 | 0 | DI Val | 101 | 18 | 1899-12-31 | TR2_49_ALARME | 479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | 49AT - Desligamento | 21 | 0 | 0 | DI Val | 101 | 19 | 1899-12-31 | TR2_49_ATUADO | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Partida Externa do 62BF | 22 | 0 | 0 | - | - | - | - | (Uso Interno) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | B23P2 | 86FD/BT (23kV) - Abertura e Bloqueio Disj.52-03 | 23 | 0 | 0 | - | - | - | - | (Somente p/Intertravamento!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | B69 | 86FD/AT (69kV) - Abertura e Bloqueio Disj.52-03 | 24 | 0 | 0 | - | - | - | - | (Somente p/Intertravamento!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 43TC - Excluída | - | 0 | 0 | DI Val | 101 | 85 | 1899-12-31 | TR2AT_43TC_EXCLUIDA | 481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | TRIP da Prot.26/49 - Atuado | - | 0 | 15 | DI Val | 240 | 200 | 1899-12-31 | TR2_26_49_TRIP_ATUADO | 482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2 | TRIP da Prot.50/63T/63C - Atuado | - | 0 | 14 | - | - | - | - | (Somente p/Intertravamento!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 62BF - Atuado | - | 0 | 3 | Auto Fault | 160 | 85 | 1900-01-01 | TR2AT_62BF_ATUADO | 483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 50 ABC - Estágio 1 - Atuado | - | 0 | 4/10 | Auto Fault | 160 | 90 | 1900-01-01 | TR2AT_50ABC_E1_ATUADO | 484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 50 ABC - Estágio 2 - Atuado | - | 0 | 4/10 | Auto Fault | 160 | 91 | 1900-01-01 | TR2AT_50ABC_E2_ATUADO | 485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 50 N - Estágio 1 - Atuado | - | 0 | 4 | Auto Fault | 160 | 92 | 1900-01-01 | TR2AT_50N_E1_ATUADO | 486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 50 N - Estágio 2 - Atuado | - | 0 | 4 | Auto Fault | 160 | 93 | 1900-01-01 | TR2AT_50N_E2_ATUADO | 487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 50/51 Fase A - Atuado | - | 0 | - | Fault DI | 60 | 54 | 1900-01-01 | TR2AT_50FA_51FA_ATUADO | 488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 50/51 Fase B - Atuado | - | 0 | - | Fault DI | 60 | 55 | 1900-01-01 | TR2AT_50FB_51FB_ATUADO | 489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 50/51 Fase C - Atuado | - | 0 | - | Fault DI | 60 | 56 | 1900-01-01 | TR2AT_50FC_51FC_ATUADO | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 51 ABC - Atuado | - | 0 | 4/10 | Fault DI | 60 | 58 | 1900-01-01 | TR2AT_51ABC_ATUADO | 491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | 51 N - Atuado | - | 0 | 4/10 | Fault DI | 60 | 66 | 1900-01-01 | TR2AT_51N_ATUADO | 492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Prot.67 - Bloqueada | - | 0 | - | DiVal | 63 | 11 | 1899-12-31 | TR2AT_67_BLOQUEADA | 493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Atuado 67 - Estágio 1 | - | 0 | 4 | Fault Di | 63 | 25 | 1900-01-01 | TR2AT_67_E1_ATUADO | 494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Atuado 67 - Estágio 2 | - | 0 | 4 | Fault Di | 63 | 72 | 1900-01-01 | TR2AT_67_E2_ATUADO | 495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Atuado 67 - TOC | - | 0 | 4 | Fault Di | 63 | 35 | 1900-01-01 | TR2AT_67TOC_ATUADO | 496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Atuado 67N - Estágio 1 | - | 0 | 4 | Fault Di | 63 | 43 | 1900-01-01 | TR2AT_67N_E1_ATUADO | 497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Atuado 67N - Estágio 2 | - | 0 | 4 | Fault Di | 63 | 64 | 1900-01-01 | TR2AT_67N_E2_ATUADO | 498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Atuado 67N - TOC | - | 0 | 4 | Fault Di | 63 | 46 | 1900-01-01 | TR2AT_67N_TOC_ATUADO | 499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Atuado 67 - Fase A | - | 0 | 0 | Fault Di | 63 | 75 | 1900-01-01 | TR2AT_67_FA_ATUADO | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Atuado 67 - Fase B | - | 0 | - | Fault Di | 63 | 76 | 1900-01-01 | TR2AT_67_FB_ATUADO | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Atuado 67 - Fase C | - | 0 | - | Fault Di | 63 | 77 | 1900-01-01 | TR2AT_67_FC_ATUADO | 502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Supervisão Medição: Falha Fusível TPs | - | 0 | - | DiVal | 135 | 149 | 1899-12-31 | TR2AT_60FF_ALARME | 503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Saúde Comunicação | - | 0 | - | 0 | 0 | 0 | 0 | TR2AT_SAUDE_COMUNIC | 504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Secc. 89-62 (15QE) – Aberta | 1 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | TR2BT_S8962_ABERTA | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Secc. 89-62 (15QE) – Fechada | 2 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | TR2BT_S8962_FECHADA | 521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7SJ62 (End.: 02) | TR2BT | Secc. 89-62 (15QE) – Falta VCC Comando | 8 | 0 | 0 | DiVal | 240 | 190 | 1899-12-31 | TR2BT_FALTA_VCC_COMANDO | 522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Secc. 89-62 (15QE) – Falta VCC Motor | 4 | 0 | 0 | DiVal | 240 | 191 | 1899-12-31 | TR2BT_FALTA_VCC_MOTOR | 523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Secc. 89-62 (15QE) – Chave Local/Remoto - Pos. Local | 5 | 0 | 0 | DiVal | 240 | 189 | 1899-12-31 | TR2BT_43LR_POS_LOCAL | 524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Secc. 89-62 (15QE) – 43TC - Excluída | 0 | 0 | 0 | DI Val | 101 | 85 | 1899-12-31 | TR2BT_43TC_EXCLUIDA | 525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | B23P2 | 86FD Barra P2 23kV Atuado | 6 | 0 | 0 | DiVal | 240 | 199 | 1899-12-31 | B23P2_86FD_P2_ATUADO | 526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 50 ABC - Estágio 1 - Atuado | 0 | 0 | 0 | AF | 160 | 90 | 1900-01-01 | TR2BT_50ABC_1_ATUADO | 527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 50 ABC - Estágio 2 - Atuado | 0 | 0 | 0 | AF | 160 | 91 | 1900-01-01 | TR2BT_50ABC_2_ATUADO | 528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 50 N - Estágio 1 - Atuado | 0 | 0 | 0 | AF | 160 | 92 | 1900-01-01 | TR2BT_50N_1_ATUADO | 529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 50 N - Estágio 2 - Atuado | 0 | 0 | 0 | AF | 160 | 93 | 1900-01-01 | TR2BT_50N_2_ATUADO | 530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 50/51 Fase A - Atuado | 0 | 0 | 0 | FDI | 60 | 54 | 1900-01-01 | TR2BT_50FA_51FA_ATUADO | 531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 50/51 Fase B - Atuado | 0 | 0 | 0 | FDI | 60 | 55 | 1900-01-01 | TR2BT_50FB_51FB_ATUADO | 532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 50/51 Fase C - Atuado | 0 | 0 | 0 | FDI | 60 | 56 | 1900-01-01 | TR2BT_50FC_51FC_ATUADO | 533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 51 ABC - Atuado | 0 | 0 | 0 | FDI | 60 | 58 | 1900-01-01 | TR2BT_51ABC_ATUADO | 534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 51 N - Atuado | 0 | 0 | 0 | FDI | 60 | 66 | 1900-01-01 | TR2BT_51N_ATUADO | 535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Grupo A Ativo | 0 | 0 | 0 | DiVal | 160 | 23 | 1899-12-31 | TR2BT_GRUPO_A_ATIVO | 536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Grupo B Ativo | 0 | 0 | 0 | DiVal | 160 | 24 | 1899-12-31 | TR2BT_GRUPO_B_ATIVO | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 81 - Estágio 1 - Atuado (Subfrequencia) | 0 | 0 | 0 | FDI | 70 | 234 | 1900-01-01 | TR2BT_81_E1 | 537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 81 - Estágio 2 - Atuado | 0 | 0 | 0 | FDI | 70 | 235 | 1900-01-01 | TR2BT_81_E2 | 538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | 81 - Excluido | 0 | 0 | 0 | DiVal | 240 | 221 | 1899-12-31 | TR2BT_81_Excluido | 539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Saude Comunicação | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TR2BT_SAUDE_COMUNIC | 540 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 01) | TR2 | 87 Trip Geral - Atuado | 0 | 1/2 | 0 | AF | 176 | 68 | 1900-01-01 | TR2DIF_87_ATUADO | 510 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 01) | TR2 | 87 Fase A - Atuado | 0 | 0 | 1 | AF | 176 | 86 | 1900-01-01 | TR2DIF_87_FA_ATUADO | 511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 01) | TR2 | 87 Fase B - Atuado | 0 | 0 | 2 | AF | 176 | 87 | 1900-01-01 | TR2DIF_87_FB_ATUADO | 512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 01) | TR2 | 87 Fase C - Atuado | 0 | 0 | 3 | AF | 176 | 88 | 1900-01-01 | TR2DIF_87_FC_ATUADO | 513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 01) | TR2 | 87 - Excluído | 0 | 0 | 0 | DiVal | 75 | 15 | 1899-12-31 | TR2DIF_87_EXCLUIDO | 514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 01) | TR2 | 20 - Alarme | 1 | 1/2 | 0 | DiVal | 101 | 10 | 1899-12-31 | TR2DIF_20_ALARME | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 01) | TR2 | 20 - Desligamento | 2 | 1/2 | 0 | DiVal | 101 | 11 | 1899-12-31 | TR2DIF_20_DESLIGAMENTO | 516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 01) | TR2 | Saúde Comunicação | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TR2DIF_SAUDE_COMUNIC | 517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Disj.52-17 – Aberto | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | TR1AT_DJ_ABERTO | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Disj.52-17 – Fechado | 2 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | TR1AT_DJ_FECHADO | 601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-112 (S89D) - Aberto | 8 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | TR1AT_S89D_ABERTO | 602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-112 (S89D) - Fechado | 9 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | TR1AT_S89D_FECHADO | 603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-114 (S89E) - Aberto | 11 | 0 | 0 | DiSOEx2 | 240 | 162 | 1899-12-31 | TR1AT_S89E_ABERTO | 604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-114 (S89E) - Fechado | 12 | 0 | 0 | DiSOEx2 | 240 | 162 | 1899-12-31 | TR1AT_S89E_FECHADO | 605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-116 (S89C) - Aberto | 16 | 0 | 0 | DiSOEx2 | 240 | 163 | 1899-12-31 | TR1AT_S89C_ABERTO | 606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-116 (S89C) - Fechado | 17 | 0 | 0 | DiSOEx2 | 240 | 163 | 1899-12-31 | TR1AT_S89C_FECHADO | 607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Disj. 52-17 - BP SF6 (1o.Estágio) - ALARME | 3 | 0 | 0 | DI Val | 240 | 190 | 1899-12-31 | TR1AT_DJ_SF6_ALARME | 608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Disj. 52-17 - BP SF6 (2o.Estágio) - ALARME | 4 | 0 | 0 | DI Val | 240 | 191 | 1899-12-31 | TR1AT_DJ_SF6_BLOQUEIO | 609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Disj. 52-17 - Mola Descarregada/Falta VCC Motor | 5 | 0 | 0 | DI Val | 240 | 192 | 1899-12-31 | TR1AT_DJ_MOLA_DESC | 610 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Disj. 52-17 - 43LR em posição LOCAL | 6 | 0 | 0 | DI Val | 240 | 193 | 1899-12-31 | TR1AT_DJ_43LR_LOCAL | 611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Disj. 52-17 - Superv.Circuito TRIP - Alarme | 7 | 0 | 0 | DI Val | 170 | 57 | 1899-12-31 | TR1AT_CIRC_TRIP_FALHADO | 612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-112/114/116 - 43LR em posição LOCAL | 10 | 0 | 0 | DI Val | 240 | 194 | 1899-12-31 | TR1AT_SECC_43LR_LOCAL | 613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89-112/114/116 - Falta VCC COM/MOTOR | 13 | 0 | 0 | DI Val | 240 | 195 | 1899-12-31 | TR1AT_SECC_FALTA_VCC | 614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 43TC - Excluída | - | 0 | 0 | DI Val | 101 | 85 | 1899-12-31 | TR1AT_43TC_EXCLUIDA | 615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1 | 26T/49AT/49BT - Alarme | 14 | 0 | 0 | DI Val | 101 | 10 | 1899-12-31 | TR1_26T_49HX_ALARME | 616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1 | 26T/49AT/49BT - Desligamento | 15 | 0 | 4 | DI Val | 101 | 11 | 1899-12-31 | TR1_26T_49HX_ATUADOI | 617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Oper.Indevida Seccionadoras | 18 | 0 | 0 | DI Val | 240 | 198 | 1899-12-31 | TR1AT_OP_IND_SECC | 618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1 | 86T1 - Atuado | 19 | 0 | 0 | DI Val | 240 | 199 | 1899-12-31 | TR1_86T1_ATUADO | 619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1 | 63T - Alarme | 20 | 0 | 0 | DI Val | 101 | 12 | 1899-12-31 | TR1_63T_ALARME | 620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1 | 63T - Desligamento | 21 | 0 | 0 | DI Val | 101 | 13 | 1899-12-31 | TR1_63T_ATUADO | 621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Reserva | 22 | 0 | 0 | - | - | - | - | Reserva | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Trip externo do 62BF do Disj.52-01 (BT) | 23 | 0 | 0 | - | - | - | - | (Somente p/Intertravamento!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | B138 | 86FD/AT (138 kV) - Abertura e Bloqueio Disj.52-17 | 24 | 0 | 0 | - | - | - | - | (Somente p/Intertravamento!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Secc.89--116 (S89C) - Libera Manobra | - | 13 | 0 | - | - | - | - | (Somente p/Intertravamento!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | ??? | - | 14 | 0 | - | - | - | - | (Somente p/Intertravamento!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 62BF - Atuado | - | 3 | 0 | Auto Fault | 160 | 85 | 1900-01-01 | TR1AT_62BF_ATUADO | 622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 50 ABC - Estágio 1 - Atuado | - | 4 | 0 | Auto Fault | 160 | 90 | 1900-01-01 | TR1AT_50ABC_E1_ATUADO | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 50 ABC - Estágio 2 - Atuado | - | 4 | 0 | Auto Fault | 160 | 91 | 1900-01-01 | TR1AT_50ABC_E2_ATUADO | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 50 N - Estágio 1 - Atuado | - | 4 | 0 | Auto Fault | 160 | 92 | 1900-01-01 | TR1AT_50N_E1_ATUADO | 625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 50 N - Estágio 2 - Atuado | - | 4 | 0 | Auto Fault | 160 | 93 | 1900-01-01 | TR1AT_50N_E2_ATUADO | 626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 50/51 Fase A - Atuado | - | 0 | 0 | Fault DI | 60 | 54 | 1900-01-01 | TR1AT_50FA_51FA_ATUADO | 627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 50/51 Fase B - Atuado | - | 0 | 0 | Fault DI | 60 | 55 | 1900-01-01 | TR1AT_50FB_51FB_ATUADO | 628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 50/51 Fase C - Atuado | - | 0 | 0 | Fault DI | 60 | 56 | 1900-01-01 | TR1AT_50FC_51FC_ATUADO | 629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 51 ABC - Atuado | - | 4 | 0 | Fault DI | 60 | 58 | 1900-01-01 | TR1AT_51ABC_ATUADO | 630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | 51 N - Atuado | - | 4 | 0 | Fault DI | 60 | 66 | 1900-01-01 | TR1AT_51N_ATUADO | 631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Prot.67 - Bloqueada | 0 | 0 | 0 | DiVal | 63 | 11 | 1899-12-31 | TR1AT_67_BLOQUEADA | 632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Atuado 67 - Estágio 1 | 0 | 4 | 0 | Fault Di | 63 | 25 | 1900-01-01 | TR1AT_67_E1_ATUADO | 633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Atuado 67 - Estágio 2 | 0 | 4 | 0 | Fault Di | 63 | 72 | 1900-01-01 | TR1AT_67_E2_ATUADO | 634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Atuado 67 - TOC | 0 | 4 | 0 | Fault Di | 63 | 35 | 1900-01-01 | TR1AT_67TOC_ATUADO | 635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Atuado 67N - Estágio 1 | 0 | 4 | 0 | Fault Di | 63 | 43 | 1900-01-01 | TR1AT_67N_E1_ATUADO | 636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Atuado 67N - Estágio 2 | 0 | 4 | 0 | Fault Di | 63 | 64 | 1900-01-01 | TR1AT_67N_E2_ATUADO | 637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Atuado 67N - TOC | 0 | 4 | 0 | Fault Di | 63 | 46 | 1900-01-01 | TR1AT_67N_TOC_ATUADO | 638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Atuado 67 - Fase A | 0 | 0 | 0 | Fault Di | 63 | 75 | 1900-01-01 | TR1AT_67_FA_ATUADO | 639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Atuado 67 - Fase B | 0 | 0 | 0 | Fault Di | 63 | 76 | 1900-01-01 | TR1AT_67_FB_ATUADO | 640 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Atuado 67 - Fase C | 0 | 0 | 0 | Fault Di | 63 | 77 | 1900-01-01 | TR1AT_67_FC_ATUADO | 641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Supervisão Medição: Falha Fusível TPs | 0 | 0 | 0 | DiVal | 135 | 149 | 1899-12-31 | TR1AT_60FF_ALARME | 642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Saúde Comunicação | - | 0 | 0 | 0 | 0 | 0 | 0 | TR1AT_SAUDE_COMUNIC | 643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | 87 Trip Geral - Atuado | 0 | 0 | 0 | AF | 176 | 68 | 1900-01-01 | TR1DIF_87_ATUADO | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | 87 Fase A - Atuado | 0 | 0 | 0 | AF | 176 | 86 | 1900-01-01 | TR1DIF_87_FA_ATUADO | 651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | 87 Fase B - Atuado | 0 | 0 | 0 | AF | 176 | 87 | 1900-01-01 | TR1DIF_87_FB_ATUADO | 652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | 87 Fase C - Atuado | 0 | 0 | 0 | AF | 176 | 88 | 1900-01-01 | TR1DIF_87_FC_ATUADO | 653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | 87 - Excluído | 0 | 0 | 0 | DiVal | 75 | 15 | 1899-12-31 | TR1DIF_87_EXCLUIDO | 654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | 87 - Bloqueado | 0 | 0 | 0 | DiVal | 75 | 16 | 1899-12-31 | TR1DIF_87_BLOQUEADO | 655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | 62BF - Atuado | 0 | 0 | 0 | AF | 166 | 193 | 1900-01-01 | TR1DIF_62BF_ATUADO | 656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | Estado seccionadora 29-120 | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | TR1DIF_S329D_ABERTA | 657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | Estado seccionadora 29-120 | 2 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | TR1DIF_S329D_FECHADA | 658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | 20T - Atuado | 3 | 0 | 0 | DiVal | 101 | 10 | 1899-12-31 | TR1DIF_20T_ATUADO | 659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7UT612 (End.: 15d/0Fh) | TR1 | Saúde Comunicação | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TR1DIF_SAUDE_COMUNIC | 660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Disj. 52-01 – Aberto | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | TR1BT_DJ_ABERTO | 670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Disj. 52-01 – Fechado | 2 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | TR1BT_DJ_FECHADO | 671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Disj. 52-01 - Superv.Circuito TRIP - Alarme | 3 | 0 | 0 | DiVal | 240 | 190 | 1899-12-31 | TR1BT_CIRC_TRIP_FALHADO | 672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Disj. 52-01 - Mola Descarregada | 4 | 0 | 0 | DiVal | 240 | 191 | 1899-12-31 | TR1BT_DJ_MOLA_DESC | 673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Disj. 52-01 - BP SF6 (1o/2o.Estágio) - ALARME | 5 | 0 | 0 | DiVal | 240 | 192 | 1899-12-31 | TR1BT_DJ_SF6_BLOQUEIO | 674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Operação Indevida da Secc.29-120 (S329D) | 6 | 0 | 0 | DiVal | 240 | 193 | 1899-12-31 | TR1BT_OPER_INDEV_SECC | 675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | B69 | 86FD da 69kV ou 86T1 Atuado - Abertura e Bloqueio Disj.52-01 | 7 | 0 | 0 | - | - | - | - | (Somente p/Intertravamento!) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Disj.52-01 – 43LR em posição LOCAL | 8 | 0 | 0 | DI Val | 240 | 195 | 1899-12-31 | TR1BT_DJ_43LR_LOCAL | 676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Disj.52-01 – 43TC Excluída | - | 0 | 0 | DI Val | 101 | 85 | 1899-12-31 | TR1BT_43TC_EXCLUIDA | 677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 62BF - Atuado | 0 | 3/4 | 0 | Auto Fault | 160 | 85 | 1900-01-01 | TR1BT_62BF_ATUADO | 678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 50 ABC - Estágio 1 - Atuado | 0 | 1 | 0 | AF | 160 | 90 | 1900-01-01 | TR1BT_50ABC_E1_ATUADO | 679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 50 ABC - Estágio 2 - Atuado | 0 | 1 | 0 | AF | 160 | 91 | 1900-01-01 | TR1BT_50ABC_E2_ATUADO | 680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 50 N - Estágio 1 - Atuado | 0 | 1 | 0 | AF | 160 | 92 | 1900-01-01 | TR1BT_50N_E1_ATUADO | 681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 50 N - Estágio 2 - Atuado | 0 | 1 | 0 | AF | 160 | 93 | 1900-01-01 | TR1BT_50N_E2_ATUADO | 682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 50/51 Fase A - Atuado | 0 | 0 | 0 | FDI | 60 | 54 | 1900-01-01 | TR1BT_50FA_51FA_ATUADO | 683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 50/51 Fase B - Atuado | 0 | 0 | 0 | FDI | 60 | 55 | 1900-01-01 | TR1BT_50FB_51FB_ATUADO | 684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 50/51 Fase C - Atuado | 0 | 0 | 0 | FDI | 60 | 56 | 1900-01-01 | TR1BT_50FC_51FC_ATUADO | 685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 51 ABC - Atuado | 0 | 1 | 0 | FDI | 60 | 58 | 1900-01-01 | TR1BT_51ABC_ATUADO | 686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 51 N - Atuado | 0 | 1 | 0 | FDI | 60 | 66 | 1900-01-01 | TR1BT_51N_ATUADO | 687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | 60FF - falha Fusível | 0 | 0 | 0 | DI Val | 135 | 149 | 1899-12-31 | TR1BT_60FF_ALARME | 688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Saude Comunicação | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TR1BT_SAUDE_COMUNIC | 689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Disjuntor 52-16 – Aberto | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | LT21PCH_DJ_ABERTO | IDF | LTPCH_DJ_ABERTO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Disjuntor 52-16 – Fechado | 2 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | LT21PCH_DJ_FECHADO | IDF | LTPCH_DJ_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Secc.89-100 (S89E) - Aberto | 8 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | LT21PCH_S89E_ABERTA | IDF | LTPCH_S89E_ABERTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Secc.89-100 (S89E) - Fechado | 9 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | LT21PCH_S89E_FECHADO | IDF | LTPCH_S89E_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Secc.89-102 (S89D) - Aberto | 10 | 0 | 0 | DiSOEx2 | 240 | 162 | 1899-12-31 | LT21PCH_S89D_ABERTA | IDF | LTPCH_S89D_ABERTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Secc.89-102 (S89D) - Fechado | 11 | 0 | 0 | DiSOEx2 | 240 | 162 | 1899-12-31 | LT21PCH_S89D_FECHADO | IDF | LTPCH_S89D_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Secc.89-104 (S89C) - Aberto | 12 | 0 | 0 | DiSOEx2 | 240 | 163 | 1899-12-31 | LT21PCH_S89C_ABERTA | IDF | LTPCH_S89C_ABERTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Secc.89-104 (S89C) - Fechado | 13 | 0 | 0 | DiSOEx2 | 240 | 163 | 1899-12-31 | LT21PCH_S89C_FECHADO | IDF | LTPCH_S89C_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Seccion. 29-05 (S29T) - Aberto | 14 | 0 | 0 | DiSOEx2 | 240 | 165 | 1899-12-31 | LT21PCH_S29T_ABERTA | IDF | LTPCH_S29T_ABERTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Seccion. 29-05 (S29T) - Fechado | 15 | 0 | 0 | DiSOEx2 | 240 | 165 | 1899-12-31 | LT21PCH_S29T_FECHADO | IDF | LTPCH_S29T_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | DJ - Chave 43TC - Incluir/Excluir | 0 | 0 | 0 | DiVal | 101 | 85 | 1899-12-31 | LT21PCH_43TC_EXCLUIDA | OR | LTPCH_43TC_EXCLUIDA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | DJ - SF6 - Alarme | 3 | 0 | 0 | DiVal | 240 | 192 | 1899-12-31 | LT21PCH_SF6_ALARME | IDF | LTPCH_SF6_ALARME | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | DJ - SF6 - Bloqueio | 4 | 0 | 0 | DiVal | 240 | 191 | 1899-12-31 | LT21PCH_SF6_BLOQUEIO | IDF | LTPCH_SF6_BLOQUEIO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | DJ - Mola Descarregada | 5 | 0 | 0 | DiVal | 240 | 190 | 1899-12-31 | LT21PCH_MOLA_DESC | IDF | LTPCH_MOLA_DESC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | DJ - 43LR - Posição LOCAL | 6 | 0 | 0 | DiVal | 240 | 193 | 1899-12-31 | LT21PCH_43LR_POS_LOCAL | IDF | LTPCH_43LR_POS_LOCAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | DJ - Falta VCC de COM/MOTOR - Alarme | 7 | 0 | 0 | DiVal | 240 | 198 | 1899-12-31 | LT21PCH_F_CC_COM_MOT | IDF | LTPCH_F_CC_COM_MOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Sinal Rele 24F02(F67) - Excluir 43TC | 16 | 0 | 0 | - | - | - | - | (Só para lógica interna de intertravamento!) | 0 | (Só para lógica interna de intertravamento!) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Sinal Rele 24F02(F67) - Excluir 79 | 17 | 0 | 0 | - | - | - | - | (Só para lógica interna de intertravamento!) | 0 | (Só para lógica interna de intertravamento!) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | B138 | 86FD/AT - Atuado | 18 | 0 | 0 | Di Val | 240 | 195 | 1899-12-31 | B138_86FD_ATUADO | OR | B138_86FD_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Operação Indevida de SECCIONADORAS | 19 | 0 | 0 | DiVal | 240 | 194 | 1899-12-31 | LT21PCH_OP_INDEV_SECC | OR | LTPCH_OP_INDEV_SECC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | DJ - Supervisão Circuito TRIP - Alarme | 20 | 0 | 0 | DiVal | 170 | 56 | 1899-12-31 | LT21PCH_CIRC_TRIP_FALHADO | OR | LTPCH_CIRC_TRIP_FALHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | 79 - Excluído | 0 | 0 | 0 | DiVal | 40 | 81 | 1899-12-31 | LT21PCH_79_EXCLUIDO | OR | LTPCH_79_EXCLUIDO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | 79 - Disparo | 0 | 0 | 0 | AutoDi | 160 | 128 | 1899-12-31 | LT21PCH_79_DISPARO | 775 | LT21PCH_79_DISPARO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | 79 - Religamento Sucedido | 0 | 0 | 0 | AutoDi | 40 | 162 | 1899-12-31 | LT21PCH_79_SUCEDIDO | 776 | LT21PCH_79_SUCEDIDO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | 79 - Bloqueado (Lockout) | 0 | 0 | 0 | FDI | 40 | 83 | 1900-01-01 | LT21PCH_79_BLOQUEADO | 777 | LT21PCH_79_BLOQUEADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | 25 - Falha Operação Sincronismo | 0 | 0 | 0 | AutoDi | 41 | 35 | 1899-12-31 | LT21PCH_25_FALHA_SINCRO | OR | LTPCH_25_FALHA_SINCRO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 50 BF | 0 | 0 | 0 | Auto Fault | 160 | 85 | 1900-01-01 | LT21PCH_50BF_ATUADO | 778 | LT21PCH_50BF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Supervisão Medição: Falha Fusível TPs | 0 | 0 | 0 | DiVal | 135 | 149 | 1899-12-31 | LT21PCH_60FF_ALARME | 779 | LT21PCH_60FF_ALARME | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Prot.21 - Bloqueada | 0 | 0 | 0 | DiVal | 28 | 52 | 1899-12-31 | LT21PCH_21_BLOQUEADA | 780 | LT21PCH_21_BLOQUEADA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 21 Trip Fase A | 0 | 0 | 0 | Fault Di | 28 | 206 | 1900-01-01 | LT21PCH_21FA_ATUADO | 781 | LT21PCH_21FA_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 21 Trip Fase B | 0 | 0 | 0 | Fault Di | 28 | 207 | 1900-01-01 | LT21PCH_21FB_ATUADO | 782 | LT21PCH_21FB_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 21 Trip Fase C | 0 | 0 | 0 | Fault Di | 28 | 208 | 1900-01-01 | LT21PCH_21FC_ATUADO | 783 | LT21PCH_21FC_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 21 N Trip | 0 | 0 | 0 | Fault Di | 28 | 212 | 1900-01-01 | LT21PCH_21N_ATUADO | 784 | LT21PCH_21N_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 21 Trip3p.Z1sf | 0 | 0 | 0 | Auto Fault | 28 | 224 | 1900-01-01 | LT21PCH_21Z1SF_ATUADO | 785 | LT21PCH_21Z1SF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 21 Trip3p.Z1mf | 0 | 0 | 0 | Auto Fault | 28 | 225 | 1900-01-01 | LT21PCH_21Z1MF_ATUADO | 786 | LT21PCH_21Z1MF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 21 Trip3p.Z2 | 0 | 0 | 0 | Auto Fault | 28 | 217 | 1900-01-01 | LT21PCH_21Z2_ATUADO | 787 | LT21PCH_21Z2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 21 Trip3p.Z3 | 0 | 0 | 0 | Auto Fault | 28 | 218 | 1900-01-01 | LT21PCH_21Z3_ATUADO | 788 | LT21PCH_21Z3_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 21 Trip3p.Z4 | 0 | 0 | 0 | Auto Fault | 28 | 209 | 1900-01-01 | LT21PCH_21Z4_ATUADO | 789 | LT21PCH_21Z4_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 21 Trip3p.Z5 | 0 | 0 | 0 | Auto Fault | 28 | 210 | 1900-01-01 | LT21PCH_21Z5_ATUADO | 790 | LT21PCH_21Z5_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Falta Tensão LT - Alarme | 0 | 0 | 0 | DiVal | 240 | 204 | 1899-12-31 | LT21PCH_FALTA_TENSAO_LT | OR | LTPCH_FALTA_TENSAO_LT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Localiz.Defeito - Disparo | 0 | 0 | 0 | DiVal | 151 | 7 | 1899-12-31 | LT21PCH_LDF_ATUADO | 791 | LT21PCH_LDF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuada Proteção Backup: 5XB TRIP | 0 | 0 | 0 | Auto Fault | 128 | 72 | 1900-01-01 | LT21PCH_5XB_ATUADO | 792 | LT21PCH_5XB_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuada Proteção 50HS - Trip ABC (SOTF) | 0 | 0 | 0 | Auto Fault | 25 | 95 | 1900-01-01 | LT21PCH_50HS_ABC_ATUADO | 793 | LT21PCH_50HS_ABC_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Atuado 67N TRIP | 0 | 0 | 0 | Auto Fault | 166 | 69 | 1900-01-01 | LT21PCH_67N_ATUADO | 794 | LT21PCH_67N_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Saúde Comunicação | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 795 | LT21PCH_SAUDE_COMUNIC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Disjuntor 52-16 – Aberto | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | LT67PCH_DJ_ABERTO | 720 | LTPCH_DJ_ABERTO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Disjuntor 52-16 – Fechado | 2 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | LT67PCH_DJ_FECHADO | 721 | LTPCH_DJ_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Secc.89-100 (S89E) - Aberto | 8 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | LT67PCH_S89E_ABERTA | 722 | LTPCH_S89E_ABERTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Secc.89-100 (S89E) - Fechado | 9 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | LT67PCH_S89E_FECHADO | 723 | LTPCH_S89E_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Secc.89-102 (S89D) - Aberto | 10 | 0 | 0 | DiSOEx2 | 240 | 162 | 1899-12-31 | LT67PCH_S89D_ABERTA | 724 | LTPCH_S89D_ABERTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Secc.89-102 (S89D) - Fechado | 11 | 0 | 0 | DiSOEx2 | 240 | 162 | 1899-12-31 | LT67PCH_S89D_FECHADO | 725 | LTPCH_S89D_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Secc.89-104 (S89C) - Aberto | 12 | 0 | 0 | DiSOEx2 | 240 | 163 | 1899-12-31 | LT67PCH_S89C_ABERTA | 726 | LTPCH_S89C_ABERTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Secc.89-104 (S89C) - Fechado | 13 | 0 | 0 | DiSOEx2 | 240 | 163 | 1899-12-31 | LT67PCH_S89C_FECHADO | 727 | LTPCH_S89C_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Seccion. 29-05 (S29T) - Aberto | 14 | 0 | 0 | DiSOEx2 | 240 | 165 | 1899-12-31 | LT67PCH_S29T_ABERTA | 728 | LTPCH_S29T_ABERTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Seccion. 29-05 (S29T) - Fechado | 15 | 0 | 0 | DiSOEx2 | 240 | 165 | 1899-12-31 | LT67PCH_S29T_FECHADO | 729 | LTPCH_S29T_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | S89E - 43LR - Posição LOCAL | 6 | 0 | 0 | DiVal | 240 | 154 | 1899-12-31 | LT67PCH_S89E_43LR_LOCAL | 730 | LT67PCH_S89E_43LR_LOCAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | S89D - 43LR - Posição LOCAL | 6 | 0 | 0 | DiVal | 240 | 158 | 1899-12-31 | LT67PCH_S89D_43LR_LOCAL | 731 | LT67PCH_S89D_43LR_LOCAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | S89C- 43LR - Posição LOCAL | 6 | 0 | 0 | DiVal | 240 | 156 | 1899-12-31 | LT67PCH_S89C_43LR_LOCAL | 732 | LT67PCH_S89C_43LR_LOCAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | S89E - Falta VCC/VCA - Alarme | 7 | 0 | 0 | DiVal | 240 | 159 | 1899-12-31 | LT67PCH_S89E_F_CC_CA | 733 | LT67PCH_S89E_F_CC_CA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | S89D - Falta VCC/VCA - Alarme | 7 | 0 | 0 | DiVal | 240 | 157 | 1899-12-31 | LT67PCH_S89D_F_CC_CA | 734 | LT67PCH_S89D_F_CC_CA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | S89C - Falta VCC/VCA - Alarme | 7 | 0 | 0 | DiVal | 240 | 155 | 1899-12-31 | LT67PCH_S89C_F_CC_CA | 735 | LT67PCH_S89C_F_CC_CA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | DJ - Chave 43TC - Incluir/Excluir | 0 | 0 | 0 | DiVal | 101 | 85 | 1899-12-31 | LT67PCH_43TC_EXCLUIDA | 736 | LTPCH_43TC_EXCLUIDA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | DJ - SF6 - Alarme | 3 | 0 | 0 | DiVal | 240 | 192 | 1899-12-31 | LT67PCH_SF6_ALARME | 737 | LTPCH_SF6_ALARME | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | DJ - SF6 - Bloqueio | 4 | 0 | 0 | DiVal | 240 | 191 | 1899-12-31 | LT67PCH_SF6_BLOQUEIO | 738 | LTPCH_SF6_BLOQUEIO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | DJ - Mola Descarregada | 5 | 0 | 0 | DiVal | 240 | 190 | 1899-12-31 | LT67PCH_MOLA_DESC | 739 | LTPCH_MOLA_DESC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | DJ - 43LR - Posição LOCAL | 6 | 0 | 0 | DiVal | 240 | 193 | 1899-12-31 | LT67PCH_43LR_POS_LOCAL | 740 | LTPCH_43LR_POS_LOCAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | DJ - Falta VCC/VCA de COM/MOTOR - Alarme | 7 | 0 | 0 | DiVal | 240 | 198 | 1899-12-31 | LT67PCH_F_CC_COM_MOT | 741 | LTPCH_F_CC_COM_MOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Sinal Rele 24F02(F67) - Excluir 43TC | 16 | 0 | 0 | - | - | - | - | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Sinal Rele 24F02(F67) - Excluir 79 | 17 | 0 | 0 | - | - | - | - | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | B138 | 86FD/AT - Atuado | 18 | 0 | 0 | Di Val | 240 | 195 | 1899-12-31 | B138_86FD_ATUADO | 742 | B138_86FD_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Operação Indevida de SECCIONADORAS | 19 | 0 | 0 | DiVal | 240 | 194 | 1899-12-31 | LT67PCH_OP_INDEV_SECC | 743 | LTPCH_OP_INDEV_SECC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | DJ - Supervisão Circuito TRIP - Alarme | 20 | 0 | 0 | DiVal | 170 | 55 | 1899-12-31 | LT67PCH_CIRC_TRIP_FALHADO | 744 | LTPCH_CIRC_TRIP_FALHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Grupo de Ajustes B - Ativado | 0 | 0 | 0 | DiVal | 160 | 24 | 1899-12-31 | LT67PCH_GRUPOB_ATIVADO | 745 | LT67PCH_GRUPOB_ATIVADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | 79 - Excluído | 0 | 0 | 0 | DiVal | 40 | 81 | 1899-12-31 | LT67PCH_79_EXCLUIDO | 746 | LTPCH_79_EXCLUIDO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | 79 - Disparo | 0 | 0 | 0 | AutoDi | 160 | 128 | 1899-12-31 | LT67PCH_79_DISPARO | 747 | LT67PCH_79_DISPARO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | 79 - Religamento Sucedido | 0 | 0 | 0 | DiVal | 40 | 162 | 1899-12-31 | LT67PCH_79_SUCEDIDO | 748 | LT67PCH_79_SUCEDIDO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | 79 - Bloqueado | 0 | 0 | 0 | Fault Di | 40 | 163 | 1900-01-01 | LT67PCH_79_BLOQUEADO | 749 | LT67PCH_79_BLOQUEADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | 25 - Falha Operação Sincronismo | 0 | 0 | 0 | AutoDi | 41 | 35 | 1899-12-31 | LT67PCH_25_FALHA_SINCRO | 750 | LTPCH_25_FALHA_SINCRO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuado 50 BF | 0 | 0 | 0 | Auto Fault | 160 | 85 | 1900-01-01 | LT67PCH_50BF_ATUADO | 751 | LT67PCH_50BF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Supervisão Medição: Falha Fusível TPs (10s) | 0 | 0 | 0 | DiVal | 135 | 189 | 1899-12-31 | LT67PCH_60FF_ALARME | 752 | LT67PCH_60FF_ALARME | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Prot.67 - Bloqueada | 0 | 0 | 0 | DiVal | 63 | 11 | 1899-12-31 | LT67PCH_67_BLOQUEADA | 753 | LT67PCH_67_BLOQUEADA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuado 67-1 | 0 | 0 | 0 | Fault Di | 63 | 25 | 1900-01-01 | LT67PCH_67_1_ATUADO | 754 | LT67PCH_67_1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuado 67-2 | 0 | 0 | 0 | Fault Di | 63 | 72 | 1900-01-01 | LT67PCH_67_2_ATUADO | 755 | LT67PCH_67_2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuado 67 - TOC | 0 | 0 | 0 | Fault Di | 63 | 35 | 1900-01-01 | LT67PCH_67TOC_ATUADO | 756 | LT67PCH_67TOC_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuado 67N-1 | 0 | 0 | 0 | Fault Di | 63 | 43 | 1900-01-01 | LT67PCH_67N_1_ATUADO | 757 | LT67PCH_67N_1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuado 67N-2 | 0 | 0 | 0 | Fault Di | 63 | 64 | 1900-01-01 | LT67PCH_67N_2_ATUADO | 758 | LT67PCH_67N_2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuado 67N - TOC | 0 | 0 | 0 | Fault Di | 63 | 46 | 1900-01-01 | LT67PCH_67N_TOC_ATUADO | 759 | LT67PCH_67N_TOC_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuado 67 - Fase A | 0 | 0 | 0 | Fault Di | 63 | 75 | 1900-01-01 | LT67PCH_67_FA_ATUADO | 760 | LT67PCH_67_FA_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuado 67 - Fase B | 0 | 0 | 0 | Fault Di | 63 | 76 | 1900-01-01 | LT67PCH_67_FB_ATUADO | 761 | LT67PCH_67_FB_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuado 67 - Fase C | 0 | 0 | 0 | Fault Di | 63 | 77 | 1900-01-01 | LT67PCH_67_FC_ATUADO | 762 | LT67PCH_67_FC_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Falta Tensão LT - Alarme | 0 | 0 | 0 | DiVal | 240 | 204 | 1899-12-31 | LT67PCH_FALTA_TENSAO_LT | 763 | LTPCH_FALTA_TENSAO_LT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Localiz.Defeito - Disparo | 0 | 0 | 0 | DiVal | 151 | 7 | 1899-12-31 | LT67PCH_LDF_ATUADO | 764 | LT67PCH_LDF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuada Proteção Sub-Frequencia - E1 | 0 | 0 | 0 | Fdi | 70 | 234 | 1900-01-01 | LT67PCH_81U_E1_ATUADO | 765 | LT67PCH_81U_E1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuada Proteção Sub-Frequencia - E2 | 0 | 0 | 0 | Fdi | 70 | 235 | 1900-01-01 | LT67PCH_81U_E2_ATUADO | 766 | LT67PCH_81U_E2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuada Proteção Sobre-Frequencia - E1 | 0 | 0 | 0 | Fdi | 70 | 236 | 1900-01-01 | LT67PCH_81O_E1_ATUADO | 767 | LT67PCH_81O_E1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuada Proteção Sobre-Frequencia - E2 | 0 | 0 | 0 | Fdi | 70 | 237 | 1900-01-01 | LT67PCH_81O_E2_ATUADO | 768 | LT67PCH_81O_E2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuada Proteção 27 E1 | 0 | 0 | 0 | FDi | 74 | 81 | 1900-01-01 | LT67PCH_27_E1_ATUADO | 769 | LT67PCH_27_E1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuada Proteção 27 E2 | 0 | 0 | 0 | FDi | 74 | 40 | 1900-01-01 | LT67PCH_27_E2_ATUADO | 770 | LT67PCH_27_E2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuada Proteção 59 E1 | 0 | 0 | 0 | FDi | 74 | 83 | 1900-01-01 | LT67PCH_59_E1_ATUADO | 771 | LT67PCH_59_E1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Atuada Proteção 59 E2 | 0 | 0 | 0 | FDi | 74 | 41 | 1900-01-01 | LT67PCH_59_E2_ATUADO | 772 | LT67PCH_59_E2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Saúde Comunicação | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773 | LT67PCH_SAUDE_COMUNIC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Dj.52-04 – Aberto | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | LT67KNP_DJ_ABERTO | 810 | LTKNP_DJ_ABERTO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Dj.52-04 – Fechado | 2 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | LT67KNP_DJ_FECHADO | 811 | LTKNP_DJ_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Seccion. 29-12 (329E) - Aberto | 8 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | LT67KNP_S329E_ABERTO | 812 | LTKNP_S329E_ABERTO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Seccion. 29-12 (329E) - Fechado | 9 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | LT67KNP_S329E_FECHADO | 813 | LTKNP_S329E_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Seccion. 29-10 (329D) - Aberto | 10 | 0 | 0 | DiSOEx2 | 240 | 162 | 1899-12-31 | LT67KNP_S329D_ABERTO | 814 | LTKNP_S329D_ABERTO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Seccion. 29-10 (329D) - Fechado | 11 | 0 | 0 | DiSOEx2 | 240 | 162 | 1899-12-31 | LT67KNP_S329D_FECHADO | 815 | LTKNP_S329D_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Seccion. 29-14 (329C) - Aberto | 12 | 0 | 0 | DiSOEx2 | 240 | 163 | 1899-12-31 | LT67KNP_S329C_ABERTO | 816 | LTKNP_S329C_ABERTO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Seccion. 29-14 (329C) - Fechado | 13 | 0 | 0 | DiSOEx2 | 240 | 163 | 1899-12-31 | LT67KNP_S329C_FECHADO | 817 | LTKNP_S329C_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Seccion. 29-01 (229T) - Aberto | 14 | 0 | 0 | DiSOEx2 | 240 | 165 | 1899-12-31 | LT67KNP_S229T_ABERTO | 818 | LTKNP_S229T_ABERTO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Seccion. 29-01 (229T) - Fechado | 15 | 0 | 0 | DiSOEx2 | 240 | 165 | 1899-12-31 | LT67KNP_S229T_FECHADO | 819 | LTKNP_S229T_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | DJ - SF6 - Alarme | 0 | 0 | 0 | DiVal | 240 | 191 | 1899-12-31 | LT67KNP_DJ_SF6_ALARME | 820 | LTKNP_DJ_SF6_ALARME | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | DJ - SF6 - Bloqueio | 0 | 0 | 0 | DiVal | 240 | 192 | 1899-12-31 | LT67KNP_DJ_SF6_BLOQUEIO | 821 | LTKNP_DJ_SF6_BLOQUEIO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | DJ - 43LR - Posição LOCAL | 3 | 0 | 0 | DiVal | 240 | 193 | 1899-12-31 | LT67KNP_43LR_POS_LOCAL | 822 | LTKNP_43LR_POS_LOCAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | DJ - Mola Descarregada | 4 | 0 | 0 | DiVal | 240 | 190 | 1899-12-31 | LT67KNP_MOLA_DESC | 823 | LTKNP_MOLA_DESC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | DJ - Falta VCC Motor | 5 | 0 | 0 | DiVal | 240 | 198 | 1899-12-31 | LT67KNP_FVCC_MOTOR | 824 | LTKNP_FVCC_MOTOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | DJ - Supervisão Circuito TRIP - Alarme | 6 | 0 | 0 | DiVal | 170 | 55 | 1899-12-31 | LT67KNP_CIRC_TRIP_FALHA | 825 | LTKNP_CIRC_TRIP_FALHA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Reserva | 7 | 0 | 0 | - | - | - | - | Reserva | - | Reserva | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Sinal Relé 02F1 (F21) - Excluir Telecomando COS | 16 | 0 | 0 | - | - | - | - | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Sinal Rele 02F1 (F21) - Excluir 79 | 17 | 0 | 0 | - | - | - | - | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | B69 | 86FD /AT - Atuado | 18 | 0 | 0 | DiVal | 240 | 195 | 1899-12-31 | B69_86FD_ATUADO | 826 | B69_86FD_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Operação Indevida da Seccionadoras Isoladoras | 19 | 0 | 0 | DiVal | 240 | 194 | 1899-12-31 | LT67KNP_OP_INDEV_SECC | 827 | LTKNP_OP_INDEV_SECC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Reserva | 20 - 33 | 0 | 0 | - | - | - | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | DJ - Chave 43TC Excluida | 0 | 0 | 0 | DiVal | 101 | 85 | 1899-12-31 | LT67KNP_43TC_EXCLUIDA | 828 | LTKNP_43TC_EXCLUIDA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | 79 - Disparo | 0 | 0 | 0 | DiVal | 160 | 128 | 1899-12-31 | LT67KNP_79_DISPARO | 829 | LT67KNP_79_DISPARO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | 79 - Excluído | 0 | 0 | 0 | DiVal | 40 | 81 | 1899-12-31 | LT67KNP_79_EXCLUIDO | 830 | LTKNP_79_EXCLUIDO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | 79 - Religamento Sucedido | 0 | 0 | 0 | DiVal | 40 | 162 | 1899-12-31 | LT67KNP_79_SUCEDIDO | 831 | LT67KNP_79_SUCEDIDO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | 79 - Bloqueado (Lockout) | 0 | 0 | 0 | FaltDi | 40 | 163 | 1900-01-01 | LT67KNP_79_BLOQUEADO | 832 | LT67KNP_79_BLOQUEADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Reserva | 0 | 0 | 0 | - | - | - | - | Reserva | - | Reserva | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuado 50 BF | 0 | 0 | 0 | Auto Fault | 160 | 85 | 1900-01-01 | LT67KNP_50BF_ATUADO | 833 | LT67KNP_50BF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Prot.67 - Bloqueada | 0 | 0 | 0 | DiVal | 63 | 11 | 1899-12-31 | LT67KNP_67_BLOQUEADA | 834 | LT67KNP_67_BLOQUEADA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuado 67-1 | 0 | 0 | 0 | Fault Di | 63 | 25 | 1900-01-01 | LT67KNP_67_1_ATUADO | 835 | LT67KNP_67_1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuado 67-2 | 0 | 0 | 0 | Fault Di | 63 | 72 | 1900-01-01 | LT67KNP_67_2_ATUADO | 836 | LT67KNP_67_2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuado 67 - TOC | 0 | 0 | 0 | Fault Di | 63 | 35 | 1900-01-01 | LT67KNP_67TOC_ATUADO | 837 | LT67KNP_67TOC_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuado 67N-1 | 0 | 0 | 0 | Fault Di | 63 | 43 | 1900-01-01 | LT67KNP_67N_1_ATUADO | 838 | LT67KNP_67N_1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuado 67N-2 | 0 | 0 | 0 | Fault Di | 63 | 64 | 1900-01-01 | LT67KNP_67N_2_ATUADO | 839 | LT67KNP_67N_2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuado 67N - TOC | 0 | 0 | 0 | Fault Di | 63 | 46 | 1900-01-01 | LT67KNP_67N_TOC_ATUADO | 840 | LT67KNP_67N_TOC_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuado 67 - Fase A | 0 | 0 | 0 | Fault Di | 63 | 75 | 1900-01-01 | LT67KNP_67_FA_ATUADO | 841 | LT67KNP_67_FA_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuado 67 - Fase B | 0 | 0 | 0 | Fault Di | 63 | 76 | 1900-01-01 | LT67KNP_67_FB_ATUADO | 842 | LT67KNP_67_FB_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuado 67 - Fase C | 0 | 0 | 0 | Fault Di | 63 | 77 | 1900-01-01 | LT67KNP_67_FC_ATUADO | 843 | LT67KNP_67_FC_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Supervisão Medição: Falha Fusível TPs | 0 | 0 | 0 | DiVal | 135 | 149 | 1899-12-31 | LT67KNP_60FF_ALARME | 844 | LT67KNP_60FF_ALARME | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Localiz.Defeito - Disparo | 0 | 0 | 0 | DiVal | 151 | 7 | 1899-12-31 | LT67KNP_LDF_ATUADO | 845 | LT67KNP_LDF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuada Proteção Sub-Frequencia - E1 | 0 | 0 | 0 | Fdi | 70 | 234 | 1900-01-01 | LT67KNP_81U_E1_ATUADO | 846 | LT67KNP_81U_E1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuada Proteção Sub-Frequencia - E2 | 0 | 0 | 0 | Fdi | 70 | 235 | 1900-01-01 | LT67KNP_81U_E2_ATUADO | 847 | LT67KNP_81U_E2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuada Proteção Sobre-Frequencia - E1 | 0 | 0 | 0 | Fdi | 70 | 236 | 1900-01-01 | LT67KNP_81O_E1_ATUADO | 848 | LT67KNP_81O_E1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuada Proteção Sobre-Frequencia - E2 | 0 | 0 | 0 | Fdi | 70 | 237 | 1900-01-01 | LT67KNP_81O_E2_ATUADO | 849 | LT67KNP_81O_E2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuada Proteção 27 | 0 | 0 | 0 | FDi | 74 | 81 | 1900-01-01 | LT67KNP_27_ATUADO | 850 | LT67KNP_27_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Atuada Proteção 59 | 0 | 0 | 0 | FDi | 74 | 83 | 1900-01-01 | LT67KNP_59_ATUADO | 851 | LT67KNP_59_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | 25 diferença de Tensão | 0 | 0 | 0 | DiVal | 254 | 130 | 1899-12-31 | LT67KNP_25_V_DIFF | 852 | LTKNP_25_V_DIFF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | 25 diferença de Frequência | 0 | 0 | 0 | DiVal | 254 | 129 | 1899-12-31 | LT67KNP_25_HZ_DIFF | 853 | LTKNP_25_HZ_DIFF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | 25 diferença de Ângulo | 0 | 0 | 0 | DiVal | 254 | 128 | 1899-12-31 | LT67KNP_25_ANG_DIFF | 854 | LTKNP_25_ANG_DIFF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | 25 Supervisiona 79 | 0 | 0 | 0 | DiVal | 254 | 127 | 1899-12-31 | LT67KNP_25_SUP_79 | 855 | LT67KNP_25_SUP_79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Saúde Comunicação | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 856 | LT67KNP_SAUDE_COMUNIC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Dj.52-04 – Aberto | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | LT21KNP_DJ_ABERTO | IDF | LTKNP_DJ_ABERTO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Dj.52-04 – Fechado | 2 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | LT21KNP_DJ_FECHADO | IDF | LTKNP_DJ_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Seccion. 29-12 (329E) - Aberto | 8 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | LT21KNP_S89E_ABERTA | IDF | LTKNP_S89E_ABERTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Seccion. 29-12 (329E) - Fechado | 9 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | LT21KNP_S89E_FECHADO | IDF | LTKNP_S89E_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Seccion. 29-10 (329D) - Aberto | 10 | 0 | 0 | DiSOEx2 | 240 | 162 | 1899-12-31 | LT21KNP_S89D_ABERTA | IDF | LTKNP_S89D_ABERTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Seccion. 29-10 (329D) - Fechado | 11 | 0 | 0 | DiSOEx2 | 240 | 162 | 1899-12-31 | LT21KNP_S89D_FECHADO | IDF | LTKNP_S89D_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Seccion. 29-14 (329C) - Aberto | 12 | 0 | 0 | DiSOEx2 | 240 | 163 | 1899-12-31 | LT21KNP_S89C_ABERTA | IDF | LTKNP_S89C_ABERTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Seccion. 29-14 (329C) - Fechado | 13 | 0 | 0 | DiSOEx2 | 240 | 163 | 1899-12-31 | LT21KNP_S89C_FECHADO | IDF | LTKNP_S89C_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Seccion. 29-01 (229T) - Aberto | 14 | 0 | 0 | DiSOEx2 | 240 | 165 | 1899-12-31 | LT21KNP_S29T_ABERTA | IDF | LTKNP_S29T_ABERTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Seccion. 29-01 (229T) - Fechado | 15 | 0 | 0 | DiSOEx2 | 240 | 165 | 1899-12-31 | LT21KNP_S29T_FECHADO | IDF | LTKNP_S29T_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | DJ - SF6 - Alarme | 0 | 0 | 0 | DiVal | 240 | 191 | 1899-12-31 | LT21KNP_DJ_SF6_ALARME | IDF | LTKNP_DJ_SF6_ALARME | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | DJ - SF6 - Bloqueio | 0 | 0 | 0 | DiVal | 240 | 190 | 1899-12-31 | LT21KNP_DJ_SF6_BLOQUEIO | IDF | LTKNP_DJ_SF6_BLOQUEIO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | DJ - 43LR - Posição LOCAL | 3 | 0 | 0 | DiVal | 240 | 193 | 1899-12-31 | LT21KNP_43LR_POS_LOCAL | IDF | LTKNP_43LR_POS_LOCAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | DJ - Mola Descarregada | 4 | 0 | 0 | DiVal | 240 | 192 | 1899-12-31 | LT21KNP_MOLA_DESC | IDF | LTKNP_MOLA_DESC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | DJ - Falta VCC Motor | 5 | 0 | 0 | DiVal | 240 | 198 | 1899-12-31 | LT21KNP_FVCC_MOTOR | IDF | LTKNP_FVCC_MOTOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | DJ - Supervisão Circuito TRIP - Alarme | 6 | 0 | 0 | DiVal | 170 | 55 | 1899-12-31 | LT21KNP_CIRC_TRIP_FALHADO | OR | LTKNP_CIRC_TRIP_FALHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Reserva | 7 | 0 | 0 | - | - | - | - | Reserva | - | Reserva | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Sinal Relé 25F2 (F67) - Excluir Telecomando COS | 16 | 0 | 0 | - | - | - | - | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Sinal Rele 25F2(F67) - Excluir 79 | 17 | 0 | 0 | - | - | - | - | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | B69 | 86FD /AT - Atuado | 18 | 0 | 0 | DiVal | 240 | 195 | 1899-12-31 | B69_86FD_ATUADO | OR | B69_86FD_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Operação Indevida da Seccionadoras Isoladoras | 19 | 0 | 0 | DiVal | 240 | 196 | 1899-12-31 | LT21KNP_OP_INDEV_SECC | OR | LTKNP_OP_INDEV_SECC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Reserva | 20 | 0 | 0 | - | - | - | - | Reserva | - | Reserva | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | DJ - Chave 43TC Excluida | 0 | 10 | 0 | DiVal | 101 | 85 | 1899-12-31 | LT21KNP_43TC_EXCLUIDA | OR | LTKNP_43TC_EXCLUIDA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | 79 - Disparo | 0 | 0 | 0 | AutoDi | 160 | 128 | 1899-12-31 | LT21KNP_79_DISPARO | 860 | LT21KNP_79_DISPARO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | 79 - Excluído | 0 | 0 | 0 | DiVal | 40 | 81 | 1899-12-31 | LT21KNP_79_EXCLUIDO | OR | LTKNP_79_EXCLUIDO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | 79 - Religamento Sucedido | 0 | 0 | 0 | AutoDi | 40 | 162 | 1899-12-31 | LT21KNP_79_SUCEDIDO | 861 | LT21KNP_79_SUCEDIDO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | 79 - Definitive TRIP (Lockout) | 0 | 0 | 0 | Fault Di | 150 | 180 | 1900-01-01 | LT21KNP_79_BLOQUEADO | 862 | LT21KNP_79_BLOQUEADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Reserva | 0 | 0 | 0 | - | - | - | - | Reserva | - | Reserva | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 50 BF | 0 | 4 | 0 | Auto Fault | 160 | 85 | 1900-01-01 | LT21KNP_50BF_ATUADO | 863 | LT21KNP_50BF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Prot.21 - Bloqueada | 0 | 0 | 0 | DiVal | 28 | 52 | 1899-12-31 | LT21KNP_21_BLOQUEADA | 864 | LT21KNP_21_BLOQUEADA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 21 Trip Fase A | 0 | 6 | 0 | Fault Di | 28 | 206 | 1900-01-01 | LT21KNP_21FA_ATUADO | 865 | LT21KNP_21FA_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 21 Trip Fase B | 0 | 6 | 0 | Fault Di | 28 | 207 | 1900-01-01 | LT21KNP_21FB_ATUADO | 866 | LT21KNP_21FB_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 21 Trip Fase C | 0 | 6 | 0 | Fault Di | 28 | 208 | 1900-01-01 | LT21KNP_21FC_ATUADO | 867 | LT21KNP_21FC_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 21 N Trip | 0 | 6 | 0 | Fault Di | 28 | 212 | 1900-01-01 | LT21KNP_21N_ATUADO | 868 | LT21KNP_21N_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 21 Trip3p.Z1sf | 0 | 6 | 0 | Auto Fault | 28 | 224 | 1900-01-01 | LT21KNP_21Z1SF_ATUADO | 869 | LT21KNP_21Z1SF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 21 Trip3p.Z1mf | 0 | 6 | 0 | Auto Fault | 28 | 225 | 1900-01-01 | LT21KNP_21Z1MF_ATUADO | 870 | LT21KNP_21Z1MF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 21 Trip3p.Z2 | 0 | 6 | 0 | Auto Fault | 28 | 217 | 1900-01-01 | LT21KNP_21Z2_ATUADO | 871 | LT21KNP_21Z2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 21 Trip3p.Z3 | 0 | 6 | 0 | Auto Fault | 28 | 218 | 1900-01-01 | LT21KNP_21Z3_ATUADO | 872 | LT21KNP_21Z3_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 21 Trip3p.Z4 | 0 | 6 | 0 | Auto Fault | 28 | 209 | 1900-01-01 | LT21KNP_21Z4_ATUADO | 873 | LT21KNP_21Z4_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Ligar DJ Sobre Falha | 0 | 0 | 0 | Auto Fault | 25 | 95 | 1900-01-01 | LT21KNP_50HS_ATUADO | 874 | LT21KNP_50HS_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuado 67N TRIP | 0 | 6 | 0 | Auto Fault | 166 | 69 | 1900-01-01 | LT21KNP_67N_ATUADO | 875 | LT21KNP_67N_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Atuada Proteção Backup: 5XB TRIP | 0 | 6 | 0 | Auto Fault | 128 | 72 | 1900-01-01 | LT21KNP_5XB_ATUADO | 876 | LT21KNP_5XB_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Supervisão Medição: Falha Fusível TPs | 0 | 0 | 0 | DiVal | 135 | 149 | 1899-12-31 | LT21KNP_60FF_ALARME | 877 | LT21KNP_60FF_ALARME | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Localiz.Defeito - Disparo | 0 | 0 | 0 | DiVal | 151 | 7 | 1899-12-31 | LT21KNP_LDF_ATUADO | 878 | LT21KNP_LDF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | 25 diferença de Tensão | 0 | 0 | 0 | DiVal | 254 | 130 | 1899-12-31 | LT21KNP_25_V_DIFF | OR | LTKNP_25_V_DIFF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | 25 diferença de Frequência | 0 | 0 | 0 | DiVal | 254 | 129 | 1899-12-31 | LT21KNP_25_HZ_DIFF | OR | LTKNP_25_HZ_DIFF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | 25 diferença de Ângulo | 0 | 0 | 0 | DiVal | 254 | 128 | 1899-12-31 | LT21KNP_25_ANG_DIFF | OR | LTKNP_25_ANG_DIFF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Saúde Comunicação | 0 | 0 | 0 | - | - | - | - | 0 | 879 | LT21KNP_SAUDE_COMUNIC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Disjuntor 52-18 – Aberto | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | LT67CAS_DJ_ABERTO | 890 | LTCAS_DJ_ABERTO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Disjuntor 52-18 – Fechado | 2 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | LT67CAS_DJ_FECHADO | 891 | LTCAS_DJ_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.89-108 (S89E) - Aberto | 8 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | LT67CAS_S329E_ABERTO | 892 | LTCAS_S329E_ABERTO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.89-108 (S89E) - Fechado | 9 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | LT67CAS_S329E_FECHADO | 893 | LTCAS_S329E_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.89-106 (S89D) - Aberto | 10 | 0 | 0 | DiSOEx2 | 240 | 162 | 1899-12-31 | LT67CAS_S329D_ABERTO | 894 | LTCAS_S329D_ABERTO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.89-106 (S89D) - Fechado | 11 | 0 | 0 | DiSOEx2 | 240 | 162 | 1899-12-31 | LT67CAS_S329D_FECHADO | 895 | LTCAS_S329D_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.89-110 (S89C) - Aberto | 12 | 0 | 0 | DiSOEx2 | 240 | 163 | 1899-12-31 | LT67CAS_S329C_ABERTO | 896 | LTCAS_S329C_ABERTO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.89-110 (S89C) - Fechado | 13 | 0 | 0 | DiSOEx2 | 240 | 163 | 1899-12-31 | LT67CAS_S329C_FECHADO | 897 | LTCAS_S329C_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc. 29-03 (S29T) - Aberto | 14 | 0 | 0 | DiSOEx2 | 240 | 165 | 1899-12-31 | LT67CAS_S229T_ABERTO | 898 | LTCAS_S229T_ABERTO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc. 29-03 (S29T) - Fechado | 15 | 0 | 0 | DiSOEx2 | 240 | 165 | 1899-12-31 | LT67CAS_S229T_FECHADO | 899 | LTCAS_S229T_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | DJ - SF6 Alarme | 3 | 0 | 0 | DiVal | 240 | 192 | 1899-12-31 | LT67CAS_SF6_ALARME | 900 | LTCAS_SF6_ALARME | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | DJ - SF6 Abertura e Bloqueio | 4 | 0 | 0 | DiVal | 240 | 191 | 1899-12-31 | LT67CAS_SF6_BLOQUEIO | 901 | LTCAS_SF6_BLOQUEIO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | DJ - Mola Descarregada | 5 | 0 | 0 | DiVal | 240 | 190 | 1899-12-31 | LT67CAS_MOLA_DESC | 902 | LTCAS_MOLA_DESC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | DJ - 43LR - Posição LOCAL | 6 | 0 | 0 | DiVal | 240 | 193 | 1899-12-31 | LT67CAS_43LR_POS_LOCAL | 903 | LTCAS_43LR_POS_LOCAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | DJ - Falta VCC CMD/VCA AQUEC | 7 | 0 | 0 | DiVal | 240 | 198 | 1899-12-31 | LT67CAS_FALTA_VCA_VCC | 904 | LTCAS_FALTA_VCA_VCC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Sinal Relé (F21) - Excluir Telecomando COS | 16 | 0 | 0 | - | - | - | - | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Sinal Rele (F21) - Excluir 79 | 17 | 0 | 0 | - | - | - | - | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | B138 | 86FD /AT - Atuado | 18 | 0 | 0 | DiVal | 240 | 195 | 1899-12-31 | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | DJ - Supervisão Circuito TRIP - Alarme | 20 | 0 | 0 | DiVal | 170 | 55 | 1899-12-31 | LT67CAS_CIRC_TRIP_FALHA | 906 | LTCAS_CIRC_TRIP_FALHA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.(89-108) - 43LR - Posição LOCAL | 21 | 0 | 0 | DiVal | 240 | 196 | 1899-12-31 | LT67CAS_S289E_43LR | 907 | LT67CAS_S289E_43LR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.(89-108)-VCC CMD/MOTOR | 22 | 0 | 0 | DiVal | 240 | 197 | 1899-12-31 | LT67CAS_S289E_DEF_INTERN | 908 | LT67CAS_S289E_DEF_INTERN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.(89-106) - 43LR - Posição LOCAL | 23 | 0 | 0 | DiVal | 240 | 199 | 1899-12-31 | LT67CAS_S289D_43LR | 909 | LT67CAS_S289D_43LR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.(89-106)-VCC CMD/MOTOR | 24 | 0 | 0 | DiVal | 240 | 200 | 1899-12-31 | LT67CAS_S289D_DEF_INTERN | 910 | LT67CAS_S289D_DEF_INTERN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.(89-110) - 43LR - Posição LOCAL | 25 | 0 | 0 | DiVal | 240 | 201 | 1899-12-31 | LT67CAS_S289C_43LR | 911 | LT67CAS_S289C_43LR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Secc.(89-110)-VCC CMD/MOTOR | 26 | 0 | 0 | DiVal | 240 | 202 | 1899-12-31 | LT67CAS_S289C_DEF_INTERN | 912 | LT67CAS_S289C_DEF_INTERN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Operação Indevida das Secc.Isoladoras | 33 | 0 | 0 | DiVal | 240 | 194 | 1899-12-31 | LT67CAS_OPER_INDEV_SECC | 913 | LTCAS_OPER_INDEV_SECC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | TRIP LT PCH Autodromo | 0 | 0 | 0 | DiVal | 240 | 203 | 1899-12-31 | LT67CAS_TRIP_LT_AUTODROMO | 914 | LT67CAS_TRIP_LT_AUTODROMO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | DJ - Chave 43TC Excluida | 0 | 0 | 0 | DiVal | 101 | 85 | 1899-12-31 | LT67CAS_43TC_EXCLUIDA | 915 | LTCAS_43TC_EXCLUIDA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | 79 supervisionado pelo 25 | 0 | 0 | 0 | DiVal | 160 | 129 | 1899-12-31 | LT67CAS_25_SUPERV_79 | 916 | LT67CAS_25_SUPERV_79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | 79 - Excluído | 0 | 0 | 0 | DiVal | 40 | 81 | 1899-12-31 | LT67CAS_79_EXCLUIDO | 917 | LTCAS_79_EXCLUIDO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | 79 - Religamento Sucedido | 0 | 0 | 0 | DiVal | 40 | 162 | 1899-12-31 | LT67CAS_79_SUCEDIDO | 918 | LT67CAS_79_SUCEDIDO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | 79 - Bloqueado (Lockout) | 0 | 0 | 0 | FaltDi | 40 | 163 | 1900-01-01 | LT67CAS_79_BLOQUEADO | 919 | LT67CAS_79_BLOQUEADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | 25 - Falha Operação Sincronismo | 0 | 0 | 0 | AutoDi | 41 | 35 | 1899-12-31 | LT67CAS_25_FALHA_SINCRO | 920 | LTCAS_25_FALHA_SINCRO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuado 50 BF | 0 | 0 | 0 | Auto Fault | 160 | 85 | 1900-01-01 | LT67CAS_50BF_ATUADO | 921 | LT67CAS_50BF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Prot.67 - Bloqueada | 0 | 0 | 0 | DiVal | 63 | 11 | 1899-12-31 | LT67CAS_67_BLOQUEADA | 922 | LT67CAS_67_BLOQUEADA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuado 67-1 | 0 | 0 | 0 | Fault Di | 63 | 25 | 1900-01-01 | LT67CAS_67_1_ATUADO | 923 | LT67CAS_67_1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuado 67-2 | 0 | 0 | 0 | Fault Di | 63 | 72 | 1900-01-01 | LT67CAS_67_2_ATUADO | 924 | LT67CAS_67_2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuado 67 - TOC | 0 | 0 | 0 | Fault Di | 63 | 35 | 1900-01-01 | LT67CAS_67TOC_ATUADO | 925 | LT67CAS_67TOC_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuado 67N-1 | 0 | 0 | 0 | Fault Di | 63 | 43 | 1900-01-01 | LT67CAS_67N_1_ATUADO | 926 | LT67CAS_67N_1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuado 67N-2 | 0 | 0 | 0 | Fault Di | 63 | 64 | 1900-01-01 | LT67CAS_67N_2_ATUADO | 927 | LT67CAS_67N_2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuado 67N - TOC | 0 | 0 | 0 | Fault Di | 63 | 46 | 1900-01-01 | LT67CAS_67N_TOC_ATUADO | 928 | LT67CAS_67N_TOC_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuado 67 - Fase A | 0 | 0 | 0 | Fault Di | 63 | 75 | 1900-01-01 | LT67CAS_67_FA_ATUADO | 929 | LT67CAS_67_FA_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuado 67 - Fase B | 0 | 0 | 0 | Fault Di | 63 | 76 | 1900-01-01 | LT67CAS_67_FB_ATUADO | 930 | LT67CAS_67_FB_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuado 67 - Fase C | 0 | 0 | 0 | Fault Di | 63 | 77 | 1900-01-01 | LT67CAS_67_FC_ATUADO | 931 | LT67CAS_67_FC_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Supervisão Medição: Falha Fusível TPs | 0 | 0 | 0 | DiVal | 135 | 149 | 1899-12-31 | LT67CAS_60FF_ALARME | 932 | LT67CAS_60FF_ALARME | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Falta Tensão LT - Alarme | 0 | 0 | 0 | DiVal | 240 | 204 | 1899-12-31 | LT67CAS_FALTA_TENSAO_LT | 933 | LTCAS_FALTA_TENSAO_LT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Localiz.Defeito - Disparo | 0 | 0 | 0 | DiVal | 151 | 7 | 1899-12-31 | LT67CAS_LDF_ATUADO | 934 | LT67CAS_LDF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuada Proteção Sub-Frequencia - E1 | 0 | 0 | 0 | Fdi | 70 | 234 | 1900-01-01 | LT67CAS_81U_E1_ATUADO | 935 | LT67CAS_81U_E1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuada Proteção Sub-Frequencia - E2 | 0 | 0 | 0 | Fdi | 70 | 235 | 1900-01-01 | LT67CAS_81U_E2_ATUADO | 936 | LT67CAS_81U_E2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuada Proteção Sobre-Frequencia - E1 | 0 | 0 | 0 | Fdi | 70 | 236 | 1900-01-01 | LT67CAS_81O_E1_ATUADO | 937 | LT67CAS_81O_E1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuada Proteção Sobre-Frequencia - E2 | 0 | 0 | 0 | Fdi | 70 | 237 | 1900-01-01 | LT67CAS_81O_E2_ATUADO | 938 | LT67CAS_81O_E2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuada Proteção 27 | 0 | 0 | 0 | FDi | 74 | 81 | 1900-01-01 | LT67CAS_27_ATUADO | 939 | LT67CAS_27_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Atuada Proteção 59 | 0 | 0 | 0 | FDi | 74 | 83 | 1900-01-01 | LT67CAS_59_ATUADO | 940 | LT67CAS_59_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Saúde Comunicação | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 941 | LT67CAS_SAUDE_COMUNIC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Disjuntor 52-18 – Aberto | 1 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | LT21CAS_DJ_ABERTO | IDF | LTCAS_DJ_ABERTO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Disjuntor 52-18 – Fechado | 2 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | LT21CAS_DJ_FECHADO | IDF | LTCAS_DJ_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Secc.89-108 (S89E) - Aberto | 8 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | LT21CAS_S329E_ABERTO | IDF | LTCAS_S329E_ABERTO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Secc.89-108 (S89E) - Fechado | 9 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | LT21CAS_S329E_FECHADO | IDF | LTCAS_S329E_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Secc.89-106 (S89D) - Aberto | 10 | 0 | 0 | DiSOEx2 | 240 | 162 | 1899-12-31 | LT21CAS_S329D_ABERTO | IDF | LTCAS_S329D_ABERTO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Secc.89-106 (S89D) - Fechado | 11 | 0 | 0 | DiSOEx2 | 240 | 162 | 1899-12-31 | LT21CAS_S329D_FECHADO | IDF | LTCAS_S329D_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Secc.89-110 (S89C) - Aberto | 12 | 0 | 0 | DiSOEx2 | 240 | 163 | 1899-12-31 | LT21CAS_S329C_ABERTO | IDF | LTCAS_S329C_ABERTO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Secc.89-110 (S89C) - Fechado | 13 | 0 | 0 | DiSOEx2 | 240 | 163 | 1899-12-31 | LT21CAS_S329C_FECHADO | IDF | LTCAS_S329C_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Secc. 29-03 (S29T) - Aberto | 14 | 0 | 0 | DiSOEx2 | 240 | 165 | 1899-12-31 | LT21CAS_S229T_ABERTO | IDF | LTCAS_S229T_ABERTO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Secc. 29-03 (S29T) - Fechado | 15 | 0 | 0 | DiSOEx2 | 240 | 165 | 1899-12-31 | LT21CAS_S229T_FECHADO | IDF | LTCAS_S229T_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | DJ - SF6 Alarme | 3 | 0 | 0 | DiVal | 240 | 190 | 1899-12-31 | LT21CAS_SF6_ALARME | IDF | LTCAS_SF6_ALARME | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | DJ - SF6 Abertura e Bloqueio | 4 | 0 | 0 | DiVal | 240 | 191 | 1899-12-31 | LT21CAS_SF6_BLOQUEIO | IDF | LTCAS_SF6_BLOQUEIO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | DJ - Mola Descarregada/Falta VCC Motor | 5 | 0 | 0 | DiVal | 240 | 192 | 1899-12-31 | LT21CAS_MOLA_DESC | IDF | LTCAS_MOLA_DESC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | DJ - 43LR - Posição LOCAL | 6 | 0 | 0 | DiVal | 240 | 193 | 1899-12-31 | LT21CAS_43LR_POS_LOCAL | IDF | LTCAS_43LR_POS_LOCAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Falta VCC CMD/VCA AQUEC | 7 | 0 | 0 | DiVal | 240 | 194 | 1899-12-31 | LT21CAS_FALTA_VCA_VCC | IDF | LTCAS_FALTA_VCA_VCC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Sinal Relé (F67) - Excluir Telecomando COS | 16 | 0 | 0 | - | - | - | - | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Sinal Rele (F67) - Excluir 79 | 17 | 0 | 0 | - | - | - | - | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | B138 | 86FD /AT - Atuado | 18 | 0 | 0 | DiVal | 240 | 195 | 1899-12-31 | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Operação Indevida da Seccs | 19 | 0 | 0 | DiVal | 240 | 196 | 1899-12-31 | LT21CAS_OP_INDEV_SECC | OR | LTCAS_OP_INDEV_SECC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | DJ - Supervisão Circuito TRIP - Alarme | 20 | 0 | 0 | DiVal | 170 | 55 | 1899-12-31 | LT21CAS_CIRC_TRIP_FALHADO | OR | LTCAS_CIRC_TRIP_FALHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | TRIP LT PCH Autodromo | 0 | 0 | 0 | DiVal | 240 | 203 | 1899-12-31 | LT21CAS_TRIP_LT_AUTODROMO | 945 | LT21CAS_TRIP_LT_AUTODROMO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | DJ - Chave 43TC Excluida | 0 | 0 | 0 | DiVal | 101 | 85 | 1899-12-31 | LT21CAS_43TC_EXCLUIDA | OR | LTCAS_43TC_EXCLUIDA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | 79 - Disparo | 0 | 0 | 0 | AutoDi | 160 | 128 | 1899-12-31 | LT21CAS_79_DISPARO | 946 | LT21CAS_79_DISPARO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | 79 - Excluído | 0 | 0 | 0 | DiVal | 40 | 81 | 1899-12-31 | LT21CAS_79_EXCLUIDO | OR | LTCAS_79_EXCLUIDO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | 79 - Religamento Sucedido | 0 | 0 | 0 | AutoDi | 40 | 162 | 1899-12-31 | LT21CAS_79_SUCEDIDO | 947 | LT21CAS_79_SUCEDIDO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | 79 - Definiteve TRIP (Lockout) | 0 | 0 | 0 | Fault Di | 150 | 180 | 1900-01-01 | LT21CAS_79_BLOQUEADO | 948 | LT21CAS_79_BLOQUEADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | 25 - Falha Operação Sincronismo | 0 | 0 | 0 | AutoDi | 41 | 83 | 1899-12-31 | LT21CAS_25_FALHA_SINCRO | OR | LTCAS_25_FALHA_SINCRO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 50 BF | 0 | 0 | 0 | Auto Fault | 160 | 85 | 1900-01-01 | LT21CAS_50BF_ATUADO | 949 | LT21CAS_50BF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Prot.21 - Bloqueada | 0 | 0 | 0 | DiVal | 28 | 52 | 1899-12-31 | LT21CAS_21_BLOQUEADA | 950 | LT21CAS_21_BLOQUEADA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 21 Trip Fase A | 0 | 0 | 0 | Fault Di | 28 | 206 | 1900-01-01 | LT21CAS_21FA_ATUADO | 951 | LT21CAS_21FA_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 21 Trip Fase B | 0 | 0 | 0 | Fault Di | 28 | 207 | 1900-01-01 | LT21CAS_21FB_ATUADO | 952 | LT21CAS_21FB_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 21 Trip Fase C | 0 | 0 | 0 | Fault Di | 28 | 208 | 1900-01-01 | LT21CAS_21FC_ATUADO | 953 | LT21CAS_21FC_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 21 N Trip | 0 | 0 | 0 | Fault Di | 28 | 212 | 1900-01-01 | LT21CAS_21N_ATUADO | 954 | LT21CAS_21N_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 21 Trip3p.Z1sf | 0 | 0 | 0 | Auto Fault | 28 | 224 | 1900-01-01 | LT21CAS_21Z1SF_ATUADO | 955 | LT21CAS_21Z1SF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 22 Trip3p.Z1mf | 0 | 0 | 0 | Auto Fault | 28 | 225 | 1900-01-01 | LT21CAS_21Z1MF_ATUADO | 956 | LT21CAS_21Z1MF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 21 Trip3p.Z2 | 0 | 0 | 0 | Auto Fault | 28 | 217 | 1900-01-01 | LT21CAS_21Z2_ATUADO | 957 | LT21CAS_21Z2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 21 Trip3p.Z3 | 0 | 0 | 0 | Auto Fault | 28 | 218 | 1900-01-01 | LT21CAS_21Z3_ATUADO | 958 | LT21CAS_21Z3_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 21 Trip3p.Z4 | 0 | 0 | 0 | Auto Fault | 28 | 209 | 1900-01-01 | LT21CAS_21Z4_ATUADO | 959 | LT21CAS_21Z4_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Ligar DJ Sobre Falha | 0 | 0 | 0 | Auto Fault | 25 | 95 | 1900-01-01 | LT21CAS_50HS_ATUADO | 960 | LT21CAS_50HS_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuado 67N TRIP | 0 | 0 | 0 | Auto Fault | 166 | 69 | 1900-01-01 | LT21CAS_67N_ATUADO | 961 | LT21CAS_67N_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Atuada Proteção Backup: 5XB TRIP | 0 | 0 | 0 | Auto Fault | 128 | 72 | 1900-01-01 | LT21CAS_5XB_ATUADO | 962 | LT21CAS_5XB_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Supervisão Medição: Falha Fusível TPs | 0 | 0 | 0 | DiVal | 135 | 149 | 1899-12-31 | LT21CAS_60FF_ALARME | 963 | LT21CAS_60FF_ALARME | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Falta Tensão LT - Alarme | 0 | 0 | 0 | DiVal | 240 | 204 | 1899-12-31 | LT21CAS_FALTA_TENSAO_LT | OR | LTCAS_FALTA_TENSAO_LT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Localiz.Defeito - Disparo | 0 | 0 | 0 | DiVal | 151 | 7 | 1899-12-31 | LT21CAS_LDF_ATUADO | 964 | LT21CAS_LDF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Saúde Comunicação | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LT21CAS_SAUDE_COMUNIC | 965 | LT21CAS_SAUDE_COMUNIC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Disjuntor 52-20 – Aberto | 0 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | LT67ARV_DJ_ABERTO | 980 | LTARV_DJ_ABERTO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Disjuntor 52-20 – Fechado | 0 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | LT67ARV_DJ_FECHADO | 981 | LTARV_DJ_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.89-120 - Aberto | 0 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | LT67ARV_S26QB_ABERTA | 982 | LTARV_S26QB_ABERTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.89-120 - Fechado | 0 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | LT67ARV_S26QB_FECHADA | 983 | LTARV_S26QB_FECHADA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.89-118 - Aberto | 0 | 0 | 0 | DiSOEx2 | 240 | 162 | 1899-12-31 | LT67ARV_S26QC_ABERTA | 984 | LTARV_S26QC_ABERTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.89-118 - Fechado | 0 | 0 | 0 | DiSOEx2 | 240 | 162 | 1899-12-31 | LT67ARV_S26QC_FECHADA | 985 | LTARV_S26QC_FECHADA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.89-122 - Aberto | 0 | 0 | 0 | DiSOEx2 | 240 | 163 | 1899-12-31 | LT67ARV_S26QD_ABERTA | 986 | LTARV_S26QD_ABERTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.89-122 - Fechado | 0 | 0 | 0 | DiSOEx2 | 240 | 163 | 1899-12-31 | LT67ARV_S26QD_FECHADA | 987 | LTARV_S26QD_FECHADA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Seccion. 29-07 - Aberto | 0 | 0 | 0 | DiSOEx2 | 240 | 164 | 1899-12-31 | LT67ARV_S29T_ABERTA | 988 | LTARV_S29T_ABERTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Seccion. 29-07 - Fechado | 0 | 0 | 0 | DiSOEx2 | 240 | 164 | 1899-12-31 | LT67ARV_S29T_FECHADA | 989 | LTARV_S29T_FECHADA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | DJ - SF6 Alarme | 0 | 0 | 0 | DiVal | 240 | 192 | 1899-12-31 | LT67ARV_SF6_ALARME | 990 | LTARV_SF6_ALARME | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | DJ - SF6 Abertura e Bloqueio | 0 | 0 | 0 | DiVal | 240 | 191 | 1899-12-31 | LT67ARV_SF6_BLOQUEIO | 991 | LTARV_SF6_BLOQUEIO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | DJ - Mola Descarregada | 0 | 0 | 0 | DiVal | 240 | 190 | 1899-12-31 | LT67ARV_MOLA_DESC | 992 | LTARV_MOLA_DESC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | DJ - 43LR - Posição LOCAL | 0 | 0 | 0 | DiVal | 240 | 193 | 1899-12-31 | LT67ARV_43LR_POS_LOCAL | 993 | LTARV_43LR_POS_LOCAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | DJ - Falta VCC CMD/VCA AQUEC | 0 | 0 | 0 | DiVal | 240 | 194 | 1899-12-31 | LT67ARV_FALTA_VCA_VCC | 994 | LTARV_FALTA_VCA_VCC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Sinal Relé (F21) - Excluir Telecomando COS | 0 | 0 | 0 | - | 0 | 0 | 1899-12-31 | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Sinal Rele (F21) - Excluir 79 | 0 | 0 | 0 | - | 0 | 0 | 1899-12-31 | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | DJ - Supervisão Circuito TRIP - Alarme | 0 | 0 | 0 | DiVal | 170 | 55 | 1899-12-31 | LT67ARV_CIRC_TRIP_FALHA | 995 | LTARV_CIRC_TRIP_FALHA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.(89-120) - 43LR - Posição LOCAL | 0 | 0 | 0 | DiVal | 240 | 196 | 1899-12-31 | LT67ARV_S289B_43LR | 996 | LT67ARV_S289B_43LR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.(89-120)-VCC CMD/MOTOR | 0 | 0 | 0 | DiVal | 240 | 197 | 1899-12-31 | LT67ARV_S289B_DEF_INTERN | 997 | LT67ARV_S289B_DEF_INTERN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.(89-118) - 43LR - Posição LOCAL | 0 | 0 | 0 | DiVal | 240 | 200 | 1899-12-31 | LT67ARV_S289D_43LR | 998 | LT67ARV_S289D_43LR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.(89-118)-VCC CMD/MOTOR | 0 | 0 | 0 | DiVal | 240 | 201 | 1899-12-31 | LT67ARV_S289D_DEF_INTERN | 999 | LT67ARV_S289D_DEF_INTERN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.(89-122) - 43LR - Posição LOCAL | 0 | 0 | 0 | DiVal | 240 | 198 | 1899-12-31 | LT67ARV_S289C_43LR | 1000 | LT67ARV_S289C_43LR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Secc.(89-122)-VCC CMD/MOTOR | 0 | 0 | 0 | DiVal | 240 | 199 | 1899-12-31 | LT67ARV_S289C_DEF_INTERN | 1001 | LT67ARV_S289C_DEF_INTERN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Operação Indevida das Secc.Isoladoras | 0 | 0 | 0 | DiVal | 240 | 195 | 1899-12-31 | LT67ARV_OPER_INDEV_SECC | 1002 | LTARV_OPER_INDEV_SECC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | DJ - Chave 43TC Excluida | 0 | 0 | 0 | DiVal | 101 | 85 | 1899-12-31 | LT67ARV_43TC_EXCLUIDA | 1003 | LTARV_43TC_EXCLUIDA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Grupo de Ajustes B - Ativado | 0 | 0 | 0 | DiVal | 160 | 24 | 1899-12-31 | LT67ARV_GRUPOB_ATIVADO | 1004 | LT67ARV_GRUPOB_ATIVADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | 79 supervisionado pelo 25 | 0 | 0 | 0 | Auto DI | 160 | 129 | 1899-12-31 | LT67ARV_25_SUPERV_79 | 1005 | LT67ARV_25_SUPERV_79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | 79 - Excluído | 0 | 0 | 0 | DiVal | 40 | 81 | 1899-12-31 | LT67ARV_79_EXCLUIDO | 1006 | LTARV_79_EXCLUIDO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | 79 - Religamento Sucedido | 0 | 0 | 0 | DiVal | 40 | 162 | 1899-12-31 | LT67ARV_79_SUCEDIDO | 1007 | LT67ARV_79_SUCEDIDO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | 79 - Bloqueado (Lockout) | 0 | 0 | 0 | FaultDI | 40 | 163 | 1900-01-01 | LT67ARV_79_BLOQUEADO | 1008 | LT67ARV_79_BLOQUEADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | 25 - Bloqueado | 0 | 0 | 0 | DiVal | 41 | 204 | 1899-12-31 | LT67ARV_25_BLOQUEADO | 1009 | LT67ARV_25_BLOQUEADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | 25 - Falha Operação Sincronismo | 0 | 0 | 0 | Auto DI | 41 | 35 | 1899-12-31 | LT67ARV_25_FALHA_SINCRO | 1010 | LTARV_25_FALHA_SINCRO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 50 BF | 0 | 0 | 0 | AutoFault | 160 | 85 | 1900-01-01 | LT67ARV_50BF_ATUADO | 1011 | LT67ARV_50BF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Prot.67 - Bloqueada | 0 | 0 | 0 | DiVal | 63 | 11 | 1899-12-31 | LT67ARV_67_BLOQUEADA | 1012 | LT67ARV_67_BLOQUEADA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 67-1 | 0 | 0 | 0 | FaultDI | 63 | 25 | 1900-01-01 | LT67ARV_67_1_ATUADO | 1013 | LT67ARV_67_1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 67-2 | 0 | 0 | 0 | FaultDI | 63 | 72 | 1900-01-01 | LT67ARV_67_2_ATUADO | 1014 | LT67ARV_67_2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 67 - TOC | 0 | 0 | 0 | FaultDI | 63 | 35 | 1900-01-01 | LT67ARV_67TOC_ATUADO | 1015 | LT67ARV_67TOC_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 67N-1 | 0 | 0 | 0 | FaultDI | 63 | 43 | 1900-01-01 | LT67ARV_67N_1_ATUADO | 1016 | LT67ARV_67N_1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 67N-2 | 0 | 0 | 0 | FaultDI | 63 | 64 | 1900-01-01 | LT67ARV_67N_2_ATUADO | 1017 | LT67ARV_67N_2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 67N - TOC | 0 | 0 | 0 | FaultDI | 63 | 46 | 1900-01-01 | LT67ARV_67N_TOC_ATUADO | 1018 | LT67ARV_67N_TOC_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 67 - Fase A | 0 | 0 | 0 | FaultDI | 63 | 75 | 1900-01-01 | LT67ARV_67_FA_ATUADO | 1019 | LT67ARV_67_FA_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 67 - Fase B | 0 | 0 | 0 | FaultDI | 63 | 76 | 1900-01-01 | LT67ARV_67_FB_ATUADO | 1020 | LT67ARV_67_FB_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 67 - Fase C | 0 | 0 | 0 | FaultDI | 63 | 77 | 1900-01-01 | LT67ARV_67_FC_ATUADO | 1021 | LT67ARV_67_FC_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Supervisão Medição: Falha Fusível TPs | 0 | 0 | 0 | DiVal | 135 | 149 | 1899-12-31 | LT67ARV_60FF_ALARME | 1022 | LT67ARV_60FF_ALARME | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Falta Tensão LT - Alarme | 0 | 0 | 0 | DiVal | 240 | 217 | 1899-12-31 | LT67ARV_FALTA_TENSAO_LT | 1023 | LTARV_FALTA_TENSAO_LT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Localiz.Defeito - Disparo | 0 | 0 | 0 | DiVal | 151 | 7 | 1899-12-31 | LT67ARV_LDF_ATUADO | 1024 | LT67ARV_LDF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuada Proteção Sub-Frequencia - E1 | 0 | 0 | 0 | FaultDI | 70 | 234 | 1900-01-01 | LT67ARV_81U_E1_ATUADO | 1025 | LT67ARV_81U_E1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuada Proteção Sobre-Frequencia - E1 | 0 | 0 | 0 | FaultDI | 70 | 236 | 1900-01-01 | LT67ARV_81O_E1_ATUADO | 1026 | LT67ARV_81O_E1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 50-1 | 0 | 0 | 0 | AutoFault | 160 | 90 | 1900-01-01 | LT50ARV_50_1_ATUADO | 1027 | LT50ARV_50_1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 50-2 | 0 | 0 | 0 | AutoFault | 160 | 91 | 1900-01-01 | LT50ARV_50_2_ATUADO | 1028 | LT50ARV_50_2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 51 | 0 | 0 | 0 | FaultDI | 60 | 58 | 1900-01-01 | LT50ARV_51F_ATUADO | 1029 | LT50ARV_51F_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 50N-1 | 0 | 0 | 0 | AutoFault | 160 | 92 | 1900-01-01 | LT50ARV_50N_1_ATUADO | 1030 | LT50ARV_50N_1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 50N-2 | 0 | 0 | 0 | AutoFault | 160 | 93 | 1900-01-01 | LT50ARV_50N_2_ATUADO | 1031 | LT50ARV_50N_2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuado 51N | 0 | 0 | 0 | FaultDI | 60 | 66 | 1900-01-01 | LT50ARV_51N_ATUADO | 1032 | LT50ARV_51N_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuada Proteção 27 | 0 | 0 | 0 | FaultDI | 74 | 81 | 1900-01-01 | LT67ARV_27_ATUADO | 1033 | LT67ARV_27_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Atuada Proteção 59 | 0 | 0 | 0 | FaultDI | 74 | 83 | 1900-01-01 | LT67ARV_59_ATUADO | 1034 | LT67ARV_59_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | 25 diferença de Tensão | 0 | 0 | 0 | Auto DI | 41 | 207 | 1899-12-31 | LT67ARV_25_TENSAO_DIF | 1035 | LTARV_25_TENSAO_DIF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | 25 diferença de Frequência | 0 | 0 | 0 | Auto DI | 41 | 208 | 1899-12-31 | LT67ARV_25_FREQ_DIF | 1036 | LTARV_25_FREQ_DIF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | 25 diferença de Ângulo | 0 | 0 | 0 | Auto DI | 41 | 209 | 1899-12-31 | LT67ARV_25_ANG_DIF | 1037 | LTARV_25_ANG_DIF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Saúde Comunicação | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1038 | LT67ARV_SAUDE_COMUNIC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Disjuntor 52-20 – Aberto | 0 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | LT21ARV_DJ_ABERTO | IDF | LTARV_DJ_ABERTO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Disjuntor 52-20 – Fechado | 0 | 0 | 0 | DiSOEx2 | 240 | 160 | 1899-12-31 | LT21ARV_DJ_FECHADO | IDF | LTARV_DJ_FECHADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Secc.89-120 - Aberto | 0 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | LT21ARV_S26QB_ABERTA | IDF | LTARV_S26QB_ABERTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Secc.89-120 - Fechado | 0 | 0 | 0 | DiSOEx2 | 240 | 161 | 1899-12-31 | LT21ARV_S26QB_FECHADA | IDF | LTARV_S26QB_FECHADA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Secc.89-118 - Aberto | 0 | 0 | 0 | DiSOEx2 | 240 | 162 | 1899-12-31 | LT21ARV_S26QC_ABERTA | IDF | LTARV_S26QC_ABERTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Secc.89-118 - Fechado | 0 | 0 | 0 | DiSOEx2 | 240 | 162 | 1899-12-31 | LT21ARV_S26QC_FECHADA | IDF | LTARV_S26QC_FECHADA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Secc.89-122 - Aberto | 0 | 0 | 0 | DiSOEx2 | 240 | 163 | 1899-12-31 | LT21ARV_S26QD_ABERTA | IDF | LTARV_S26QD_ABERTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Secc.89-122 - Fechado | 0 | 0 | 0 | DiSOEx2 | 240 | 163 | 1899-12-31 | LT21ARV_S26QD_FECHADA | IDF | LTARV_S26QD_FECHADA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Seccion. 29-07 - Aberto | 0 | 0 | 0 | DiSOEx2 | 240 | 164 | 1899-12-31 | LT21ARV_S29T_ABERTA | IDF | LTARV_S29T_ABERTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Seccion. 29-07 - Fechado | 0 | 0 | 0 | DiSOEx2 | 240 | 164 | 1899-12-31 | LT21ARV_S29T_FECHADA | IDF | LTARV_S29T_FECHADA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | DJ - Chave 43TC - Incluir/Excluir | 0 | 0 | 0 | DiVal | 101 | 85 | 1899-12-31 | LT21ARV_43TC_EXCLUIDA | OR | LTARV_43TC_EXCLUIDA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | DJ - SF6 - Alarme | 0 | 0 | 0 | DiVal | 240 | 192 | 1899-12-31 | LT21ARV_DJ_SF6_ALARME | IDF | LTARV_DJ_SF6_ALARME | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | DJ - SF6 - Bloqueio | 0 | 0 | 0 | DiVal | 240 | 191 | 1899-12-31 | LT21ARV_DJ_SF6_BLOQ | IDF | LTARV_DJ_SF6_BLOQ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | DJ - Mola Descarregada | 0 | 0 | 0 | DiVal | 240 | 190 | 1899-12-31 | LT21ARV_DJ_MOLA_DESC | IDF | LTARV_DJ_MOLA_DESC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | DJ - 43LR - Posição LOCAL | 0 | 0 | 0 | DiVal | 240 | 193 | 1899-12-31 | LT21ARV_DJ_43LR_LOC | IDF | LTARV_DJ_43LR_LOC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | DJ - Falta VCC de COM/MOTOR - Alarme | 0 | 0 | 0 | DiVal | 240 | 194 | 1899-12-31 | LT21ARV_DJ_FVCC_CMD | IDF | LTARV_DJ_FVCC_CMD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Sinal Rele (F67) - Excluir 43TC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Sinal Rele (F67) - Excluir 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (Só para lógica interna de intertravamento!) | - | (Só para lógica interna de intertravamento!) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Operação Indevida de SECCIONADORAS | 0 | 0 | 0 | DiVal | 240 | 195 | 1899-12-31 | LT21ARV_OP_INDEV_SEC | OR | LTARV_OP_INDEV_SEC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | DJ - Supervisão Circuito TRIP - Alarme | 0 | 0 | 0 | DiVal | 170 | 55 | 1899-12-31 | LT21ARV_DJ_SBOB_TRIP | OR | LTARV_DJ_SBOB_TRIP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Grupo de Ajustes B - Ativado | 0 | 0 | 0 | DiVal | 128 | 24 | 1899-12-31 | LT21ARV_GRPB_ATIVADO | 1040 | LT21ARV_GRPB_ATIVADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | 79 - Excluído | 0 | 0 | 0 | DiVal | 40 | 81 | 1899-12-31 | LT21ARV_79_EXCLUIDO | OR | LTARV_79_EXCLUIDO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | 79 - Disparo | 0 | 0 | 0 | Auto DI | 160 | 128 | 1899-12-31 | LT21ARV_25_SUP_79 | 1041 | LT21ARV_25_SUP_79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | 79 - Religamento Sucedido | 0 | 0 | 0 | Auto DI | 40 | 162 | 1899-12-31 | LT21ARV_79_SUCEDIDO | 1042 | LT21ARV_79_SUCEDIDO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | 79 - Bloqueado (Lockout) | 0 | 0 | 0 | AutoFault | 150 | 180 | 1900-01-01 | LT21ARV_79_BLOQUEADO | 1044 | LT21ARV_79_BLOQUEADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | 25 - Bloqueado | 0 | 0 | 0 | DiVal | 41 | 32 | 1899-12-31 | LT21ARV_25_BLOQUEADO | 1043 | LT21ARV_25_BLOQUEADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | 25 - Falha Operação Sincronismo | 0 | 0 | 0 | Auto DI | 41 | 35 | 1899-12-31 | LT21ARV_25_FALHA_SINC | OR | LTARV_25_FALHA_SINC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 50 BF | 0 | 0 | 0 | AutoFault | 160 | 85 | 1900-01-01 | LT21ARV_50BF_ATUADO | 1045 | LT21ARV_50BF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Supervisão Medição: Falha Fusível TPs | 0 | 0 | 0 | DiVal | 135 | 149 | 1899-12-31 | LT21ARV_60FF_ALARME | 1046 | LT21ARV_60FF_ALARME | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Prot.21 - Bloqueada | 0 | 0 | 0 | DiVal | 28 | 52 | 1899-12-31 | LT21ARV_21_BLOQUEADA | 1047 | LT21ARV_21_BLOQUEADA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 21 Trip Fase A | 0 | 0 | 0 | FaultDI | 28 | 206 | 1900-01-01 | LT21ARV_21FA_ATUADO | 1048 | LT21ARV_21FA_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 21 Trip Fase B | 0 | 0 | 0 | FaultDI | 28 | 207 | 1900-01-01 | LT21ARV_21FB_ATUADO | 1049 | LT21ARV_21FB_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 21 Trip Fase C | 0 | 0 | 0 | FaultDI | 28 | 208 | 1900-01-01 | LT21ARV_21FC_ATUADO | 1050 | LT21ARV_21FC_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 21 N Trip | 0 | 0 | 0 | FaultDI | 28 | 212 | 1900-01-01 | LT21ARV_21N_ATUADO | 1051 | LT21ARV_21N_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 21 Trip3p.Z1sf | 0 | 0 | 0 | AutoFault | 28 | 224 | 1900-01-01 | LT21ARV_21Z1SF_ATUADO | 1052 | LT21ARV_21Z1SF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 21 Trip3p.Z1mf | 0 | 0 | 0 | AutoFault | 28 | 225 | 1900-01-01 | LT21ARV_21Z1MF_ATUADO | 1053 | LT21ARV_21Z1MF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 21 Trip3p.Z2 | 0 | 0 | 0 | AutoFault | 28 | 217 | 1900-01-01 | LT21ARV_21Z2_ATUADO | 1054 | LT21ARV_21Z2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 21 Trip3p.Z3 | 0 | 0 | 0 | AutoFault | 28 | 218 | 1900-01-01 | LT21ARV_21Z3_ATUADO | 1055 | LT21ARV_21Z3_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 21 Trip3p.Z4 | 0 | 0 | 0 | AutoFault | 28 | 209 | 1900-01-01 | LT21ARV_21Z4_ATUADO | 1056 | LT21ARV_21Z4_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Falta Tensão LT - Alarme | 0 | 0 | 0 | DiVal | 240 | 205 | 1899-12-31 | LT21ARV_LT_SEM_VCA | OR | LTARV_LT_SEM_VCA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Localiz.Defeito - Disparo | 0 | 0 | 0 | DiVal | 151 | 7 | 1899-12-31 | LT21ARV_LDF_ATUADO | 1057 | LT21ARV_LDF_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuada Proteção Backup: 5XB TRIP | 0 | 0 | 0 | AutoFault | 128 | 72 | 1900-01-01 | LT21ARV_5XB_ATUADO | 1058 | LT21ARV_5XB_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuada Proteção 50HS - Trip ABC (SOTF) | 0 | 0 | 0 | AutoFault | 25 | 95 | 1900-01-01 | LT21ARV_50HS_ATUADO | 1059 | LT21ARV_50HS_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 50N-1 | 0 | 0 | 0 | AutoFault | 160 | 92 | 1900-01-01 | LT21ARV_50NE1_ATUADO | 1060 | LT21ARV_50NE1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 50N-2 | 0 | 0 | 0 | AutoFault | 160 | 93 | 1900-01-01 | LT21ARV_50NE2_ATUADO | 1061 | LT21ARV_50NE2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 50/51 - Fase A | 0 | 0 | 0 | FaultDI | 64 | 117 | 1900-01-01 | LT21ARV_5051FA_ATUADO | 1062 | LT21ARV_5051FA_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 50/51 - Fase B | 0 | 0 | 0 | FaultDI | 64 | 118 | 1900-01-01 | LT21ARV_5051FB_ATUADO | 1063 | LT21ARV_5051FB_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 50/51 - Fase C | 0 | 0 | 0 | FaultDI | 64 | 119 | 1900-01-01 | LT21ARV_5051FC_ATUADO | 1064 | LT21ARV_5051FC_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 51N | 0 | 0 | 0 | FaultDI | 60 | 66 | 1900-01-01 | LT21ARV_51N_ATUADO | 1065 | LT21ARV_51N_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 50-1 | 0 | 0 | 0 | AutoFault | 64 | 121 | 1900-01-01 | LT21ARV_50FNE1_ATUADO | 1066 | LT21ARV_50FNE1_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 50-2 | 0 | 0 | 0 | AutoFault | 64 | 122 | 1900-01-01 | LT21ARV_50FNE2_ATUADO | 1067 | LT21ARV_50FNE2_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Atuado 51 | 0 | 0 | 0 | AutoFault | 64 | 123 | 1900-01-01 | LT21ARV_51FN_ATUADO | 1068 | LT21ARV_51FN_ATUADO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | 25 diferença de Tensão | 0 | 0 | 0 | Auto DI | 41 | 47 | 1899-12-31 | LT21ARV_25_TENSAO_DIF | OR | LTARV_25_TENSAO_DIF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | 25 diferença de Frequência | 0 | 0 | 0 | Auto DI | 41 | 48 | 1899-12-31 | LT21ARV_25_FREQ_DIF | OR | LTARV_25_FREQ_DIF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | 25 diferença de Ângulo | 0 | 0 | 0 | Auto DI | 41 | 49 | 1899-12-31 | LT21ARV_25_ANG_DIF | OR | LTARV_25_ANG_DIF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Saúde Comunicação | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1069 | LT21ARV_SAUDE_COMUNIC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A

## ANALOGICOS
SE GUAPORÉ
|  | PONTO | RELÉ |  |  | IEC 60870-5-103 | [5 empty] | COS |  |  |  |  | LOCAL |  | COS |  | NOPER | COS
EQUIPAMENTO | MÓDULO |  | Entrada Binária | Saída Binária | LED | Tipo Ponto | Type | Inf N. | Asdu | Identificação do ponto na UTR: | DNP3.0 | Identificação do ponto | Estado0 | Estado1 | Estado0 | Estado1 | SULENGE | RGE | SULENGE | RGE |  | INFO S4 | LOAD S4
Medição
TREETECH TM (End: 16) | TR2 | Temperatura do óleo | 3 (Read Holding Reg) | 40020 | 0 | 16 Bits | 0 | TR2_TM11_TEMP_OLEO | IDF | TR2_TEMP_OLEO | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 16) | TR2AT | Temperatura do enrolamento 1 | 3 (Read Holding Reg) | 40021 | 0 | 16 Bits | 0 | TR2_TM11_TEMP_ENROL_AT | 0 | TR2_TEMP_ENROL_AT | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 15) | TR2 | Temperatura do óleo | 3 (Read Holding Reg) | 40020 | 0 | 16 Bits | 0 | TR2_TM12_TEMP_OLEO | IDF | TR2_TEMP_OLEO | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 15) | TR2BT | Temperatura do enrolamento 1 | 3 (Read Holding Reg) | 40021 | 0 | 16 Bits | 0 | TR2_TM12_TEMP_ENROL_BT | 0 | TR2_TEMP_ENROL_BT | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPS (End: 14) | TR2 | Medida TAP ATUAL | 3 (Read Holding Reg) | 40009 | 0 | 16 Bits | 0 | TR2_TAP | SPS | TR2_TAP | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPS (End: 14) | TR3 | Medida TAP ATUAL | 3 (Read Holding Reg) | 40018 | 0 | 16 Bits | 0 | TR3_TAP | SPS | TR3_TAP | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 02) | TR1 | Temperatura do óleo | 3 (Read Holding Reg) | 40020 | 0 | 16 Bits | 0 | TR1_TM11_TEMP_OLEO | IDF | TR1_TEMP_OLEO | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 02) | TR1AT | Temperatura do enrolamento 1 | 3 (Read Holding Reg) | 40021 | 0 | 16 Bits | 0 | TR1_TM11_TEMP_ENROL_AT | IDF | TR1_TEMP_ENROL_AT | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 03) | TR1 | Temperatura do óleo | 3 (Read Holding Reg) | 40020 | 0 | 16 Bits | 0 | TR1_TM12_TEMP_OLEO | IDF | TR1_TEMP_OLEO | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TREETECH TM (End: 03) | TR1BT | Temperatura do enrolamento 1 | 3 (Read Holding Reg) | 40021 | 0 | 16 Bits | 0 | TR1_TM12_TEMP_ENROL_BT | 0 | TR1_TEMP_ENROL_BT | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PM820 (End: 09) | SA | CORRENTE A | 3 (Read Holding Reg) | 43000 | 0 | 32 Bits | 0 | SACA_CORRENTE_FA | 0 | SACA_CORRENTE_FA | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PM820 (End: 09) | SA | CORRENTE B | 3 (Read Holding Reg) | 43002 | 0 | 32 Bits | 0 | SACA_CORRENTE_FB | 0 | SACA_CORRENTE_FB | 271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PM820 (End: 09) | SA | CORRENTE C | 3 (Read Holding Reg) | 43004 | 0 | 32 Bits | 0 | SACA_CORRENTE_FC | 0 | SACA_CORRENTE_FC | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PM820 (End: 09) | SA | TENSAO AB | 3 (Read Holding Reg) | 43020 | 0 | 32 Bits | 0 | SACA_TENSAO_AB | 0 | SACA_TENSAO_AB | 273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PM820 (End: 09) | SA | TENSAO BC | 3 (Read Holding Reg) | 43022 | 0 | 32 Bits | 0 | SACA_TENSAO_BC | 0 | SACA_TENSAO_BC | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PM820 (End: 09) | SA | TENSAO CA | 3 (Read Holding Reg) | 43024 | 0 | 32 Bits | 0 | SACA_TENSAO_CA | 0 | SACA_TENSAO_CA | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PM820 (End: 09) | SA | TENSAO A | 3 (Read Holding Reg) | 43028 | 0 | 32 Bits | 0 | SACA_TENSAO_A | 0 | SACA_TENSAO_A | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PM820 (End: 09) | SA | TENSAO B | 3 (Read Holding Reg) | 43030 | 0 | 32 Bits | 0 | SACA_TENSAO_B | 0 | SACA_TENSAO_B | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PM820 (End: 09) | SA | TENSAO C | 3 (Read Holding Reg) | 43032 | 0 | 32 Bits | 0 | SACA_TENSAO_C | 0 | SACA_TENSAO_C | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PM820 (End: 09) | SA | POTÊNCIA ATIVA TOTAL | 3 (Read Holding Reg) | 43068 | 0 | 32 Bits | 0 | SACA_POT_ATIVA | 0 | SACA_POT_ATIVA | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PM820 (End: 09) | SA | POTÊNCIA REATIVA TOTAL | 3 (Read Holding Reg) | 43078 | 0 | 32 Bits | 0 | SACA_POT_REATIVA | 0 | SACA_POT_REATIVA | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | B138 | TENSAO AB BARRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BARRA138_TENSAO_VAB | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | B69 | TENSAO AB BARRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BARRA69_TENSAO_VAB | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | B23P1 | TENSAO AB BARRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BARRAP1_23_TENSAO_VAB | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | B23P2 | TENSAO AB BARRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BARRAP2_23_TENSAO_VAB | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TR1 | TAP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TR1_TAP | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AI-1 | SA | Tensão Vcc | R1SI-1 | 0 | 0 | 0 | 0 | 0 | 0 | SA_VCC | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AI-2 | TR3 | Temperatura do óleo | R1SI-4 | 0 | 0 | 0 | 0 | 0 | 0 | TR3_TEMPERATURA_OLEO | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AI-3 | 0 | 0 | R1SI-6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AI-4 | 0 | 0 | R1SI-9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AI-5 | 0 | 0 | R1SI-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AI-6 | 0 | 0 | R1SI-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AI-7 | 0 | 0 | R1SI-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AI-8 | 0 | 0 | R1SI-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AI-9 | 0 | 0 | R1SI-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AI-10 | 0 | 0 | R1SI-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AI-11 | 0 | 0 | R1SI-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AI-12 | 0 | 0 | R1SI-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AI-13 | 0 | 0 | R1SI-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AI-14 | 0 | 0 | R1SI-34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AI-15 | 0 | 0 | R1SI-36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AI-16 | 0 | 0 | R1SC-39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7SJ632(End.: 1Ch) | GPR21 | Tensão Barra A-B | 0 | 0 | 0 | AI Val | 134 | 137 | 2015-08-09 | GPR21_TENSAO_AB | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Corrente Fase A | 0 | 0 | 0 | AI Val | 134 | 137 | 9/1 | GPR21_CORRENTE_FA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Corrente Fase B | 0 | 0 | 0 | AI Val | 134 | 137 | 9/2 | GPR21_CORRENTE_FB | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Corrente Fase C | 0 | 0 | 0 | AI Val | 134 | 137 | 9/3 | GPR21_CORRENTE_FC | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Potencia Ativa | 0 | 0 | 0 | AI Val | 134 | 137 | 9/11 | GPR21_POT_ATIVA | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ632(End.: 1Ch) | GPR21 | Potencia Reativa | 0 | 0 | 0 | AI Val | 134 | 137 | 9/12 | GPR21_POT_REATIVA | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
FORM 6 (End:4) | GPR22 | Tensão fase B | 0 | 0 | 0 | Analógico | 0 | 30 | 1900-01-28 | GPR22_TENSAO_FB | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Corrente fase A | 0 | 0 | 0 | Analógico | 0 | 30 | 0 | GPR22_CORRENTE_FA | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Corrente fase B | 0 | 0 | 0 | Analógico | 0 | 30 | 1899-12-31 | GPR22_CORRENTE_FB | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Corrente fase C | 0 | 0 | 0 | Analógico | 0 | 30 | 1900-01-01 | GPR22_CORRENTE_FC | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Potencia Ativa | 0 | 0 | 0 | Analógico | 0 | 30 | 1900-01-24 | GPR22_POT_ATIVA | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Potencia Reativa | 0 | 0 | 0 | Analógico | 0 | 30 | 1900-01-25 | GPR22_POT_REATIVA | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
FORM 6 (End:4) | GPR22 | Tensão Bateria | 0 | 0 | 0 | Analógico | 0 | 30 | 1900-01-22 | GPR22_TENSAO_BATERIAS | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | Corrente Fase A | 0 | 0 | 0 | Analógico | 0 | 30 | 0 | GPR23_CORRENTE_FA | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | Corrente Fase B | 0 | 0 | 0 | Analógico | 0 | 30 | 1899-12-31 | GPR23_CORRENTE_FB | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | Corrente Fase C | 0 | 0 | 0 | Analógico | 0 | 30 | 1900-01-01 | GPR23_CORRENTE_FC | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | Potência Reativa | 0 | 0 | 0 | Analógico | 0 | 30 | 1900-01-04 | GPR23_POT_REATIVA | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | Tensão Trifásica | 0 | 0 | 0 | Analógico | 0 | 30 | 1900-01-06 | GPR23_TENSAO_3F | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | Potência Ativa | 0 | 0 | 0 | Analógico | 0 | 30 | 1900-01-16 | GPR23_POT_ATIVA | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:26) | GPR23 | Tensão Bateria | 0 | 0 | 0 | Analógico | 0 | 30 | 1900-01-18 | GPR23_TENSAO_BATERIA | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | Corrente Fase A | 0 | 0 | 0 | Analógico | 0 | 30 | 0 | GPR24_CORRENTE_FA | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | Corrente Fase B | 0 | 0 | 0 | Analógico | 0 | 30 | 1899-12-31 | GPR24_CORRENTE_FB | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | Corrente Fase C | 0 | 0 | 0 | Analógico | 0 | 30 | 1900-01-01 | GPR24_CORRENTE_FC | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | Potência Reativa | 0 | 0 | 0 | Analógico | 0 | 30 | 1900-01-04 | GPR24_POT_REATIVA | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | Tensão Trifásica | 0 | 0 | 0 | Analógico | 0 | 30 | 1900-01-06 | GPR24_TENSAO_3F | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | Potência Ativa | 0 | 0 | 0 | Analógico | 0 | 30 | 1900-01-16 | GPR24_POT_ATIVA | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
ADVC (End:27) | GPR24 | Tensão Bateria | 0 | 0 | 0 | Analógico | 0 | 30 | 1900-01-18 | GPR24_TENSAO_BATERIA | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
7SJ63 (End: 18d/12h) | GPR31 | Tensão A-B | 0 | 0 | 0 | AI Val | 134 | 137 | 2011-08-09 | GPR31_TENSAO_AB | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Corrente Fase A | 0 | 0 | 0 | AiVal | 134 | 137 | 9/1 | GPR31_CORRENTE_FA | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Corrente Fase B | 0 | 0 | 0 | AiVal | 134 | 137 | 9/2 | GPR31_CORRENTE_FB | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Corrente Fase C | 0 | 0 | 0 | AiVal | 134 | 137 | 9/3 | GPR31_CORRENTE_FC | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Potência Ativa | 0 | 0 | 0 | AiVal | 134 | 137 | 9/11 | GPR31_POT_ATIVA | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 18d/12h) | GPR31 | Potência Reativa | 0 | 0 | 0 | AiVal | 134 | 137 | 9/12 | GPR31_POT_REATIVA | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Tensão A-B | 0 | 0 | 0 | AI Val | 134 | 137 | 2011-08-09 | GPR32_TENSAO_AB | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Corrente Fase A | 0 | 0 | 0 | AiVal | 134 | 137 | 9/1 | GPR32_CORRENTE_FA | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Corrente Fase B | 0 | 0 | 0 | AiVal | 134 | 137 | 9/2 | GPR32_CORRENTE_FB | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Corrente Fase C | 0 | 0 | 0 | AiVal | 134 | 137 | 9/3 | GPR32_CORRENTE_FC | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Potência Ativa | 0 | 0 | 0 | AiVal | 134 | 137 | 9/11 | GPR32_POT_ATIVA | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 19d/13h) | GPR32 | Potência Reativa | 0 | 0 | 0 | AiVal | 134 | 137 | 9/12 | GPR32_POT_REATIVA | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Tensão A-B | 0 | 0 | 0 | AI Val | 134 | 137 | 2011-08-09 | GPR33_TENSAO_AB | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Corrente Fase A | 0 | 0 | 0 | AiVal | 134 | 137 | 9/1 | GPR33_CORRENTE_FA | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Corrente Fase B | 0 | 0 | 0 | AiVal | 134 | 137 | 9/2 | GPR33_CORRENTE_FB | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Corrente Fase C | 0 | 0 | 0 | AiVal | 134 | 137 | 9/3 | GPR33_CORRENTE_FC | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Potência Ativa | 0 | 0 | 0 | AiVal | 134 | 137 | 9/11 | GPR33_POT_ATIVA | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 20d/14h) | GPR33 | Potência Reativa | 0 | 0 | 0 | AiVal | 134 | 137 | 9/12 | GPR33_POT_REATIVA | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Tensão A-B | 0 | 0 | 0 | AI Val | 134 | 137 | 2011-08-09 | GPR34_TENSAO_AB | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Corrente Fase A | 0 | 0 | 0 | AiVal | 134 | 137 | 9/1 | GPR34_CORRENTE_FA | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Corrente Fase B | 0 | 0 | 0 | AiVal | 134 | 137 | 9/2 | GPR34_CORRENTE_FB | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Corrente Fase C | 0 | 0 | 0 | AiVal | 134 | 137 | 9/3 | GPR34_CORRENTE_FC | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Potência Ativa | 0 | 0 | 0 | AiVal | 134 | 137 | 9/11 | GPR34_POT_ATIVA | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 21d/15h) | GPR34 | Potência Reativa | 0 | 0 | 0 | AiVal | 134 | 137 | 9/12 | GPR34_POT_REATIVA | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Tensão A-B | 0 | 0 | 0 | AI Val | 134 | 137 | 2011-08-09 | GPR35_TENSAO_AB | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Corrente Fase A | 0 | 0 | 0 | AiVal | 134 | 137 | 9/1 | GPR35_CORRENTE_FA | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Corrente Fase B | 0 | 0 | 0 | AiVal | 134 | 137 | 9/2 | GPR35_CORRENTE_FB | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Corrente Fase C | 0 | 0 | 0 | AiVal | 134 | 137 | 9/3 | GPR35_CORRENTE_FC | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Potência Ativa | 0 | 0 | 0 | AiVal | 134 | 137 | 9/11 | GPR35_POT_ATIVA | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 22d/16h) | GPR35 | Potência Reativa | 0 | 0 | 0 | AiVal | 134 | 137 | 9/12 | GPR35_POT_REATIVA | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Tensão A-B | 0 | 0 | 0 | AI Val | 134 | 137 | 2011-08-09 | GPR36_TENSAO_AB | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Corrente Fase A | 0 | 0 | 0 | AiVal | 134 | 137 | 9/1 | GPR36_CORRENTE_FA | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Corrente Fase B | 0 | 0 | 0 | AiVal | 134 | 137 | 9/2 | GPR36_CORRENTE_FB | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Corrente Fase C | 0 | 0 | 0 | AiVal | 134 | 137 | 9/3 | GPR36_CORRENTE_FC | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Potência Ativa | 0 | 0 | 0 | AiVal | 134 | 137 | 9/11 | GPR36_POT_ATIVA | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 23d/17h) | GPR36 | Potência Reativa | 0 | 0 | 0 | AiVal | 134 | 137 | 9/12 | GPR36_POT_REATIVA | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Tensão A-B | 0 | 0 | 0 | AI Val | 134 | 137 | 2011-08-09 | IB23_TENSAO_AB | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Corrente Fase A | 0 | 0 | 0 | AiVal | 134 | 137 | 9/1 | IB23_CORRENTE_FA | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Corrente Fase B | 0 | 0 | 0 | AiVal | 134 | 137 | 9/2 | IB23_CORRENTE_FB | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Corrente Fase C | 0 | 0 | 0 | AiVal | 134 | 137 | 9/3 | IB23_CORRENTE_FC | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Potência Ativa | 0 | 0 | 0 | AiVal | 134 | 137 | 9/11 | IB23_POT_ATIVA | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 05) | IB23 | Potência Reativa | 0 | 0 | 0 | AiVal | 134 | 137 | 9/12 | IB23_POT_REATIVA | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End: 24d/18h) | BC1 | Tensão A-B | 0 | 0 | 0 | AI Val | 134 | 137 | 2011-08-09 | BC1_TENSAO_AB | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End: 6) | BC2 | Tensão A-B | 0 | 0 | 0 | AI Val | 134 | 137 | 2011-08-09 | BC2_TENSAO_AB | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Tensão Fase B da Barra de 69 kV | 0 | 0 | 0 | AI Val | 134 | 137 | 9/6 | TR3AT_TENSAO_FB | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Corrente Fase A | 0 | 0 | 0 | AI Val | 134 | 137 | 9/1 | TR3AT_CORRENTE_FA | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Corrente Fase B | 0 | 0 | 0 | AI Val | 134 | 137 | 9/2 | TR3AT_CORRENTE_FB | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Corrente Fase C | 0 | 0 | 0 | AI Val | 134 | 137 | 9/3 | TR3AT_CORRENTE_FC | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Potência Ativa | 0 | 0 | 0 | AI Val | 134 | 137 | 9/11 | TR3AT_POT_ATIVA | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 17d/11h) | TR3AT | Potência Reativa | 0 | 0 | 0 | AI Val | 134 | 137 | 9/12 | TR3AT_POT_REATIVA | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Tensão Fase B da Barra P1 23kV | 0 | 0 | 0 | AiVal | 134 | 137 | 9/6 | TR3BT_TENSAO_FB | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Corrente Fase A | 0 | 0 | 0 | AiVal | 134 | 137 | 9/1 | TR3BT_CORRENTE_FA | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Corrente Fase B | 0 | 0 | 0 | AiVal | 134 | 137 | 9/2 | TR3BT_CORRENTE_FB | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Corrente Fase C | 0 | 0 | 0 | AiVal | 134 | 137 | 9/3 | TR3BT_CORRENTE_FC | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Potência Ativa | 0 | 0 | 0 | AiVal | 134 | 137 | 9/11 | TR3BT_POT_ATIVA | 124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 04) | TR3BT | Potência Reativa | 0 | 0 | 0 | AiVal | 134 | 137 | 9/12 | TR3BT_POT_REATIVA | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Tensão Fase B da Barra de 69 kV | 0 | 0 | 0 | AI Val | 134 | 137 | 9/6 | TR2AT_TENSAO_FB | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Corrente Fase A | 0 | 0 | 0 | AI Val | 134 | 137 | 9/1 | TR2AT_CORRENTE_FA | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Corrente Fase B | 0 | 0 | 0 | AI Val | 134 | 137 | 9/2 | TR2AT_CORRENTE_FB | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Corrente Fase C | 0 | 0 | 0 | AI Val | 134 | 137 | 9/3 | TR2AT_CORRENTE_FC | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Potência Ativa | 0 | 0 | 0 | AI Val | 134 | 137 | 9/11 | TR2AT_POT_ATIVA | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 13d/0Dh) | TR2AT | Potência Reativa | 0 | 0 | 0 | AI Val | 134 | 137 | 9/12 | TR2AT_POT_REATIVA | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Tensão Fase B da Barra P2 23kV | 0 | 0 | 0 | AiVal | 134 | 137 | 9/6 | TR2BT_TENSAO_FB | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Corrente Fase A | 0 | 0 | 0 | AiVal | 134 | 137 | 9/1 | TR2BT_CORRENTE_FA | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Corrente Fase B | 0 | 0 | 0 | AiVal | 134 | 137 | 9/2 | TR2BT_CORRENTE_FB | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Corrente Fase C | 0 | 0 | 0 | AiVal | 134 | 137 | 9/3 | TR2BT_CORRENTE_FC | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Potência Ativa | 0 | 0 | 0 | AiVal | 134 | 137 | 9/11 | TR2BT_POT_ATIVA | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ62 (End.: 02) | TR2BT | Potência Reativa | 0 | 0 | 0 | AiVal | 134 | 137 | 9/12 | TR2BT_POT_REATIVA | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Tensão Fase B da Barra de 138 kV | 0 | 0 | 0 | AI Val | 134 | 137 | 9/6 | TR1AT_TENSAO_FB | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Corrente Fase A | 0 | 0 | 0 | AI Val | 134 | 137 | 9/1 | TR1AT_CORRENTE_FA | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Corrente Fase B | 0 | 0 | 0 | AI Val | 134 | 137 | 9/2 | TR1AT_CORRENTE_FB | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Corrente Fase C | 0 | 0 | 0 | AI Val | 134 | 137 | 9/3 | TR1AT_CORRENTE_FC | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Potência Ativa | 0 | 0 | 0 | AI Val | 134 | 137 | 9/11 | TR1AT_POT_ATIVA | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ63 (End.: 14d/0Eh) | TR1AT | Potência Reativa | 0 | 0 | 0 | AI Val | 134 | 137 | 9/12 | TR1AT_POT_REATIVA | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Tensão Fase B da Barra de 69 kV | 0 | 0 | 0 | AiVal | 134 | 137 | 9/6 | TR1BT_TENSAO_FB | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Corrente Fase A | 0 | 0 | 0 | AiVal | 134 | 137 | 9/1 | TR1BT_CORRENTE_FA | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Corrente Fase B | 0 | 0 | 0 | AiVal | 134 | 137 | 9/2 | TR1BT_CORRENTE_FB | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Corrente Fase C | 0 | 0 | 0 | AiVal | 134 | 137 | 9/3 | TR1BT_CORRENTE_FC | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Potência Ativa | 0 | 0 | 0 | AiVal | 134 | 137 | 9/11 | TR1BT_POT_ATIVA | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ621 (End.: 16d/10h) | TR1BT | Potência Reativa | 0 | 0 | 0 | AiVal | 134 | 137 | 9/12 | TR1BT_POT_REATIVA | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Tensão fase B da LT | 0 | 0 | 0 | AI Val | 134 | 124 | 9/5 | LT21PCH_TENSAO_FB | IDF | LTPCH_TENSAO_FB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Corrente fase A | 0 | 0 | 0 | AI Val | 134 | 124 | 9/1 | LT21PCH_CORRENTE_FA | IDF | LTPCH_CORRENTE_FA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Corrente fase B | 0 | 0 | 0 | AI Val | 134 | 124 | 9/2 | LT21PCH_CORRENTE_FB | IDF | LTPCH_CORRENTE_FB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Corrente fase C | 0 | 0 | 0 | AI Val | 134 | 124 | 9/3 | LT21PCH_CORRENTE_FC | IDF | LTPCH_CORRENTE_FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Potência Ativa | 0 | 0 | 0 | AI Val | 134 | 124 | 9/7 | LT21PCH_POT_ATIVA | IDF | LTPCH_POT_ATIVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Potência Reativa | 0 | 0 | 0 | AI Val | 134 | 124 | 9/8 | LT21PCH_POT_REATIVA | IDF | LTPCH_POT_REATIVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 07) | LT PCH | Defeito na Linha (km) | 0 | 0 | 0 | FPAI | 151 | 19 | 1900-01-03 | LT21PCH_DIST_DEFEITO | 217 | LT21PCH_DIST_DEFEITO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Tensão fase B da LT | 0 | 0 | 0 | AI Val | 134 | 137 | 9/6 | LT67PCH_TENSAO_FB | 210 | LTPCH_TENSAO_FB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Corrente fase A | 0 | 0 | 0 | AI Val | 134 | 137 | 9/1 | LT67PCH_CORRENTE_FA | 211 | LTPCH_CORRENTE_FA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Corrente fase B | 0 | 0 | 0 | AI Val | 134 | 137 | 9/2 | LT67PCH_CORRENTE_FB | 212 | LTPCH_CORRENTE_FB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Corrente fase C | 0 | 0 | 0 | AI Val | 134 | 137 | 9/3 | LT67PCH_CORRENTE_FC | 213 | LTPCH_CORRENTE_FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Potência Ativa | 0 | 0 | 0 | AI Val | 134 | 137 | 9/11 | LT67PCH_POT_ATIVA | 214 | LTPCH_POT_ATIVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Potência Reativa | 0 | 0 | 0 | AI Val | 134 | 137 | 9/12 | LT67PCH_POT_REATIVA | 215 | LTPCH_POT_REATIVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 08) | LT PCH | Defeito na Linha (km) | 0 | 0 | 0 | FPAI | 151 | 19 | 1900-01-03 | LT67PCH_DIST_DEFEITO | 216 | LT67PCH_DIST_DEFEITO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Tensão Barra A-B | 0 | 0 | 0 | AI Val | 134 | 137 | 9_6 | LT67KNP_TENSAO_AB | 220 | LTKNP_TENSAO_AB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Corrente Fase A | 0 | 0 | 0 | AI Val | 134 | 137 | 9/1 | LT67KNP_CORRENTE_FA | 221 | LTKNP_CORRENTE_FA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Corrente Fase B | 0 | 0 | 0 | AI Val | 134 | 137 | 9/2 | LT67KNP_CORRENTE_FB | 222 | LTKNP_CORRENTE_FB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Corrente Fase C | 0 | 0 | 0 | AI Val | 134 | 137 | 9/3 | LT67KNP_CORRENTE_FC | 223 | LTKNP_CORRENTE_FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Potência Ativa | 0 | 0 | 0 | AI Val | 134 | 137 | 9_11 | LT67KNP_POT_ATIVA | 224 | LTKNP_POT_ATIVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Potência Reativa | 0 | 0 | 0 | AI Val | 134 | 137 | 9_12 | LT67KNP_POT_REATIVA | 225 | LTKNP_POT_REATIVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 12d/0Ch) | LT KNP | Defeito na Linha (km) | 0 | 0 | 0 | FPAI | 151 | 19 | 1900-01-03 | LT67KNP_DIST_DEFEITO | 226 | LT67KNP_DIST_DEFEITO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Tensão Barra A-B | 0 | 0 | 0 | AI Val | 134 | 124 | 9/5 | LT21KNP_TENSAO_FB | IDF | LTKNP_TENSAO_FB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Corrente Fase A | 0 | 0 | 0 | AI Val | 134 | 124 | 9/1 | LT21KNP_CORRENTE_FA | IDF | LTKNP_CORRENTE_FA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Corrente Fase B | 0 | 0 | 0 | AI Val | 134 | 124 | 9/2 | LT21KNP_CORRENTE_FB | IDF | LTKNP_CORRENTE_FB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Corrente Fase C | 0 | 0 | 0 | AI Val | 134 | 124 | 9/3 | LT21KNP_CORRENTE_FC | IDF | LTKNP_CORRENTE_FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Potencia Ativa | 0 | 0 | 0 | AI Val | 134 | 124 | 9/7 | LT21KNP_POT_ATIVA | IDF | LTKNP_POT_ATIVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Potencia Reativa | 0 | 0 | 0 | AI Val | 134 | 124 | 9/8 | LT21KNP_POT_REATIVA | IDF | LTKNP_POT_REATIVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 11d/0Bh) | LT KNP | Defeito na Linha (km) | 0 | 0 | 0 | FPAI | 151 | 19 | 1900-01-03 | LT21KNP_DIST_DEFEITO | 227 | LT21KNP_DIST_DEFEITO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Tensão Barra A-B | 0 | 0 | 0 | AI Val | 134 | 137 | 9/6 | LT67CAS_TENSAO_FB | 230 | LTCAS_TENSAO_FB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Corrente Fase A | 0 | 0 | 0 | AI Val | 134 | 137 | 9/1 | LT67CAS_CORRENTE_FA | 231 | LTCAS_CORRENTE_FA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Corrente Fase B | 0 | 0 | 0 | AI Val | 134 | 137 | 9/2 | LT67CAS_CORRENTE_FB | 232 | LTCAS_CORRENTE_FB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Corrente Fase C | 0 | 0 | 0 | AI Val | 134 | 137 | 9/3 | LT67CAS_CORRENTE_FC | 233 | LTCAS_CORRENTE_FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Potência Ativa | 0 | 0 | 0 | AI Val | 134 | 137 | 9/11 | LT67CAS_POT_ATIVA | 234 | LTCAS_POT_ATIVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Potência Reativa | 0 | 0 | 0 | AI Val | 134 | 137 | 9/12 | LT67CAS_POT_REATIVA | 235 | LTCAS_POT_REATIVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 10/0Ah) | LT CAS | Defeito na Linha (km) | 0 | 0 | 0 | FPAI | 151 | 19 | 1900-01-03 | LT67CAS_DIST_DEFEITO | 236 | LT67CAS_DIST_DEFEITO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Tensão Barra A-B | 0 | 0 | 0 | AI Val | 134 | 124 | 9_5 | LT21CAS_TENSAO_AB | IDF | LTCAS_TENSAO_AB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Corrente Fase A | 0 | 0 | 0 | AI Val | 134 | 124 | 9/1 | LT21CAS_CORRENTE_FA | IDF | LTCAS_CORRENTE_FA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Corrente Fase B | 0 | 0 | 0 | AI Val | 134 | 124 | 9/2 | LT21CAS_CORRENTE_FB | IDF | LTCAS_CORRENTE_FB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Corrente Fase C | 0 | 0 | 0 | AI Val | 134 | 124 | 9/3 | LT21CAS_CORRENTE_FC | IDF | LTCAS_CORRENTE_FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Potencia Ativa | 0 | 0 | 0 | AI Val | 134 | 124 | 9/7 | LT21CAS_POT_ATIVA | IDF | LTCAS_POT_ATIVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Potencia Reativa | 0 | 0 | 0 | AI Val | 134 | 124 | 9/8 | LT21CAS_POT_REATIVA | IDF | LTCAS_POT_REATIVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA63 (End.: 9) | LT CAS | Defeito na Linha (km) | 0 | 0 | 0 | FPAI | 151 | 19 | 1900-01-03 | LT21CAS_DIST_DEFEITO | 237 | LT21CAS_DIST_DEFEITO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Tensão Barra A-B | 0 | 0 | 0 | AI Val | 134 | 137 | 9/6 | LT67ARV_TENSAO_FB | 240 | LTARV_TENSAO_FB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Corrente Fase A | 0 | 0 | 0 | AI Val | 134 | 137 | 9/1 | LT67ARV_CORRENTE_FA | 241 | LTARV_CORRENTE_FA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Corrente Fase B | 0 | 0 | 0 | AI Val | 134 | 137 | 9/2 | LT67ARV_CORRENTE_FB | 242 | LTARV_CORRENTE_FB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Corrente Fase C | 0 | 0 | 0 | AI Val | 134 | 137 | 9/3 | LT67ARV_CORRENTE_FC | 243 | LTARV_CORRENTE_FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Potência Ativa | 0 | 0 | 0 | AI Val | 134 | 137 | 9/11 | LT67ARV_POT_ATIVA | 244 | LTARV_POT_ATIVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Potência Reativa | 0 | 0 | 0 | AI Val | 134 | 137 | 9/12 | LT67ARV_POT_REATIVA | 245 | LTARV_POT_REATIVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SJ64 (End.: 30/1Eh) | LT ARV | Defeito na Linha (km) | 0 | 0 | 0 | FPAI | 151 | 19 | 1900-01-03 | LT67ARV_DIST_DEFEITO | 246 | LT67ARV_DIST_DEFEITO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Tensão fase B da LT | 0 | 0 | 0 | AI Val | 134 | 124 | 9/5 | LT21ARV_TENSAO_FB | IDF | LTARV_TENSAO_FB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Corrente fase A | 0 | 0 | 0 | AI Val | 134 | 124 | 9/1 | LT21ARV_CORRENTE_FA | IDF | LTARV_CORRENTE_FA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Corrente fase B | 0 | 0 | 0 | AI Val | 134 | 124 | 9/2 | LT21ARV_CORRENTE_FB | IDF | LTARV_CORRENTE_FB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Corrente fase C | 0 | 0 | 0 | AI Val | 134 | 124 | 9/3 | LT21ARV_CORRENTE_FC | IDF | LTARV_CORRENTE_FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Potência Ativa | 0 | 0 | 0 | AI Val | 134 | 124 | 9/7 | LT21ARV_POT_ATIVA | IDF | LTARV_POT_ATIVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Potência Reativa | 0 | 0 | 0 | AI Val | 134 | 124 | 9/8 | LT21ARV_POT_REATIVA | IDF | LTARV_POT_REATIVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
7SA631 (End.: 31/1F) | LT ARV | Defeito na Linha (km) | 0 | 0 | 0 | FPAI | 151 | 19 | 1900-01-03 | LT21ARV_DIST_DEFEITO | 247 | LT21ARV_DIST_DEFEITO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A